## Dropdowns
Refrigerants
RefrigID | RefrigName | ChangeDate | ChangeUserID | HighPressure
1 | R-11 | 2005-02-23 15:34 | NULL | 0
2 | R-113 | 2005-02-23 15:34 | NULL | 0
4 | R-12 | 2005-02-23 15:34 | NULL | 1
5 | R-123 | 2005-02-23 15:34 | NULL | 0
6 | R-134a | 2005-02-23 15:34 | NULL | 1
7 | R-22 | 2005-02-23 15:34 | NULL | 1
8 | R-500 | 2005-02-23 15:34 | NULL | 1
9 | R-114 | 2008-03-17 11:16 | NULL | 0
10 | R-514A | 2022-09-09 20:33 | NULL | 0
Units
UnitID | UnitName | ChangeDate | UserID | IsMetric
1 | PSIG | 2005-02-23 15:40 | NULL | 0
2 | PSIA | 2005-02-23 15:40 | NULL | 0
3 | InHg | 2005-02-23 15:40 | NULL | 0
4 | Feet | 2005-02-23 15:40 | NULL | 0
5 | KPA | 2010-03-17 08:36 | NULL | 1
6 | Bar | 2010-03-17 08:36 | NULL | 1
Make / Manufacturers
ManuID | ManufacturerName | ChangeDate | ChangeUserID
1 | Trane | 2005-02-23 15:33 | NULL
2 | Carrier | 2005-02-23 15:33 | NULL
3 | York | 2005-02-23 15:33 | NULL
4 | McQuay | 2005-02-23 15:33 | NULL
5 | Westinghouse | 2005-02-23 15:33 | NULL
6 | Dunham-Bush | 2005-02-23 15:33 | NULL
7 | FES | 2005-02-23 15:33 | NULL
8 | Sullair | 2006-09-18 14:30 | 75
9 | Arctic Cool | 2015-02-19 08:14 | NULL
10 | Multistack | 2017-03-09 16:35 | NULL
11 | Daikin | 2020-03-04 09:09 | NULL
Year
Start | 1965
End | 2025
MaintenanceTypes
MaintTypeID | MaintCatID | MaintTypeDesc | UseMaintDesc | UseMaintQuantity | SecondaryFieldLabel | ChangeDate | ChangeUserID
1 | 1 | Annual Maintenance Date | 0 | 0 | NULL | 2005-07-06 10:30 | 75
2 | 2 | Oil Change Date | 0 | 0 | NULL | 2005-07-06 10:30 | 75
3 | 2 | Date Oil Added | 0 | 1 | Quantity of Oil Added (quarts) | 2005-07-06 10:30 | 75
4 | 2 | Oil Filter Change Date | 0 | 0 | NULL | 2005-07-06 10:31 | 75
5 | 2 | Oil Analysis Date | 0 | 0 | NULL | 2005-07-06 10:31 | 75
6 | 3 | Eddy Current Test Date (Condenser) | 0 | 0 | NULL | 2005-07-06 10:31 | 75
7 | 3 | Eddy Current Test Date (Evaporator) | 0 | 0 | NULL | 2005-07-06 10:31 | 75
8 | 4 | Major Stop Inspection | 0 | 0 | NULL | 2005-07-06 10:32 | 75
9 | 5 | Refrigerant Analysis Date | 0 | 0 | NULL | 2005-07-06 10:32 | 75
10 | 5 | Date Refrigerant Added | 0 | 1 | Quantity of Refrigerant Added (lb.) | 2005-07-06 10:32 | 75
11 | 6 | Condenser Tube Cleaning Date | 0 | 0 | NULL | 2005-07-06 10:32 | 75
12 | 6 | Evaporator Tube Cleaning Date | 0 | 0 | NULL | 2005-07-06 10:33 | 75
13 | 7 | Purge Tank Reclaim Date | 0 | 1 | Purge Run Time Reading When Tank Reclaimed | 2005-07-06 10:33 | 75
14 | 7 | Purge Filter Dryer Change Date | 0 | 0 | NULL | 2005-07-06 10:33 | 75
15 | 8 | Major Repair | 1 | 0 | Major Repair Description | 2005-07-06 10:33 | 75
16 | 9 | Running Inspection | 0 | 0 | NULL | 2018-07-31 | 75
18 | 10 | Vibration Analysis | 0 | 0 | NULL | 2021-02-16 15:23 | 75
MaintenanceCategories
MaintCatID | MaintCatDesc | ChangeUserID | ChangeDate
1 | Annual Maintenance | 75 | 2005-07-06 10:26
2 | Oil Maintenance | 75 | 2005-07-06 10:27
3 | Eddy Current Tests | 75 | 2005-07-06 10:27
4 | Major Stop Inspection (compressor teardown) | 75 | 2005-07-06 10:27
5 | Refrigerant Maintenance | 75 | 2005-07-06 10:27
6 | Tube Cleaning | 75 | 2005-07-06 10:27
7 | Purge Maintenance | 75 | 2005-07-06 10:27
8 | Major Repairs | 75 | 2005-07-06 10:28
9 | Running Inspection | 1 | 2018-07-31 09:35
10 | Vibration Analysis | 75 | 2021-02-16 15:19
Required
location

## Conversion
ConversionID | RefrigName | TempF | PSIA | PSIG | InHg
1 | R-11 | 10 | 3.35 | -11.35 | -23.1045
2 | R-11 | 10.1 | 3.36 | -11.34 | -23.0862
3 | R-11 | 10.2 | 3.37 | -11.33 | -23.0679
4 | R-11 | 10.3 | 3.38 | -11.32 | -23.0496
5 | R-11 | 10.4 | 3.39 | -11.31 | -23.0312
6 | R-11 | 10.5 | 3.4 | -11.3 | -23.0129
7 | R-11 | 10.6 | 3.41 | -11.29 | -22.9946
8 | R-11 | 10.7 | 3.42 | -11.29 | -22.9763
9 | R-11 | 10.8 | 3.42 | -11.28 | -22.9579
10 | R-11 | 10.9 | 3.43 | -11.27 | -22.9396
11 | R-11 | 11 | 3.44 | -11.26 | -22.9213
12 | R-11 | 11.1 | 3.45 | -11.25 | -22.903
13 | R-11 | 11.2 | 3.46 | -11.24 | -22.8846
14 | R-11 | 11.3 | 3.47 | -11.23 | -22.8663
15 | R-11 | 11.4 | 3.48 | -11.22 | -22.846
16 | R-11 | 11.5 | 3.49 | -11.21 | -22.8276
17 | R-11 | 11.6 | 3.5 | -11.2 | -22.8093
18 | R-11 | 11.7 | 3.51 | -11.19 | -22.791
19 | R-11 | 11.8 | 3.52 | -11.19 | -22.7727
20 | R-11 | 11.9 | 3.52 | -11.18 | -22.7523
21 | R-11 | 12 | 3.53 | -11.17 | -22.734
22 | R-11 | 12.1 | 3.54 | -11.16 | -22.7157
23 | R-11 | 12.2 | 3.55 | -11.15 | -22.6953
24 | R-11 | 12.3 | 3.56 | -11.14 | -22.677
25 | R-11 | 12.4 | 3.57 | -11.13 | -22.6586
26 | R-11 | 12.5 | 3.58 | -11.12 | -22.6383
27 | R-11 | 12.6 | 3.59 | -11.11 | -22.62
28 | R-11 | 12.7 | 3.6 | -11.1 | -22.6016
29 | R-11 | 12.8 | 3.61 | -11.09 | -22.5813
30 | R-11 | 12.9 | 3.62 | -11.08 | -22.563
31 | R-11 | 13 | 3.63 | -11.07 | -22.5426
32 | R-11 | 13.1 | 3.64 | -11.06 | -22.5243
33 | R-11 | 13.2 | 3.65 | -11.05 | -22.5039
34 | R-11 | 13.3 | 3.66 | -11.04 | -22.4856
35 | R-11 | 13.4 | 3.67 | -11.03 | -22.4652
36 | R-11 | 13.5 | 3.68 | -11.03 | -22.4469
37 | R-11 | 13.6 | 3.69 | -11.02 | -22.4265
38 | R-11 | 13.7 | 3.7 | -11.01 | -22.4062
39 | R-11 | 13.8 | 3.7 | -11 | -22.3879
40 | R-11 | 13.9 | 3.71 | -10.99 | -22.3675
41 | R-11 | 14 | 3.72 | -10.98 | -22.3471
42 | R-11 | 14.1 | 3.73 | -10.97 | -22.3288
43 | R-11 | 14.2 | 3.74 | -10.96 | -22.3085
44 | R-11 | 14.3 | 3.75 | -10.95 | -22.2881
45 | R-11 | 14.4 | 3.76 | -10.94 | -22.2677
46 | R-11 | 14.5 | 3.77 | -10.93 | -22.2494
47 | R-11 | 14.6 | 3.78 | -10.92 | -22.2291
48 | R-11 | 14.7 | 3.79 | -10.91 | -22.2087
49 | R-11 | 14.8 | 3.8 | -10.9 | -22.1883
50 | R-11 | 14.9 | 3.81 | -10.89 | -22.168
51 | R-11 | 15 | 3.82 | -10.88 | -22.1476
52 | R-11 | 15.1 | 3.83 | -10.87 | -22.1293
53 | R-11 | 15.2 | 3.84 | -10.86 | -22.1089
54 | R-11 | 15.3 | 3.85 | -10.85 | -22.0886
55 | R-11 | 15.4 | 3.86 | -10.84 | -22.0682
56 | R-11 | 15.5 | 3.87 | -10.83 | -22.0478
57 | R-11 | 15.6 | 3.88 | -10.82 | -22.0275
58 | R-11 | 15.7 | 3.89 | -10.81 | -22.0071
59 | R-11 | 15.8 | 3.9 | -10.8 | -21.9868
60 | R-11 | 15.9 | 3.91 | -10.79 | -21.9664
61 | R-11 | 16 | 3.92 | -10.78 | -21.946
62 | R-11 | 16.1 | 3.93 | -10.77 | -21.9236
63 | R-11 | 16.2 | 3.94 | -10.76 | -21.9033
64 | R-11 | 16.3 | 3.95 | -10.75 | -21.8829
65 | R-11 | 16.4 | 3.96 | -10.74 | -21.8626
66 | R-11 | 16.5 | 3.97 | -10.73 | -21.8422
67 | R-11 | 16.6 | 3.98 | -10.72 | -21.8219
68 | R-11 | 16.7 | 3.99 | -10.71 | -21.7995
69 | R-11 | 16.8 | 4 | -10.7 | -21.7791
70 | R-11 | 16.9 | 4.01 | -10.69 | -21.7587
71 | R-11 | 17 | 4.02 | -10.68 | -21.7363
72 | R-11 | 17.1 | 4.03 | -10.67 | -21.716
73 | R-11 | 17.2 | 4.04 | -10.66 | -21.6956
74 | R-11 | 17.3 | 4.05 | -10.64 | -21.6732
75 | R-11 | 17.4 | 4.07 | -10.63 | -21.6529
76 | R-11 | 17.5 | 4.08 | -10.63 | -21.6325
77 | R-11 | 17.6 | 4.09 | -10.61 | -21.6101
78 | R-11 | 17.7 | 4.1 | -10.6 | -21.5897
79 | R-11 | 17.8 | 4.11 | -10.59 | -21.5674
80 | R-11 | 17.9 | 4.12 | -10.58 | -21.547
81 | R-11 | 18 | 4.13 | -10.57 | -21.5246
82 | R-11 | 18.1 | 4.14 | -10.56 | -21.5042
83 | R-11 | 18.2 | 4.15 | -10.55 | -21.4818
84 | R-11 | 18.3 | 4.16 | -10.54 | -21.4615
85 | R-11 | 18.4 | 4.17 | -10.53 | -21.4391
86 | R-11 | 18.5 | 4.18 | -10.52 | -21.4167
87 | R-11 | 18.6 | 4.19 | -10.51 | -21.3963
88 | R-11 | 18.7 | 4.2 | -10.5 | -21.3739
89 | R-11 | 18.8 | 4.21 | -10.49 | -21.3515
90 | R-11 | 18.9 | 4.22 | -10.48 | -21.3312
91 | R-11 | 19 | 4.23 | -10.47 | -21.3088
92 | R-11 | 19.1 | 4.25 | -10.46 | -21.2864
93 | R-11 | 19.2 | 4.26 | -10.44 | -21.264
94 | R-11 | 19.3 | 4.27 | -10.43 | -21.2436
95 | R-11 | 19.4 | 4.28 | -10.42 | -21.2212
96 | R-11 | 19.5 | 4.29 | -10.41 | -21.1988
97 | R-11 | 19.6 | 4.3 | -10.4 | -21.1764
98 | R-11 | 19.7 | 4.31 | -10.39 | -21.154
99 | R-11 | 19.8 | 4.32 | -10.38 | -21.1316
100 | R-11 | 19.9 | 4.33 | -10.37 | -21.1092
101 | R-11 | 20 | 4.34 | -10.36 | -21.0868
102 | R-11 | 20.1 | 4.35 | -10.35 | -21.0645
103 | R-11 | 20.2 | 4.37 | -10.34 | -21.0421
104 | R-11 | 20.3 | 4.38 | -10.32 | -21.0197
105 | R-11 | 20.4 | 4.39 | -10.31 | -20.9973
106 | R-11 | 20.5 | 4.4 | -10.3 | -20.9749
107 | R-11 | 20.6 | 4.41 | -10.29 | -20.9525
108 | R-11 | 20.7 | 4.42 | -10.28 | -20.9301
109 | R-11 | 20.8 | 4.43 | -10.27 | -20.9077
110 | R-11 | 20.9 | 4.44 | -10.26 | -20.8853
111 | R-11 | 21 | 4.45 | -10.25 | -20.8609
112 | R-11 | 21.1 | 4.46 | -10.23 | -20.8385
113 | R-11 | 21.2 | 4.48 | -10.22 | -20.8161
114 | R-11 | 21.3 | 4.49 | -10.21 | -20.7937
115 | R-11 | 21.4 | 4.5 | -10.2 | -20.7713
116 | R-11 | 21.5 | 4.51 | -10.19 | -20.7468
117 | R-11 | 21.6 | 4.52 | -10.18 | -20.7244
118 | R-11 | 21.7 | 4.53 | -10.17 | -20.702
119 | R-11 | 21.8 | 4.54 | -10.16 | -20.6776
120 | R-11 | 21.9 | 4.55 | -10.14 | -20.6552
121 | R-11 | 22 | 4.57 | -10.13 | -20.6308
122 | R-11 | 22.1 | 4.58 | -10.12 | -20.6084
123 | R-11 | 22.2 | 4.59 | -10.11 | -20.584
124 | R-11 | 22.3 | 4.6 | -10.1 | -20.5616
125 | R-11 | 22.4 | 4.61 | -10.09 | -20.5392
126 | R-11 | 22.5 | 4.62 | -10.08 | -20.5147
127 | R-11 | 22.6 | 4.64 | -10.06 | -20.4903
128 | R-11 | 22.7 | 4.65 | -10.05 | -20.4679
129 | R-11 | 22.8 | 4.66 | -10.04 | -20.4435
130 | R-11 | 22.9 | 4.67 | -10.03 | -20.4211
131 | R-11 | 23 | 4.68 | -10.02 | -20.3967
132 | R-11 | 23.1 | 4.69 | -10.01 | -20.3722
133 | R-11 | 23.2 | 4.71 | -10 | -20.3498
134 | R-11 | 23.3 | 4.72 | -9.98 | -20.3254
135 | R-11 | 23.4 | 4.73 | -9.97 | -20.301
136 | R-11 | 23.5 | 4.74 | -9.96 | -20.2765
137 | R-11 | 23.6 | 4.75 | -9.95 | -20.2541
138 | R-11 | 23.7 | 4.76 | -9.94 | -20.2297
139 | R-11 | 23.8 | 4.78 | -9.92 | -20.2053
140 | R-11 | 23.9 | 4.79 | -9.91 | -20.1808
141 | R-11 | 24 | 4.8 | -9.9 | -20.1564
142 | R-11 | 24.1 | 4.81 | -9.89 | -20.132
143 | R-11 | 24.2 | 4.82 | -9.88 | -20.1075
144 | R-11 | 24.3 | 4.84 | -9.86 | -20.0831
145 | R-11 | 24.4 | 4.85 | -9.85 | -20.0587
146 | R-11 | 24.5 | 4.86 | -9.84 | -20.0342
147 | R-11 | 24.6 | 4.87 | -9.83 | -20.0098
148 | R-11 | 24.7 | 4.88 | -9.82 | -19.9854
149 | R-11 | 24.8 | 4.9 | -9.8 | -19.9609
150 | R-11 | 24.9 | 4.91 | -9.79 | -19.9365
151 | R-11 | 25 | 4.92 | -9.78 | -19.9121
152 | R-11 | 25.1 | 4.93 | -9.77 | -19.8877
153 | R-11 | 25.2 | 4.94 | -9.76 | -19.8632
154 | R-11 | 25.3 | 4.96 | -9.74 | -19.8388
155 | R-11 | 25.4 | 4.97 | -9.73 | -19.8123
156 | R-11 | 25.5 | 4.98 | -9.72 | -19.7879
157 | R-11 | 25.6 | 4.99 | -9.71 | -19.7634
158 | R-11 | 25.7 | 5 | -9.7 | -19.739
159 | R-11 | 25.8 | 5.02 | -9.68 | -19.7126
160 | R-11 | 25.9 | 5.03 | -9.67 | -19.6881
161 | R-11 | 26 | 5.04 | -9.66 | -19.6637
162 | R-11 | 26.1 | 5.05 | -9.64 | -19.6372
163 | R-11 | 26.2 | 5.07 | -9.63 | -19.6128
164 | R-11 | 26.3 | 5.08 | -9.62 | -19.5863
165 | R-11 | 26.4 | 5.09 | -9.61 | -19.5619
166 | R-11 | 26.5 | 5.11 | -9.6 | -19.5354
167 | R-11 | 26.6 | 5.12 | -9.58 | -19.511
168 | R-11 | 26.7 | 5.13 | -9.57 | -19.4845
169 | R-11 | 26.8 | 5.14 | -9.56 | -19.4601
170 | R-11 | 26.9 | 5.16 | -9.54 | -19.4336
171 | R-11 | 27 | 5.17 | -9.53 | -19.4092
172 | R-11 | 27.1 | 5.18 | -9.52 | -19.3827
173 | R-11 | 27.2 | 5.19 | -9.51 | -19.3562
174 | R-11 | 27.3 | 5.21 | -9.5 | -19.3318
175 | R-11 | 27.4 | 5.22 | -9.48 | -19.3054
176 | R-11 | 27.5 | 5.23 | -9.47 | -19.2789
177 | R-11 | 27.6 | 5.24 | -9.46 | -19.2524
178 | R-11 | 27.7 | 5.26 | -9.44 | -19.228
179 | R-11 | 27.8 | 5.27 | -9.43 | -19.2015
180 | R-11 | 27.9 | 5.28 | -9.42 | -19.175
181 | R-11 | 28 | 5.29 | -9.4 | -19.1486
182 | R-11 | 28.1 | 5.31 | -9.39 | -19.1221
183 | R-11 | 28.2 | 5.32 | -9.38 | -19.0956
184 | R-11 | 28.3 | 5.33 | -9.37 | -19.0692
185 | R-11 | 28.4 | 5.35 | -9.35 | -19.0447
186 | R-11 | 28.5 | 5.36 | -9.34 | -19.0183
187 | R-11 | 28.6 | 5.37 | -9.33 | -18.9918
188 | R-11 | 28.7 | 5.38 | -9.31 | -18.9653
189 | R-11 | 28.8 | 5.4 | -9.3 | -18.9368
190 | R-11 | 28.9 | 5.41 | -9.29 | -18.9104
191 | R-11 | 29 | 5.42 | -9.28 | -18.8839
192 | R-11 | 29.1 | 5.44 | -9.26 | -18.8574
193 | R-11 | 29.2 | 5.45 | -9.25 | -18.831
194 | R-11 | 29.3 | 5.46 | -9.24 | -18.8045
195 | R-11 | 29.4 | 5.48 | -9.22 | -18.778
196 | R-11 | 29.5 | 5.49 | -9.21 | -18.7495
197 | R-11 | 29.6 | 5.5 | -9.2 | -18.7231
198 | R-11 | 29.7 | 5.52 | -9.18 | -18.6966
199 | R-11 | 29.8 | 5.53 | -9.17 | -18.6681
200 | R-11 | 29.9 | 5.54 | -9.16 | -18.6416
201 | R-11 | 30 | 5.56 | -9.14 | -18.6151
202 | R-11 | 30.1 | 5.57 | -9.13 | -18.5866
203 | R-11 | 30.2 | 5.58 | -9.12 | -18.5602
204 | R-11 | 30.3 | 5.6 | -9.1 | -18.5337
205 | R-11 | 30.4 | 5.61 | -9.09 | -18.5052
206 | R-11 | 30.5 | 5.62 | -9.08 | -18.4787
207 | R-11 | 30.6 | 5.64 | -9.06 | -18.4502
208 | R-11 | 30.7 | 5.65 | -9.05 | -18.4217
209 | R-11 | 30.8 | 5.67 | -9.04 | -18.3953
210 | R-11 | 30.9 | 5.68 | -9.02 | -18.3668
211 | R-11 | 31 | 5.69 | -9.01 | -18.3403
212 | R-11 | 31.1 | 5.71 | -8.99 | -18.3118
213 | R-11 | 31.2 | 5.72 | -8.98 | -18.2833
214 | R-11 | 31.3 | 5.73 | -8.97 | -18.2568
215 | R-11 | 31.4 | 5.75 | -8.95 | -18.2283
216 | R-11 | 31.5 | 5.76 | -8.94 | -18.1998
217 | R-11 | 31.6 | 5.78 | -8.93 | -18.1713
218 | R-11 | 31.7 | 5.79 | -8.91 | -18.1448
219 | R-11 | 31.8 | 5.8 | -8.9 | -18.1163
220 | R-11 | 31.9 | 5.82 | -8.88 | -18.0878
221 | R-11 | 32 | 5.83 | -8.87 | -18.0593
222 | R-11 | 32.1 | 5.84 | -8.86 | -18.0308
223 | R-11 | 32.2 | 5.86 | -8.84 | -18.0023
224 | R-11 | 32.3 | 5.87 | -8.83 | -17.9738
225 | R-11 | 32.4 | 5.89 | -8.81 | -17.9453
226 | R-11 | 32.5 | 5.9 | -8.8 | -17.9168
227 | R-11 | 32.6 | 5.91 | -8.79 | -17.8883
228 | R-11 | 32.7 | 5.93 | -8.77 | -17.8598
229 | R-11 | 32.8 | 5.94 | -8.76 | -17.8313
230 | R-11 | 32.9 | 5.96 | -8.74 | -17.8028
231 | R-11 | 33 | 5.97 | -8.73 | -17.7743
232 | R-11 | 33.1 | 5.99 | -8.71 | -17.7437
233 | R-11 | 33.2 | 6 | -8.7 | -17.7152
234 | R-11 | 33.3 | 6.01 | -8.69 | -17.6867
235 | R-11 | 33.4 | 6.03 | -8.67 | -17.6582
236 | R-11 | 33.5 | 6.04 | -8.66 | -17.6277
237 | R-11 | 33.6 | 6.06 | -8.64 | -17.5992
238 | R-11 | 33.7 | 6.07 | -8.63 | -17.5707
239 | R-11 | 33.8 | 6.08 | -8.62 | -17.5401
240 | R-11 | 33.9 | 6.1 | -8.6 | -17.5116
241 | R-11 | 34 | 6.11 | -8.59 | -17.4811
242 | R-11 | 34.1 | 6.13 | -8.57 | -17.4526
243 | R-11 | 34.2 | 6.14 | -8.56 | -17.4241
244 | R-11 | 34.3 | 6.16 | -8.54 | -17.3936
245 | R-11 | 34.4 | 6.17 | -8.53 | -17.365
246 | R-11 | 34.5 | 6.19 | -8.51 | -17.3345
247 | R-11 | 34.6 | 6.2 | -8.5 | -17.304
248 | R-11 | 34.7 | 6.21 | -8.48 | -17.2755
249 | R-11 | 34.8 | 6.23 | -8.47 | -17.2449
250 | R-11 | 34.9 | 6.25 | -8.46 | -17.2144
251 | R-11 | 35 | 6.26 | -8.44 | -17.1859
252 | R-11 | 35.1 | 6.27 | -8.43 | -17.1553
253 | R-11 | 35.2 | 6.29 | -8.41 | -17.1248
254 | R-11 | 35.3 | 6.3 | -8.4 | -17.0943
255 | R-11 | 35.4 | 6.32 | -8.38 | -17.0658
256 | R-11 | 35.5 | 6.33 | -8.37 | -17.0352
257 | R-11 | 35.6 | 6.35 | -8.35 | -17.0047
258 | R-11 | 35.7 | 6.36 | -8.34 | -16.9741
259 | R-11 | 35.8 | 6.38 | -8.32 | -16.9436
260 | R-11 | 35.9 | 6.39 | -8.31 | -16.913
261 | R-11 | 36 | 6.41 | -8.29 | -16.8825
262 | R-11 | 36.1 | 6.42 | -8.28 | -16.852
263 | R-11 | 36.2 | 6.44 | -8.26 | -16.8214
264 | R-11 | 36.3 | 6.45 | -8.25 | -16.7909
265 | R-11 | 36.4 | 6.47 | -8.23 | -16.7603
266 | R-11 | 36.5 | 6.48 | -8.22 | -16.7298
267 | R-11 | 36.6 | 6.5 | -8.2 | -16.6993
268 | R-11 | 36.7 | 6.51 | -8.19 | -16.6667
269 | R-11 | 36.8 | 6.53 | -8.17 | -16.6362
270 | R-11 | 36.9 | 6.54 | -8.16 | -16.6056
271 | R-11 | 37 | 6.56 | -8.14 | -16.5751
272 | R-11 | 37.1 | 6.58 | -8.13 | -16.5425
273 | R-11 | 37.2 | 6.59 | -8.11 | -16.512
274 | R-11 | 37.3 | 6.61 | -8.1 | -16.4814
275 | R-11 | 37.4 | 6.62 | -8.08 | -16.4488
276 | R-11 | 37.5 | 6.64 | -8.06 | -16.4183
277 | R-11 | 37.6 | 6.65 | -8.05 | -16.3878
278 | R-11 | 37.7 | 6.67 | -8.03 | -16.3552
279 | R-11 | 37.8 | 6.68 | -8.02 | -16.3246
280 | R-11 | 37.9 | 6.7 | -8 | -16.2921
281 | R-11 | 38 | 6.71 | -7.99 | -16.2615
282 | R-11 | 38.1 | 6.73 | -7.97 | -16.229
283 | R-11 | 38.2 | 6.75 | -7.96 | -16.1964
284 | R-11 | 38.3 | 6.76 | -7.94 | -16.1658
285 | R-11 | 38.4 | 6.78 | -7.92 | -16.1333
286 | R-11 | 38.5 | 6.79 | -7.91 | -16.1007
287 | R-11 | 38.6 | 6.81 | -7.89 | -16.0702
288 | R-11 | 38.7 | 6.82 | -7.88 | -16.0376
289 | R-11 | 38.8 | 6.84 | -7.86 | -16.005
290 | R-11 | 38.9 | 6.86 | -7.84 | -15.9724
291 | R-11 | 39 | 6.87 | -7.83 | -15.9398
292 | R-11 | 39.1 | 6.89 | -7.81 | -15.9093
293 | R-11 | 39.2 | 6.9 | -7.8 | -15.8767
294 | R-11 | 39.3 | 6.92 | -7.78 | -15.8442
295 | R-11 | 39.4 | 6.93 | -7.77 | -15.8116
296 | R-11 | 39.5 | 6.95 | -7.75 | -15.779
297 | R-11 | 39.6 | 6.97 | -7.73 | -15.7464
298 | R-11 | 39.7 | 6.98 | -7.72 | -15.7139
299 | R-11 | 39.8 | 7 | -7.7 | -15.6813
300 | R-11 | 39.9 | 7.02 | -7.69 | -15.6467
301 | R-11 | 40 | 7.03 | -7.67 | -15.6141
302 | R-11 | 40.1 | 7.05 | -7.65 | -15.5815
303 | R-11 | 40.2 | 7.06 | -7.64 | -15.5489
304 | R-11 | 40.3 | 7.08 | -7.62 | -15.5164
305 | R-11 | 40.4 | 7.09 | -7.61 | -15.4838
306 | R-11 | 40.5 | 7.11 | -7.59 | -15.4492
307 | R-11 | 40.6 | 7.13 | -7.57 | -15.4166
308 | R-11 | 40.7 | 7.14 | -7.56 | -15.384
309 | R-11 | 40.8 | 7.16 | -7.54 | -15.3494
310 | R-11 | 40.9 | 7.18 | -7.52 | -15.3168
311 | R-11 | 41 | 7.19 | -7.51 | -15.2822
312 | R-11 | 41.1 | 7.21 | -7.49 | -15.2496
313 | R-11 | 41.2 | 7.23 | -7.47 | -15.215
314 | R-11 | 41.3 | 7.24 | -7.46 | -15.1824
315 | R-11 | 41.4 | 7.26 | -7.44 | -15.1478
316 | R-11 | 41.5 | 7.28 | -7.42 | -15.1153
317 | R-11 | 41.6 | 7.29 | -7.41 | -15.0807
318 | R-11 | 41.7 | 7.31 | -7.39 | -15.046
319 | R-11 | 41.8 | 7.33 | -7.37 | -15.0135
320 | R-11 | 41.9 | 7.34 | -7.36 | -14.9788
321 | R-11 | 42 | 7.36 | -7.34 | -14.9442
322 | R-11 | 42.1 | 7.38 | -7.32 | -14.9117
323 | R-11 | 42.2 | 7.39 | -7.31 | -14.8771
324 | R-11 | 42.3 | 7.41 | -7.29 | -14.8424
325 | R-11 | 42.4 | 7.43 | -7.27 | -14.8078
326 | R-11 | 42.5 | 7.44 | -7.26 | -14.7732
327 | R-11 | 42.6 | 7.46 | -7.24 | -14.7386
328 | R-11 | 42.7 | 7.48 | -7.22 | -14.704
329 | R-11 | 42.8 | 7.5 | -7.21 | -14.6694
330 | R-11 | 42.9 | 7.51 | -7.19 | -14.6348
331 | R-11 | 43 | 7.53 | -7.17 | -14.6002
332 | R-11 | 43.1 | 7.55 | -7.15 | -14.5655
333 | R-11 | 43.2 | 7.56 | -7.14 | -14.5309
334 | R-11 | 43.3 | 7.58 | -7.12 | -14.4963
335 | R-11 | 43.4 | 7.6 | -7.1 | -14.4617
336 | R-11 | 43.5 | 7.61 | -7.09 | -14.4271
337 | R-11 | 43.6 | 7.63 | -7.07 | -14.3904
338 | R-11 | 43.7 | 7.65 | -7.05 | -14.3558
339 | R-11 | 43.8 | 7.67 | -7.03 | -14.3212
340 | R-11 | 43.9 | 7.68 | -7.02 | -14.2866
341 | R-11 | 44 | 7.7 | -7 | -14.25
342 | R-11 | 44.1 | 7.72 | -6.98 | -14.2154
343 | R-11 | 44.2 | 7.74 | -6.96 | -14.1787
344 | R-11 | 44.3 | 7.75 | -6.95 | -14.1441
345 | R-11 | 44.4 | 7.77 | -6.93 | -14.1074
346 | R-11 | 44.5 | 7.79 | -6.91 | -14.0728
347 | R-11 | 44.6 | 7.81 | -6.89 | -14.0362
348 | R-11 | 44.7 | 7.82 | -6.88 | -14.0016
349 | R-11 | 44.8 | 7.84 | -6.86 | -13.9649
350 | R-11 | 44.9 | 7.86 | -6.84 | -13.9303
351 | R-11 | 45 | 7.88 | -6.82 | -13.8937
352 | R-11 | 45.1 | 7.89 | -6.81 | -13.857
353 | R-11 | 45.2 | 7.91 | -6.79 | -13.8224
354 | R-11 | 45.3 | 7.93 | -6.77 | -13.7858
355 | R-11 | 45.4 | 7.95 | -6.75 | -13.7491
356 | R-11 | 45.5 | 7.96 | -6.74 | -13.7125
357 | R-11 | 45.6 | 7.98 | -6.72 | -13.6758
358 | R-11 | 45.7 | 8 | -6.7 | -13.6392
359 | R-11 | 45.8 | 8.02 | -6.68 | -13.6045
360 | R-11 | 45.9 | 8.04 | -6.66 | -13.5679
361 | R-11 | 46 | 8.05 | -6.65 | -13.5313
362 | R-11 | 46.1 | 8.07 | -6.63 | -13.4946
363 | R-11 | 46.2 | 8.09 | -6.61 | -13.458
364 | R-11 | 46.3 | 8.11 | -6.59 | -13.4193
365 | R-11 | 46.4 | 8.13 | -6.57 | -13.3826
366 | R-11 | 46.5 | 8.14 | -6.55 | -13.346
367 | R-11 | 46.6 | 8.16 | -6.54 | -13.3093
368 | R-11 | 46.7 | 8.18 | -6.52 | -13.2727
369 | R-11 | 46.8 | 8.2 | -6.5 | -13.236
370 | R-11 | 46.9 | 8.22 | -6.48 | -13.1974
371 | R-11 | 47 | 8.24 | -6.46 | -13.1607
372 | R-11 | 47.1 | 8.25 | -6.45 | -13.1241
373 | R-11 | 47.2 | 8.27 | -6.43 | -13.0854
374 | R-11 | 47.3 | 8.29 | -6.41 | -13.0487
375 | R-11 | 47.4 | 8.31 | -6.39 | -13.01
376 | R-11 | 47.5 | 8.33 | -6.37 | -12.9734
377 | R-11 | 47.6 | 8.35 | -6.35 | -12.9347
378 | R-11 | 47.7 | 8.37 | -6.34 | -12.8981
379 | R-11 | 47.8 | 8.38 | -6.32 | -12.8594
380 | R-11 | 47.9 | 8.4 | -6.3 | -12.8227
381 | R-11 | 48 | 8.42 | -6.28 | -12.784
382 | R-11 | 48.1 | 8.44 | -6.26 | -12.7454
383 | R-11 | 48.2 | 8.46 | -6.24 | -12.7087
384 | R-11 | 48.3 | 8.48 | -6.22 | -12.67
385 | R-11 | 48.4 | 8.5 | -6.2 | -12.6313
386 | R-11 | 48.5 | 8.51 | -6.19 | -12.5947
387 | R-11 | 48.6 | 8.53 | -6.17 | -12.556
388 | R-11 | 48.7 | 8.55 | -6.15 | -12.5173
389 | R-11 | 48.8 | 8.57 | -6.13 | -12.4786
390 | R-11 | 48.9 | 8.59 | -6.11 | -12.44
391 | R-11 | 49 | 8.61 | -6.09 | -12.4013
392 | R-11 | 49.1 | 8.63 | -6.07 | -12.3626
393 | R-11 | 49.2 | 8.65 | -6.05 | -12.3239
394 | R-11 | 49.3 | 8.67 | -6.03 | -12.2852
395 | R-11 | 49.4 | 8.69 | -6.02 | -12.2465
396 | R-11 | 49.5 | 8.7 | -6 | -12.2079
397 | R-11 | 49.6 | 8.72 | -5.98 | -12.1692
398 | R-11 | 49.7 | 8.74 | -5.96 | -12.1285
399 | R-11 | 49.8 | 8.76 | -5.94 | -12.0898
400 | R-11 | 49.9 | 8.78 | -5.92 | -12.0511
401 | R-11 | 50 | 8.8 | -5.9 | -12.0124
402 | R-11 | 50.1 | 8.82 | -5.88 | -11.9717
403 | R-11 | 50.2 | 8.84 | -5.86 | -11.933
404 | R-11 | 50.3 | 8.86 | -5.84 | -11.8943
405 | R-11 | 50.4 | 8.88 | -5.82 | -11.8536
406 | R-11 | 50.5 | 8.9 | -5.8 | -11.8149
407 | R-11 | 50.6 | 8.92 | -5.78 | -11.7742
408 | R-11 | 50.7 | 8.94 | -5.76 | -11.7355
409 | R-11 | 50.8 | 8.96 | -5.74 | -11.6948
410 | R-11 | 50.9 | 8.98 | -5.72 | -11.6541
411 | R-11 | 51 | 9 | -5.71 | -11.6154
412 | R-11 | 51.1 | 9.02 | -5.69 | -11.5747
413 | R-11 | 51.2 | 9.04 | -5.67 | -11.5339
414 | R-11 | 51.3 | 9.05 | -5.65 | -11.4953
415 | R-11 | 51.4 | 9.07 | -5.63 | -11.4545
416 | R-11 | 51.5 | 9.09 | -5.61 | -11.4138
417 | R-11 | 51.6 | 9.11 | -5.59 | -11.3731
418 | R-11 | 51.7 | 9.13 | -5.57 | -11.3324
419 | R-11 | 51.8 | 9.15 | -5.55 | -11.2937
420 | R-11 | 51.9 | 9.17 | -5.53 | -11.253
421 | R-11 | 52 | 9.19 | -5.51 | -11.2122
422 | R-11 | 52.1 | 9.21 | -5.49 | -11.1715
423 | R-11 | 52.2 | 9.23 | -5.47 | -11.1308
424 | R-11 | 52.3 | 9.25 | -5.45 | -11.0881
425 | R-11 | 52.4 | 9.27 | -5.43 | -11.0473
426 | R-11 | 52.5 | 9.29 | -5.41 | -11.0066
427 | R-11 | 52.6 | 9.31 | -5.39 | -10.9659
428 | R-11 | 52.7 | 9.33 | -5.37 | -10.9252
429 | R-11 | 52.8 | 9.35 | -5.35 | -10.8845
430 | R-11 | 52.9 | 9.38 | -5.33 | -10.8417
431 | R-11 | 53 | 9.39 | -5.3 | -10.801
432 | R-11 | 53.1 | 9.42 | -5.29 | -10.7603
433 | R-11 | 53.2 | 9.44 | -5.26 | -10.7175
434 | R-11 | 53.3 | 9.46 | -5.24 | -10.6768
435 | R-11 | 53.4 | 9.48 | -5.22 | -10.634
436 | R-11 | 53.5 | 9.5 | -5.2 | -10.5933
437 | R-11 | 53.6 | 9.52 | -5.18 | -10.5505
438 | R-11 | 53.7 | 9.54 | -5.16 | -10.5098
439 | R-11 | 53.8 | 9.56 | -5.14 | -10.4671
440 | R-11 | 53.9 | 9.58 | -5.12 | -10.4264
441 | R-11 | 54 | 9.6 | -5.1 | -10.3836
442 | R-11 | 54.1 | 9.62 | -5.08 | -10.3408
443 | R-11 | 54.2 | 9.64 | -5.06 | -10.2981
444 | R-11 | 54.3 | 9.66 | -5.04 | -10.2574
445 | R-11 | 54.4 | 9.68 | -5.02 | -10.2146
446 | R-11 | 54.5 | 9.7 | -5 | -10.1719
447 | R-11 | 54.6 | 9.72 | -4.98 | -10.1291
448 | R-11 | 54.7 | 9.75 | -4.95 | -10.0863
449 | R-11 | 54.8 | 9.77 | -4.93 | -10.0436
450 | R-11 | 54.9 | 9.79 | -4.91 | -10.0008
451 | R-11 | 55 | 9.81 | -4.89 | -9.9581
452 | R-11 | 55.1 | 9.83 | -4.87 | -9.9153
453 | R-11 | 55.2 | 9.85 | -4.85 | -9.8726
454 | R-11 | 55.3 | 9.87 | -4.83 | -9.8298
455 | R-11 | 55.4 | 9.89 | -4.81 | -9.7871
456 | R-11 | 55.5 | 9.91 | -4.79 | -9.7443
457 | R-11 | 55.6 | 9.94 | -4.76 | -9.6995
458 | R-11 | 55.7 | 9.96 | -4.74 | -9.6568
459 | R-11 | 55.8 | 9.98 | -4.72 | -9.614
460 | R-11 | 55.9 | 10 | -4.7 | -9.5692
461 | R-11 | 56 | 10.02 | -4.68 | -9.5285
462 | R-11 | 56.1 | 10.04 | -4.66 | -9.4878
463 | R-11 | 56.2 | 10.06 | -4.64 | -9.447
464 | R-11 | 56.3 | 10.09 | -4.61 | -9.386
465 | R-11 | 56.4 | 10.11 | -4.59 | -9.3452
466 | R-11 | 56.5 | 10.13 | -4.57 | -9.3045
467 | R-11 | 56.6 | 10.15 | -4.55 | -9.2638
468 | R-11 | 56.7 | 10.17 | -4.53 | -9.2231
469 | R-11 | 56.8 | 10.19 | -4.51 | -9.1824
470 | R-11 | 56.9 | 10.22 | -4.48 | -9.1213
471 | R-11 | 57 | 10.24 | -4.46 | -9.0806
472 | R-11 | 57.1 | 10.26 | -4.44 | -9.0398
473 | R-11 | 57.2 | 10.28 | -4.42 | -8.9991
474 | R-11 | 57.3 | 10.3 | -4.4 | -8.9584
475 | R-11 | 57.4 | 10.32 | -4.38 | -8.9177
476 | R-11 | 57.5 | 10.35 | -4.35 | -8.8566
477 | R-11 | 57.6 | 10.37 | -4.33 | -8.8159
478 | R-11 | 57.7 | 10.39 | -4.31 | -8.7752
479 | R-11 | 57.8 | 10.41 | -4.29 | -8.7344
480 | R-11 | 57.9 | 10.43 | -4.27 | -8.6937
481 | R-11 | 58 | 10.46 | -4.24 | -8.6326
482 | R-11 | 58.1 | 10.48 | -4.22 | -8.5919
483 | R-11 | 58.2 | 10.5 | -4.2 | -8.5512
484 | R-11 | 58.3 | 10.52 | -4.18 | -8.5105
485 | R-11 | 58.4 | 10.55 | -4.15 | -8.4494
486 | R-11 | 58.5 | 10.57 | -4.13 | -8.4087
487 | R-11 | 58.6 | 10.59 | -4.11 | -8.368
488 | R-11 | 58.7 | 10.61 | -4.09 | -8.3272
489 | R-11 | 58.8 | 10.63 | -4.07 | -8.2865
490 | R-11 | 58.9 | 10.66 | -4.04 | -8.2254
491 | R-11 | 59 | 10.68 | -4.02 | -8.1847
492 | R-11 | 59.1 | 10.7 | -4 | -8.144
493 | R-11 | 59.2 | 10.72 | -3.98 | -8.1033
494 | R-11 | 59.3 | 10.75 | -3.95 | -8.0422
495 | R-11 | 59.4 | 10.77 | -3.93 | -8.0015
496 | R-11 | 59.5 | 10.79 | -3.91 | -7.9608
497 | R-11 | 59.6 | 10.82 | -3.88 | -7.8997
498 | R-11 | 59.7 | 10.84 | -3.86 | -7.859
499 | R-11 | 59.8 | 10.86 | -3.84 | -7.8182
500 | R-11 | 59.9 | 10.88 | -3.82 | -7.7775
501 | R-11 | 60 | 10.91 | -3.79 | -7.7164
502 | R-11 | 60.1 | 10.93 | -3.77 | -7.6757
503 | R-11 | 60.2 | 10.95 | -3.75 | -7.635
504 | R-11 | 60.3 | 10.98 | -3.72 | -7.5739
505 | R-11 | 60.4 | 11 | -3.7 | -7.5332
506 | R-11 | 60.5 | 11.02 | -3.68 | -7.4925
507 | R-11 | 60.6 | 11.04 | -3.66 | -7.4518
508 | R-11 | 60.7 | 11.07 | -3.63 | -7.3907
509 | R-11 | 60.8 | 11.09 | -3.61 | -7.35
510 | R-11 | 60.9 | 11.11 | -3.59 | -7.3092
511 | R-11 | 61 | 11.14 | -3.56 | -7.2482
512 | R-11 | 61.1 | 11.16 | -3.54 | -7.2074
513 | R-11 | 61.2 | 11.18 | -3.52 | -7.1667
514 | R-11 | 61.3 | 11.21 | -3.49 | -7.1056
515 | R-11 | 61.4 | 11.23 | -3.47 | -7.0649
516 | R-11 | 61.5 | 11.25 | -3.45 | -7.0242
517 | R-11 | 61.6 | 11.28 | -3.42 | -6.9631
518 | R-11 | 61.7 | 11.3 | -3.4 | -6.9224
519 | R-11 | 61.8 | 11.32 | -3.38 | -6.8817
520 | R-11 | 61.9 | 11.35 | -3.35 | -6.8206
521 | R-11 | 62 | 11.37 | -3.33 | -6.7799
522 | R-11 | 62.1 | 11.4 | -3.3 | -6.7188
523 | R-11 | 62.2 | 11.42 | -3.28 | -6.6781
524 | R-11 | 62.3 | 11.44 | -3.26 | -6.6374
525 | R-11 | 62.4 | 11.47 | -3.23 | -6.5763
526 | R-11 | 62.5 | 11.49 | -3.21 | -6.5356
527 | R-11 | 62.6 | 11.51 | -3.19 | -6.4948
528 | R-11 | 62.7 | 11.54 | -3.16 | -6.4338
529 | R-11 | 62.8 | 11.56 | -3.14 | -6.393
530 | R-11 | 62.9 | 11.59 | -3.11 | -6.332
531 | R-11 | 63 | 11.61 | -3.09 | -6.2912
532 | R-11 | 63.1 | 11.63 | -3.07 | -6.2505
533 | R-11 | 63.2 | 11.66 | -3.04 | -6.1894
534 | R-11 | 63.3 | 11.68 | -3.02 | -6.1487
535 | R-11 | 63.4 | 11.71 | -2.99 | -6.0876
536 | R-11 | 63.5 | 11.73 | -2.97 | -6.0469
537 | R-11 | 63.6 | 11.76 | -2.94 | -5.9858
538 | R-11 | 63.7 | 11.78 | -2.92 | -5.9451
539 | R-11 | 63.8 | 11.8 | -2.9 | -5.9044
540 | R-11 | 63.9 | 11.83 | -2.87 | -5.8433
541 | R-11 | 64 | 11.85 | -2.85 | -5.8026
542 | R-11 | 64.1 | 11.88 | -2.82 | -5.7415
543 | R-11 | 64.2 | 11.9 | -2.8 | -5.7008
544 | R-11 | 64.3 | 11.93 | -2.77 | -5.6397
545 | R-11 | 64.4 | 11.95 | -2.75 | -5.599
546 | R-11 | 64.5 | 11.98 | -2.72 | -5.5379
547 | R-11 | 64.6 | 12 | -2.7 | -5.4972
548 | R-11 | 64.7 | 12.02 | -2.68 | -5.4565
549 | R-11 | 64.8 | 12.05 | -2.65 | -5.3954
550 | R-11 | 64.9 | 12.07 | -2.63 | -5.3547
551 | R-11 | 65 | 12.1 | -2.6 | -5.2936
552 | R-11 | 65.1 | 12.12 | -2.58 | -5.2529
553 | R-11 | 65.2 | 12.15 | -2.55 | -5.1918
554 | R-11 | 65.3 | 12.17 | -2.53 | -5.1511
555 | R-11 | 65.4 | 12.2 | -2.5 | -5.09
556 | R-11 | 65.5 | 12.22 | -2.48 | -5.0493
557 | R-11 | 65.6 | 12.25 | -2.45 | -4.9882
558 | R-11 | 65.7 | 12.27 | -2.43 | -4.9475
559 | R-11 | 65.8 | 12.3 | -2.4 | -4.8864
560 | R-11 | 65.9 | 12.32 | -2.38 | -4.8457
561 | R-11 | 66 | 12.35 | -2.35 | -4.7846
562 | R-11 | 66.1 | 12.37 | -2.33 | -4.7439
563 | R-11 | 66.2 | 12.4 | -2.3 | -4.6828
564 | R-11 | 66.3 | 12.43 | -2.27 | -4.6217
565 | R-11 | 66.4 | 12.45 | -2.25 | -4.581
566 | R-11 | 66.5 | 12.48 | -2.22 | -4.5199
567 | R-11 | 66.6 | 12.5 | -2.2 | -4.4792
568 | R-11 | 66.7 | 12.53 | -2.17 | -4.4181
569 | R-11 | 66.8 | 12.55 | -2.15 | -4.3774
570 | R-11 | 66.9 | 12.58 | -2.12 | -4.3163
571 | R-11 | 67 | 12.6 | -2.1 | -4.2756
572 | R-11 | 67.1 | 12.63 | -2.07 | -4.2145
573 | R-11 | 67.2 | 12.66 | -2.04 | -4.1534
574 | R-11 | 67.3 | 12.68 | -2.02 | -4.1127
575 | R-11 | 67.4 | 12.71 | -1.99 | -4.0516
576 | R-11 | 67.5 | 12.73 | -1.97 | -4.0109
577 | R-11 | 67.6 | 12.76 | -1.94 | -3.9498
578 | R-11 | 67.7 | 12.78 | -1.92 | -3.9091
579 | R-11 | 67.8 | 12.81 | -1.89 | -3.848
580 | R-11 | 67.9 | 12.84 | -1.86 | -3.787
581 | R-11 | 68 | 12.86 | -1.84 | -3.7462
582 | R-11 | 68.1 | 12.89 | -1.81 | -3.6852
583 | R-11 | 68.2 | 12.91 | -1.79 | -3.6444
584 | R-11 | 68.3 | 12.94 | -1.76 | -3.5834
585 | R-11 | 68.4 | 12.97 | -1.73 | -3.5223
586 | R-11 | 68.5 | 12.99 | -1.71 | -3.4816
587 | R-11 | 68.6 | 13.02 | -1.68 | -3.4205
588 | R-11 | 68.7 | 13.05 | -1.65 | -3.3594
589 | R-11 | 68.8 | 13.07 | -1.63 | -3.3187
590 | R-11 | 68.9 | 13.1 | -1.6 | -3.2576
591 | R-11 | 69 | 13.12 | -1.58 | -3.2169
592 | R-11 | 69.1 | 13.15 | -1.55 | -3.1558
593 | R-11 | 69.2 | 13.18 | -1.52 | -3.0947
594 | R-11 | 69.3 | 13.2 | -1.5 | -3.054
595 | R-11 | 69.4 | 13.23 | -1.47 | -2.9929
596 | R-11 | 69.5 | 13.26 | -1.44 | -2.9318
597 | R-11 | 69.6 | 13.28 | -1.42 | -2.8911
598 | R-11 | 69.7 | 13.31 | -1.39 | -2.83
599 | R-11 | 69.8 | 13.34 | -1.36 | -2.769
600 | R-11 | 69.9 | 13.36 | -1.34 | -2.7282
601 | R-11 | 70 | 13.39 | -1.31 | -2.6672
602 | R-11 | 70.1 | 13.42 | -1.28 | -2.6061
603 | R-11 | 70.2 | 13.45 | -1.25 | -2.545
604 | R-11 | 70.3 | 13.47 | -1.23 | -2.5043
605 | R-11 | 70.4 | 13.5 | -1.2 | -2.4432
606 | R-11 | 70.5 | 13.53 | -1.17 | -2.3821
607 | R-11 | 70.6 | 13.55 | -1.15 | -2.3414
608 | R-11 | 70.7 | 13.58 | -1.12 | -2.2803
609 | R-11 | 70.8 | 13.61 | -1.09 | -2.2192
610 | R-11 | 70.9 | 13.64 | -1.06 | -2.1582
611 | R-11 | 71 | 13.66 | -1.04 | -2.1174
612 | R-11 | 71.1 | 13.69 | -1.01 | -2.0564
613 | R-11 | 71.2 | 13.72 | -0.98 | -1.9953
614 | R-11 | 71.3 | 13.74 | -0.96 | -1.9546
615 | R-11 | 71.4 | 13.77 | -0.93 | -1.8935
616 | R-11 | 71.5 | 13.8 | -0.9 | -1.8324
617 | R-11 | 71.6 | 13.83 | -0.87 | -1.7713
618 | R-11 | 71.7 | 13.86 | -0.84 | -1.7102
619 | R-11 | 71.8 | 13.88 | -0.82 | -1.6695
620 | R-11 | 71.9 | 13.91 | -0.79 | -1.6084
621 | R-11 | 72 | 13.94 | -0.76 | -1.5474
622 | R-11 | 72.1 | 13.97 | -0.73 | -1.4863
623 | R-11 | 72.2 | 13.99 | -0.71 | -1.4456
624 | R-11 | 72.3 | 14.02 | -0.68 | -1.3845
625 | R-11 | 72.4 | 14.05 | -0.65 | -1.3234
626 | R-11 | 72.5 | 14.08 | -0.62 | -1.2623
627 | R-11 | 72.6 | 14.11 | -0.59 | -1.2012
628 | R-11 | 72.7 | 14.13 | -0.57 | -1.1605
629 | R-11 | 72.8 | 14.16 | -0.54 | -1.0994
630 | R-11 | 72.9 | 14.19 | -0.51 | -1.0384
631 | R-11 | 73 | 14.22 | -0.48 | -0.97728
632 | R-11 | 73.1 | 14.25 | -0.45 | -0.9162
633 | R-11 | 73.2 | 14.27 | -0.43 | -0.87548
634 | R-11 | 73.3 | 14.3 | -0.4 | -0.8144
635 | R-11 | 73.4 | 14.33 | -0.37 | -0.75332
636 | R-11 | 73.5 | 14.36 | -0.34 | -0.69224
637 | R-11 | 73.6 | 14.39 | -0.31 | -0.63116
638 | R-11 | 73.7 | 14.42 | -0.28 | -0.57008
639 | R-11 | 73.8 | 14.44 | -0.26 | -0.52936
640 | R-11 | 73.9 | 14.47 | -0.23 | -0.46828
641 | R-11 | 74 | 14.5 | -0.2 | -0.4072
642 | R-11 | 74.1 | 14.53 | -0.17 | -0.34612
643 | R-11 | 74.2 | 14.56 | -0.14 | -0.28504
644 | R-11 | 74.3 | 14.59 | -0.11 | -0.22396
645 | R-11 | 74.4 | 14.62 | -0.08 | -0.16288
646 | R-11 | 74.5 | 14.65 | -0.05 | -0.1018
647 | R-11 | 74.6 | 14.67 | -0.03 | -0.06108
648 | R-11 | 74.7 | 14.7 | 0 | 0
649 | R-11 | 74.8 | 14.73 | 0.03 | 0.06108
650 | R-11 | 74.9 | 14.76 | 0.06 | 0.12216
651 | R-11 | 75 | 14.79 | 0.09 | 0.18324
652 | R-11 | 75.1 | 14.82 | 0.12 | 0.24432
653 | R-11 | 75.2 | 14.85 | 0.15 | 0.3054
654 | R-11 | 75.3 | 14.88 | 0.18 | 0.36648
655 | R-11 | 75.4 | 14.91 | 0.21 | 0.42756
656 | R-11 | 75.5 | 14.94 | 0.24 | 0.48864
657 | R-11 | 75.6 | 14.97 | 0.27 | 0.54972
658 | R-11 | 75.7 | 14.99 | 0.29 | 0.59044
659 | R-11 | 75.8 | 15.02 | 0.32 | 0.65152
660 | R-11 | 75.9 | 15.05 | 0.35 | 0.7126
661 | R-11 | 76 | 15.08 | 0.38 | 0.77368
662 | R-11 | 76.1 | 15.11 | 0.41 | 0.83476
663 | R-11 | 76.2 | 15.14 | 0.44 | 0.89584
664 | R-11 | 76.3 | 15.17 | 0.47 | 0.95692
665 | R-11 | 76.4 | 15.2 | 0.5 | 1.018
666 | R-11 | 76.5 | 15.23 | 0.53 | 1.0791
667 | R-11 | 76.6 | 15.26 | 0.56 | 1.1402
668 | R-11 | 76.7 | 15.29 | 0.59 | 1.2012
669 | R-11 | 76.8 | 15.32 | 0.62 | 1.2623
670 | R-11 | 76.9 | 15.35 | 0.65 | 1.3234
671 | R-11 | 77 | 15.38 | 0.68 | 1.3845
672 | R-11 | 77.1 | 15.41 | 0.71 | 1.4456
673 | R-11 | 77.2 | 15.44 | 0.74 | 1.5066
674 | R-11 | 77.3 | 15.47 | 0.77 | 1.5677
675 | R-11 | 77.4 | 15.5 | 0.8 | 1.6288
676 | R-11 | 77.5 | 15.53 | 0.83 | 1.6899
677 | R-11 | 77.6 | 15.56 | 0.86 | 1.751
678 | R-11 | 77.7 | 15.59 | 0.89 | 1.812
679 | R-11 | 77.8 | 15.62 | 0.92 | 1.8731
680 | R-11 | 77.9 | 15.65 | 0.95 | 1.9342
681 | R-11 | 78 | 15.68 | 0.98 | 1.9953
682 | R-11 | 78.1 | 15.71 | 1.01 | 2.0564
683 | R-11 | 78.2 | 15.74 | 1.04 | 2.1174
684 | R-11 | 78.3 | 15.77 | 1.07 | 2.1785
685 | R-11 | 78.4 | 15.8 | 1.1 | 2.2396
686 | R-11 | 78.5 | 15.84 | 1.14 | 2.321
687 | R-11 | 78.6 | 15.87 | 1.17 | 2.3821
688 | R-11 | 78.7 | 15.9 | 1.2 | 2.4432
689 | R-11 | 78.8 | 15.93 | 1.23 | 2.5043
690 | R-11 | 78.9 | 15.96 | 1.26 | 2.5654
691 | R-11 | 79 | 15.99 | 1.29 | 2.6264
692 | R-11 | 79.1 | 16.02 | 1.32 | 2.6875
693 | R-11 | 79.2 | 16.05 | 1.35 | 2.7486
694 | R-11 | 79.3 | 16.08 | 1.38 | 2.8097
695 | R-11 | 79.4 | 16.11 | 1.41 | 2.8708
696 | R-11 | 79.5 | 16.14 | 1.44 | 2.9318
697 | R-11 | 79.6 | 16.18 | 1.48 | 3.0133
698 | R-11 | 79.7 | 16.21 | 1.51 | 3.0744
699 | R-11 | 79.8 | 16.24 | 1.54 | 3.1354
700 | R-11 | 79.9 | 16.27 | 1.57 | 3.1965
701 | R-11 | 80 | 16.3 | 1.6 | 3.2576
702 | R-11 | 80.1 | 16.33 | 1.63 | 3.3187
703 | R-11 | 80.2 | 16.36 | 1.66 | 3.3798
704 | R-11 | 80.3 | 16.4 | 1.7 | 3.4612
705 | R-11 | 80.4 | 16.43 | 1.73 | 3.5223
706 | R-11 | 80.5 | 16.46 | 1.76 | 3.5834
707 | R-11 | 80.6 | 16.49 | 1.79 | 3.6444
708 | R-11 | 80.7 | 16.52 | 1.82 | 3.7055
709 | R-11 | 80.8 | 16.55 | 1.85 | 3.7666
710 | R-11 | 80.9 | 16.58 | 1.88 | 3.8277
711 | R-11 | 81 | 16.62 | 1.92 | 3.9091
712 | R-11 | 81.1 | 16.65 | 1.95 | 3.9702
713 | R-11 | 81.2 | 16.68 | 1.98 | 4.0313
714 | R-11 | 81.3 | 16.71 | 2.01 | 4.0924
715 | R-11 | 81.4 | 16.74 | 2.04 | 4.1534
716 | R-11 | 81.5 | 16.78 | 2.08 | 4.2349
717 | R-11 | 81.6 | 16.81 | 2.11 | 4.296
718 | R-11 | 81.7 | 16.84 | 2.14 | 4.357
719 | R-11 | 81.8 | 16.87 | 2.17 | 4.4181
720 | R-11 | 81.9 | 16.91 | 2.21 | 4.4996
721 | R-11 | 82 | 16.94 | 2.24 | 4.5606
722 | R-11 | 82.1 | 16.97 | 2.27 | 4.6217
723 | R-11 | 82.2 | 17 | 2.3 | 4.6828
724 | R-11 | 82.3 | 17.03 | 2.33 | 4.7439
725 | R-11 | 82.4 | 17.07 | 2.37 | 4.8253
726 | R-11 | 82.5 | 17.1 | 2.4 | 4.8864
727 | R-11 | 82.6 | 17.13 | 2.43 | 4.9475
728 | R-11 | 82.7 | 17.16 | 2.46 | 5.0086
729 | R-11 | 82.8 | 17.2 | 2.5 | 5.09
730 | R-11 | 82.9 | 17.23 | 2.53 | 5.1511
731 | R-11 | 83 | 17.26 | 2.56 | 5.2122
732 | R-11 | 83.1 | 17.3 | 2.6 | 5.2936
733 | R-11 | 83.2 | 17.33 | 2.63 | 5.3547
734 | R-11 | 83.3 | 17.36 | 2.66 | 5.4158
735 | R-11 | 83.4 | 17.39 | 2.69 | 5.4768
736 | R-11 | 83.5 | 17.43 | 2.73 | 5.5583
737 | R-11 | 83.6 | 17.46 | 2.76 | 5.6194
738 | R-11 | 83.7 | 17.49 | 2.79 | 5.6804
739 | R-11 | 83.8 | 17.53 | 2.83 | 5.7619
740 | R-11 | 83.9 | 17.56 | 2.86 | 5.823
741 | R-11 | 84 | 17.59 | 2.89 | 5.884
742 | R-11 | 84.1 | 17.63 | 2.93 | 5.9655
743 | R-11 | 84.2 | 17.66 | 2.96 | 6.0266
744 | R-11 | 84.3 | 17.69 | 2.99 | 6.0876
745 | R-11 | 84.4 | 17.73 | 3.03 | 6.1691
746 | R-11 | 84.5 | 17.76 | 3.06 | 6.2302
747 | R-11 | 84.6 | 17.79 | 3.09 | 6.2912
748 | R-11 | 84.7 | 17.83 | 3.13 | 6.3727
749 | R-11 | 84.8 | 17.86 | 3.16 | 6.4338
750 | R-11 | 84.9 | 17.9 | 3.2 | 6.5152
751 | R-11 | 85 | 17.93 | 3.23 | 6.5763
752 | R-11 | 85.1 | 17.96 | 3.26 | 6.6374
753 | R-11 | 85.2 | 18 | 3.3 | 6.7188
754 | R-11 | 85.3 | 18.03 | 3.33 | 6.7799
755 | R-11 | 85.4 | 18.06 | 3.36 | 6.841
756 | R-11 | 85.5 | 18.1 | 3.4 | 6.9224
757 | R-11 | 85.6 | 18.13 | 3.43 | 6.9835
758 | R-11 | 85.7 | 18.17 | 3.47 | 7.0649
759 | R-11 | 85.8 | 18.2 | 3.5 | 7.126
760 | R-11 | 85.9 | 18.23 | 3.53 | 7.1871
761 | R-11 | 86 | 18.27 | 3.57 | 7.2685
762 | R-11 | 86.1 | 18.3 | 3.6 | 7.3296
763 | R-11 | 86.2 | 18.34 | 3.64 | 7.411
764 | R-11 | 86.3 | 18.37 | 3.67 | 7.4721
765 | R-11 | 86.4 | 18.41 | 3.71 | 7.5536
766 | R-11 | 86.5 | 18.44 | 3.74 | 7.6146
767 | R-11 | 86.6 | 18.48 | 3.78 | 7.6961
768 | R-11 | 86.7 | 18.51 | 3.81 | 7.7572
769 | R-11 | 86.8 | 18.54 | 3.84 | 7.8182
770 | R-11 | 86.9 | 18.58 | 3.88 | 7.8997
771 | R-11 | 87 | 18.61 | 3.91 | 7.9608
772 | R-11 | 87.1 | 18.65 | 3.95 | 8.0422
773 | R-11 | 87.2 | 18.68 | 3.98 | 8.1033
774 | R-11 | 87.3 | 18.72 | 4.02 | 8.1847
775 | R-11 | 87.4 | 18.75 | 4.05 | 8.2458
776 | R-11 | 87.5 | 18.79 | 4.09 | 8.3272
777 | R-11 | 87.6 | 18.82 | 4.12 | 8.3883
778 | R-11 | 87.7 | 18.86 | 4.16 | 8.4698
779 | R-11 | 87.8 | 18.89 | 4.19 | 8.5308
780 | R-11 | 87.9 | 18.93 | 4.23 | 8.6123
781 | R-11 | 88 | 18.96 | 4.26 | 8.6734
782 | R-11 | 88.1 | 19 | 4.3 | 8.7548
783 | R-11 | 88.2 | 19.04 | 4.34 | 8.8362
784 | R-11 | 88.3 | 19.07 | 4.37 | 8.8973
785 | R-11 | 88.4 | 19.11 | 4.41 | 8.9788
786 | R-11 | 88.5 | 19.14 | 4.44 | 9.0398
787 | R-11 | 88.6 | 19.18 | 4.48 | 9.1213
788 | R-11 | 88.7 | 19.21 | 4.51 | 9.1824
789 | R-11 | 88.8 | 19.25 | 4.55 | 9.2638
790 | R-11 | 88.9 | 19.28 | 4.58 | 9.3249
791 | R-11 | 89 | 19.32 | 4.62 | 9.4063
792 | R-11 | 89.1 | 19.36 | 4.66 | 9.4878
793 | R-11 | 89.2 | 19.39 | 4.69 | 9.5488
794 | R-11 | 89.3 | 19.43 | 4.73 | 9.6303
795 | R-11 | 89.4 | 19.46 | 4.76 | 9.6914
796 | R-11 | 89.5 | 19.5 | 4.8 | 9.7728
797 | R-11 | 89.6 | 19.54 | 4.84 | 9.8542
798 | R-11 | 89.7 | 19.57 | 4.87 | 9.9153
799 | R-11 | 89.8 | 19.61 | 4.91 | 9.9968
800 | R-11 | 89.9 | 19.64 | 4.94 | 10.0578
801 | R-11 | 90 | 19.68 | 4.98 | 10.1393
802 | R-11 | 90.1 | 19.72 | 5.02 | 10.2207
803 | R-11 | 90.2 | 19.75 | 5.05 | 10.2818
804 | R-11 | 90.3 | 19.79 | 5.09 | 10.3632
805 | R-11 | 90.4 | 19.83 | 5.13 | 10.4447
806 | R-11 | 90.5 | 19.86 | 5.16 | 10.5058
807 | R-11 | 90.6 | 19.9 | 5.2 | 10.5872
808 | R-11 | 90.7 | 19.94 | 5.24 | 10.6686
809 | R-11 | 90.8 | 19.97 | 5.27 | 10.7297
810 | R-11 | 90.9 | 20.01 | 5.31 | 10.8112
811 | R-11 | 91 | 20.05 | 5.35 | 10.8926
812 | R-11 | 91.1 | 20.08 | 5.38 | 10.9537
813 | R-11 | 91.2 | 20.12 | 5.42 | 11.0351
814 | R-11 | 91.3 | 20.16 | 5.46 | 11.1166
815 | R-11 | 91.4 | 20.19 | 5.49 | 11.1776
816 | R-11 | 91.5 | 20.23 | 5.53 | 11.2591
817 | R-11 | 91.6 | 20.27 | 5.57 | 11.3405
818 | R-11 | 91.7 | 20.31 | 5.61 | 11.422
819 | R-11 | 91.8 | 20.34 | 5.64 | 11.483
820 | R-11 | 91.9 | 20.38 | 5.68 | 11.5645
821 | R-11 | 92 | 20.42 | 5.72 | 11.6459
822 | R-11 | 92.1 | 20.46 | 5.76 | 11.7274
823 | R-11 | 92.2 | 20.49 | 5.79 | 11.7884
824 | R-11 | 92.3 | 20.53 | 5.83 | 11.8699
825 | R-11 | 92.4 | 20.57 | 5.87 | 11.9513
826 | R-11 | 92.5 | 20.61 | 5.91 | 12.0328
827 | R-11 | 92.6 | 20.64 | 5.94 | 12.0938
828 | R-11 | 92.7 | 20.68 | 5.98 | 12.1753
829 | R-11 | 92.8 | 20.72 | 6.02 | 12.2567
830 | R-11 | 92.9 | 20.76 | 6.06 | 12.3382
831 | R-11 | 93 | 20.79 | 6.09 | 12.3992
832 | R-11 | 93.1 | 20.83 | 6.13 | 12.4807
833 | R-11 | 93.2 | 20.87 | 6.17 | 12.5621
834 | R-11 | 93.3 | 20.91 | 6.21 | 12.6436
835 | R-11 | 93.4 | 20.95 | 6.25 | 12.725
836 | R-11 | 93.5 | 20.98 | 6.28 | 12.7861
837 | R-11 | 93.6 | 21.02 | 6.32 | 12.8675
838 | R-11 | 93.7 | 21.06 | 6.36 | 12.949
839 | R-11 | 93.8 | 21.1 | 6.4 | 13.0304
840 | R-11 | 93.9 | 21.14 | 6.44 | 13.1118
841 | R-11 | 94 | 21.18 | 6.48 | 13.1933
842 | R-11 | 94.1 | 21.21 | 6.51 | 13.2544
843 | R-11 | 94.2 | 21.25 | 6.55 | 13.3358
844 | R-11 | 94.3 | 21.29 | 6.59 | 13.4172
845 | R-11 | 94.4 | 21.33 | 6.63 | 13.4987
846 | R-11 | 94.5 | 21.37 | 6.67 | 13.5801
847 | R-11 | 94.6 | 21.41 | 6.71 | 13.6616
848 | R-11 | 94.7 | 21.45 | 6.75 | 13.743
849 | R-11 | 94.8 | 21.48 | 6.78 | 13.8041
850 | R-11 | 94.9 | 21.52 | 6.82 | 13.8855
851 | R-11 | 95 | 21.56 | 6.86 | 13.967
852 | R-11 | 95.1 | 21.6 | 6.9 | 14.0484
853 | R-11 | 95.2 | 21.64 | 6.94 | 14.1298
854 | R-11 | 95.3 | 21.68 | 6.98 | 14.2113
855 | R-11 | 95.4 | 21.72 | 7.02 | 14.2927
856 | R-11 | 95.5 | 21.76 | 7.06 | 14.3742
857 | R-11 | 95.6 | 21.8 | 7.1 | 14.4556
858 | R-11 | 95.7 | 21.84 | 7.14 | 14.537
859 | R-11 | 95.8 | 21.88 | 7.18 | 14.6185
860 | R-11 | 95.9 | 21.92 | 7.22 | 14.6999
861 | R-11 | 96 | 21.96 | 7.26 | 14.7814
862 | R-11 | 96.1 | 21.99 | 7.29 | 14.8424
863 | R-11 | 96.2 | 22.03 | 7.33 | 14.9239
864 | R-11 | 96.3 | 22.07 | 7.37 | 15.0053
865 | R-11 | 96.4 | 22.11 | 7.41 | 15.0868
866 | R-11 | 96.5 | 22.15 | 7.45 | 15.1682
867 | R-11 | 96.6 | 22.19 | 7.49 | 15.2496
868 | R-11 | 96.7 | 22.23 | 7.53 | 15.3311
869 | R-11 | 96.8 | 22.27 | 7.57 | 15.4125
870 | R-11 | 96.9 | 22.31 | 7.61 | 15.494
871 | R-11 | 97 | 22.35 | 7.65 | 15.5754
872 | R-11 | 97.1 | 22.39 | 7.69 | 15.6568
873 | R-11 | 97.2 | 22.43 | 7.73 | 15.7383
874 | R-11 | 97.3 | 22.47 | 7.77 | 15.8197
875 | R-11 | 97.4 | 22.51 | 7.81 | 15.9012
876 | R-11 | 97.5 | 22.55 | 7.85 | 15.9826
877 | R-11 | 97.6 | 22.6 | 7.9 | 16.0844
878 | R-11 | 97.7 | 22.64 | 7.94 | 16.1658
879 | R-11 | 97.8 | 22.68 | 7.98 | 16.2473
880 | R-11 | 97.9 | 22.72 | 8.02 | 16.3287
881 | R-11 | 98 | 22.76 | 8.06 | 16.4102
882 | R-11 | 98.1 | 22.8 | 8.1 | 16.4916
883 | R-11 | 98.2 | 22.84 | 8.14 | 16.573
884 | R-11 | 98.3 | 22.88 | 8.18 | 16.6545
885 | R-11 | 98.4 | 22.92 | 8.22 | 16.7359
886 | R-11 | 98.5 | 22.96 | 8.26 | 16.8174
887 | R-11 | 98.6 | 23 | 8.3 | 16.8988
888 | R-11 | 98.7 | 23.04 | 8.34 | 16.9802
889 | R-11 | 98.8 | 23.08 | 8.38 | 17.0617
890 | R-11 | 98.9 | 23.13 | 8.43 | 17.1635
891 | R-11 | 99 | 23.17 | 8.47 | 17.2449
892 | R-11 | 99.1 | 23.21 | 8.51 | 17.3264
893 | R-11 | 99.2 | 23.25 | 8.55 | 17.4078
894 | R-11 | 99.3 | 23.29 | 8.59 | 17.4892
895 | R-11 | 99.4 | 23.33 | 8.63 | 17.5707
896 | R-11 | 99.5 | 23.37 | 8.67 | 17.6521
897 | R-11 | 99.6 | 23.41 | 8.71 | 17.7336
898 | R-11 | 99.7 | 23.46 | 8.76 | 17.8354
899 | R-11 | 99.8 | 23.5 | 8.8 | 17.9168
900 | R-11 | 99.9 | 23.54 | 8.84 | 17.9982
901 | R-11 | 100 | 23.58 | 8.88 | 18.0797
902 | R-11 | 100.1 | 23.62 | 8.92 | 18.1611
903 | R-11 | 100.2 | 23.66 | 8.96 | 18.2426
904 | R-11 | 100.3 | 23.71 | 9.01 | 18.3444
905 | R-11 | 100.4 | 23.75 | 9.05 | 18.4258
906 | R-11 | 100.5 | 23.79 | 9.09 | 18.5072
907 | R-11 | 100.6 | 23.83 | 9.13 | 18.5887
908 | R-11 | 100.7 | 23.88 | 9.18 | 18.6905
909 | R-11 | 100.8 | 23.92 | 9.22 | 18.7719
910 | R-11 | 100.9 | 23.96 | 9.26 | 18.8534
911 | R-11 | 101 | 24 | 9.3 | 18.9348
912 | R-11 | 101.1 | 24.04 | 9.34 | 19.0162
913 | R-11 | 101.2 | 24.09 | 9.39 | 19.118
914 | R-11 | 101.3 | 24.13 | 9.43 | 19.1995
915 | R-11 | 101.4 | 24.17 | 9.47 | 19.2809
916 | R-11 | 101.5 | 24.21 | 9.51 | 19.3624
917 | R-11 | 101.6 | 24.26 | 9.56 | 19.4642
918 | R-11 | 101.7 | 24.3 | 9.6 | 19.5456
919 | R-11 | 101.8 | 24.34 | 9.64 | 19.627
920 | R-11 | 101.9 | 24.39 | 9.69 | 19.7288
921 | R-11 | 102 | 24.43 | 9.73 | 19.8103
922 | R-11 | 102.1 | 24.47 | 9.77 | 19.8917
923 | R-11 | 102.2 | 24.51 | 9.81 | 19.9732
924 | R-11 | 102.3 | 24.56 | 9.86 | 20.075
925 | R-11 | 102.4 | 24.6 | 9.9 | 20.1564
926 | R-11 | 102.5 | 24.64 | 9.94 | 20.2378
927 | R-11 | 102.6 | 24.69 | 9.99 | 20.3396
928 | R-11 | 102.7 | 24.73 | 10.03 | 20.4211
929 | R-11 | 102.8 | 24.77 | 10.07 | 20.5025
930 | R-11 | 102.9 | 24.82 | 10.12 | 20.6043
931 | R-11 | 103 | 24.86 | 10.16 | 20.6858
932 | R-11 | 103.1 | 24.9 | 10.2 | 20.7672
933 | R-11 | 103.2 | 24.95 | 10.25 | 20.869
934 | R-11 | 103.3 | 24.99 | 10.29 | 20.9504
935 | R-11 | 103.4 | 25.04 | 10.34 | 21.0522
936 | R-11 | 103.5 | 25.08 | 10.38 | 21.1337
937 | R-11 | 103.6 | 25.12 | 10.42 | 21.2151
938 | R-11 | 103.7 | 25.17 | 10.47 | 21.3169
939 | R-11 | 103.8 | 25.21 | 10.51 | 21.3984
940 | R-11 | 103.9 | 25.25 | 10.55 | 21.4798
941 | R-11 | 104 | 25.3 | 10.6 | 21.5816
942 | R-11 | 104.1 | 25.34 | 10.64 | 21.663
943 | R-11 | 104.2 | 25.39 | 10.69 | 21.7648
944 | R-11 | 104.3 | 25.43 | 10.73 | 21.8463
945 | R-11 | 104.4 | 25.48 | 10.78 | 21.9481
946 | R-11 | 104.5 | 25.52 | 10.82 | 22.0295
947 | R-11 | 104.6 | 25.56 | 10.86 | 22.111
948 | R-11 | 104.7 | 25.61 | 10.91 | 22.2128
949 | R-11 | 104.8 | 25.65 | 10.95 | 22.2942
950 | R-11 | 104.9 | 25.7 | 11 | 22.396
951 | R-11 | 105 | 25.74 | 11.04 | 22.4774
952 | R-11 | 105.1 | 25.79 | 11.09 | 22.5792
953 | R-11 | 105.2 | 25.83 | 11.13 | 22.6607
954 | R-11 | 105.3 | 25.88 | 11.18 | 22.7625
955 | R-11 | 105.4 | 25.92 | 11.22 | 22.8439
956 | R-11 | 105.5 | 25.97 | 11.27 | 22.9457
957 | R-11 | 105.6 | 26.01 | 11.31 | 23.0272
958 | R-11 | 105.7 | 26.06 | 11.36 | 23.129
959 | R-11 | 105.8 | 26.1 | 11.4 | 23.2104
960 | R-11 | 105.9 | 26.15 | 11.45 | 23.3122
961 | R-11 | 106 | 26.19 | 11.49 | 23.3936
962 | R-11 | 106.1 | 26.24 | 11.54 | 23.4954
963 | R-11 | 106.2 | 26.28 | 11.58 | 23.5769
964 | R-11 | 106.3 | 26.33 | 11.63 | 23.6787
965 | R-11 | 106.4 | 26.37 | 11.67 | 23.7601
966 | R-11 | 106.5 | 26.42 | 11.72 | 23.8619
967 | R-11 | 106.6 | 26.47 | 11.77 | 23.9637
968 | R-11 | 106.7 | 26.51 | 11.81 | 24.0452
969 | R-11 | 106.8 | 26.56 | 11.86 | 24.147
970 | R-11 | 106.9 | 26.6 | 11.9 | 24.2284
971 | R-11 | 107 | 26.65 | 11.95 | 24.3302
972 | R-11 | 107.1 | 26.69 | 11.99 | 24.4116
973 | R-11 | 107.2 | 26.74 | 12.04 | 24.5134
974 | R-11 | 107.3 | 26.79 | 12.09 | 24.6152
975 | R-11 | 107.4 | 26.83 | 12.13 | 24.6967
976 | R-11 | 107.5 | 26.88 | 12.18 | 24.7985
977 | R-11 | 107.6 | 26.93 | 12.23 | 24.9003
978 | R-11 | 107.7 | 26.97 | 12.27 | 24.9817
979 | R-11 | 107.8 | 27.02 | 12.32 | 25.0835
980 | R-11 | 107.9 | 27.06 | 12.36 | 25.165
981 | R-11 | 108 | 27.11 | 12.41 | 25.2668
982 | R-11 | 108.1 | 27.16 | 12.46 | 25.3686
983 | R-11 | 108.2 | 27.2 | 12.5 | 25.45
984 | R-11 | 108.3 | 27.25 | 12.55 | 25.5518
985 | R-11 | 108.4 | 27.3 | 12.6 | 25.6536
986 | R-11 | 108.5 | 27.34 | 12.64 | 25.735
987 | R-11 | 108.6 | 27.39 | 12.69 | 25.8368
988 | R-11 | 108.7 | 27.44 | 12.74 | 25.9386
989 | R-11 | 108.8 | 27.48 | 12.78 | 26.0201
990 | R-11 | 108.9 | 27.53 | 12.83 | 26.1219
991 | R-11 | 109 | 27.58 | 12.88 | 26.2237
992 | R-11 | 109.1 | 27.63 | 12.93 | 26.3255
993 | R-11 | 109.2 | 27.67 | 12.97 | 26.4069
994 | R-11 | 109.3 | 27.72 | 13.02 | 26.5087
995 | R-11 | 109.4 | 27.77 | 13.07 | 26.6105
996 | R-11 | 109.5 | 27.82 | 13.12 | 26.7123
997 | R-11 | 109.6 | 27.86 | 13.16 | 26.7938
998 | R-11 | 109.7 | 27.91 | 13.21 | 26.8956
999 | R-11 | 109.8 | 27.96 | 13.26 | 26.9974
1000 | R-11 | 109.9 | 28.01 | 13.31 | 27.0992
1001 | R-11 | 110 | 28.05 | 13.35 | 27.1806
1002 | R-11 | 110.1 | 28.1 | 13.4 | 27.2824
1003 | R-11 | 110.2 | 28.15 | 13.45 | 27.3842
1004 | R-11 | 110.3 | 28.2 | 13.5 | 27.486
1005 | R-11 | 110.4 | 28.24 | 13.54 | 27.5674
1006 | R-11 | 110.5 | 28.29 | 13.59 | 27.6692
1007 | R-11 | 110.6 | 28.34 | 13.64 | 27.771
1008 | R-11 | 110.7 | 28.39 | 13.69 | 27.8728
1009 | R-11 | 110.8 | 28.44 | 13.74 | 27.9746
1010 | R-11 | 110.9 | 28.49 | 13.79 | 28.0764
1011 | R-11 | 111 | 28.53 | 13.83 | 28.1579
1012 | R-11 | 111.1 | 28.58 | 13.88 | 28.2597
1013 | R-11 | 111.2 | 28.63 | 13.93 | 28.3615
1014 | R-11 | 111.3 | 28.68 | 13.98 | 28.4633
1015 | R-11 | 111.4 | 28.73 | 14.03 | 28.5651
1016 | R-11 | 111.5 | 28.78 | 14.08 | 28.6669
1017 | R-11 | 111.6 | 28.83 | 14.13 | 28.7687
1018 | R-11 | 111.7 | 28.87 | 14.17 | 28.8501
1019 | R-11 | 111.8 | 28.92 | 14.22 | 28.9519
1020 | R-11 | 111.9 | 28.97 | 14.27 | 29.0537
1021 | R-11 | 112 | 29.02 | 14.32 | 29.1555
1022 | R-11 | 112.1 | 29.07 | 14.37 | 29.2573
1023 | R-11 | 112.2 | 29.12 | 14.42 | 29.3591
1024 | R-11 | 112.3 | 29.17 | 14.47 | 29.4609
1025 | R-11 | 112.4 | 29.22 | 14.52 | 29.5627
1026 | R-11 | 112.5 | 29.27 | 14.57 | 29.6645
1027 | R-11 | 112.6 | 29.32 | 14.62 | 29.7663
1028 | R-11 | 112.7 | 29.37 | 14.67 | 29.8681
1029 | R-11 | 112.8 | 29.42 | 14.72 | 29.9699
1030 | R-11 | 112.9 | 29.46 | 14.76 | 30.0514
1031 | R-11 | 113 | 29.51 | 14.81 | 30.1532
1032 | R-11 | 113.1 | 29.56 | 14.86 | 30.255
1033 | R-11 | 113.2 | 29.61 | 14.91 | 30.3568
1034 | R-11 | 113.3 | 29.66 | 14.96 | 30.4586
1035 | R-11 | 113.4 | 29.71 | 15.01 | 30.5604
1036 | R-11 | 113.5 | 29.76 | 15.06 | 30.6622
1037 | R-11 | 113.6 | 29.81 | 15.11 | 30.764
1038 | R-11 | 113.7 | 29.86 | 15.16 | 30.8658
1039 | R-11 | 113.8 | 29.91 | 15.21 | 30.9676
1040 | R-11 | 113.9 | 29.96 | 15.26 | 31.0694
1041 | R-11 | 114 | 30.01 | 15.31 | 31.1712
1042 | R-11 | 114.1 | 30.06 | 15.36 | 31.273
1043 | R-11 | 114.2 | 30.11 | 15.41 | 31.3748
1044 | R-11 | 114.3 | 30.17 | 15.47 | 31.4969
1045 | R-11 | 114.4 | 30.22 | 15.52 | 31.5987
1046 | R-11 | 114.5 | 30.27 | 15.57 | 31.7005
1047 | R-11 | 114.6 | 30.32 | 15.62 | 31.8023
1048 | R-11 | 114.7 | 30.37 | 15.67 | 31.9041
1049 | R-11 | 114.8 | 30.42 | 15.72 | 32.0059
1050 | R-11 | 114.9 | 30.47 | 15.77 | 32.1077
1051 | R-11 | 115 | 30.52 | 15.82 | 32.2095
1052 | R-11 | 115.1 | 30.57 | 15.87 | 32.3113
1053 | R-11 | 115.2 | 30.62 | 15.92 | 32.4131
1054 | R-11 | 115.3 | 30.67 | 15.97 | 32.5149
1055 | R-11 | 115.4 | 30.72 | 16.02 | 32.6167
1056 | R-11 | 115.5 | 30.78 | 16.08 | 32.7389
1057 | R-11 | 115.6 | 30.83 | 16.13 | 32.8407
1058 | R-11 | 115.7 | 30.88 | 16.18 | 32.9425
1059 | R-11 | 115.8 | 30.93 | 16.23 | 33.0443
1060 | R-11 | 115.9 | 30.98 | 16.28 | 33.1461
1061 | R-11 | 116 | 31.03 | 16.33 | 33.2479
1062 | R-11 | 116.1 | 31.08 | 16.38 | 33.3497
1063 | R-11 | 116.2 | 31.14 | 16.44 | 33.4718
1064 | R-11 | 116.3 | 31.19 | 16.49 | 33.5736
1065 | R-11 | 116.4 | 31.24 | 16.54 | 33.6754
1066 | R-11 | 116.5 | 31.29 | 16.59 | 33.7772
1067 | R-11 | 116.6 | 31.34 | 16.64 | 33.879
1068 | R-11 | 116.7 | 31.4 | 16.7 | 34.0012
1069 | R-11 | 116.8 | 31.45 | 16.75 | 34.103
1070 | R-11 | 116.9 | 31.5 | 16.8 | 34.2048
1071 | R-11 | 117 | 31.55 | 16.85 | 34.3066
1072 | R-11 | 117.1 | 31.6 | 16.9 | 34.4084
1073 | R-11 | 117.2 | 31.66 | 16.96 | 34.5306
1074 | R-11 | 117.3 | 31.71 | 17.01 | 34.6324
1075 | R-11 | 117.4 | 31.76 | 17.06 | 34.7342
1076 | R-11 | 117.5 | 31.81 | 17.11 | 34.836
1077 | R-11 | 117.6 | 31.87 | 17.17 | 34.9581
1078 | R-11 | 117.7 | 31.92 | 17.22 | 35.0599
1079 | R-11 | 117.8 | 31.97 | 17.27 | 35.1617
1080 | R-11 | 117.9 | 32.03 | 17.33 | 35.2839
1081 | R-11 | 118 | 32.08 | 17.38 | 35.3857
1082 | R-11 | 118.1 | 32.13 | 17.43 | 35.4875
1083 | R-11 | 118.2 | 32.18 | 17.48 | 35.5893
1084 | R-11 | 118.3 | 32.24 | 17.54 | 35.7114
1085 | R-11 | 118.4 | 32.29 | 17.59 | 35.8132
1086 | R-11 | 118.5 | 32.34 | 17.64 | 35.915
1087 | R-11 | 118.6 | 32.4 | 17.7 | 36.0372
1088 | R-11 | 118.7 | 32.45 | 17.75 | 36.139
1089 | R-11 | 118.8 | 32.5 | 17.8 | 36.2408
1090 | R-11 | 118.9 | 32.56 | 17.86 | 36.363
1091 | R-11 | 119 | 32.61 | 17.91 | 36.4648
1092 | R-11 | 119.1 | 32.66 | 17.96 | 36.5666
1093 | R-11 | 119.2 | 32.72 | 18.02 | 36.6887
1094 | R-11 | 119.3 | 32.77 | 18.07 | 36.7905
1095 | R-11 | 119.4 | 32.83 | 18.13 | 36.9127
1096 | R-11 | 119.5 | 32.88 | 18.18 | 37.0145
1097 | R-11 | 119.6 | 32.93 | 18.23 | 37.1163
1098 | R-11 | 119.7 | 32.99 | 18.29 | 37.2384
1099 | R-11 | 119.8 | 33.04 | 18.34 | 37.3402
1100 | R-11 | 119.9 | 33.1 | 18.4 | 37.4624
1101 | R-11 | 120 | 33.15 | 18.45 | 37.5642
1102 | R-113 | 10 | 1.17 | -13.53 | -27.5532
1103 | R-113 | 10.1 | 1.17 | -13.53 | -27.5471
1104 | R-113 | 10.2 | 1.17 | -13.53 | -27.5389
1105 | R-113 | 10.3 | 1.18 | -13.52 | -27.5328
1106 | R-113 | 10.4 | 1.18 | -13.52 | -27.5247
1107 | R-113 | 10.5 | 1.18 | -13.52 | -27.5186
1108 | R-113 | 10.6 | 1.19 | -13.51 | -27.5104
1109 | R-113 | 10.7 | 1.19 | -13.51 | -27.5043
1110 | R-113 | 10.8 | 1.2 | -13.51 | -27.4962
1111 | R-113 | 10.9 | 1.2 | -13.5 | -27.488
1112 | R-113 | 11 | 1.2 | -13.5 | -27.4819
1113 | R-113 | 11.1 | 1.21 | -13.49 | -27.4738
1114 | R-113 | 11.2 | 1.21 | -13.49 | -27.4677
1115 | R-113 | 11.3 | 1.21 | -13.49 | -27.4595
1116 | R-113 | 11.4 | 1.22 | -13.48 | -27.4514
1117 | R-113 | 11.5 | 1.22 | -13.48 | -27.4453
1118 | R-113 | 11.6 | 1.22 | -13.48 | -27.4371
1119 | R-113 | 11.7 | 1.23 | -13.47 | -27.429
1120 | R-113 | 11.8 | 1.23 | -13.47 | -27.4229
1121 | R-113 | 11.9 | 1.24 | -13.46 | -27.4147
1122 | R-113 | 12 | 1.24 | -13.46 | -27.4066
1123 | R-113 | 12.1 | 1.24 | -13.46 | -27.4005
1124 | R-113 | 12.2 | 1.25 | -13.45 | -27.3923
1125 | R-113 | 12.3 | 1.25 | -13.45 | -27.3842
1126 | R-113 | 12.4 | 1.25 | -13.45 | -27.3781
1127 | R-113 | 12.5 | 1.26 | -13.44 | -27.3699
1128 | R-113 | 12.6 | 1.26 | -13.44 | -27.3618
1129 | R-113 | 12.7 | 1.27 | -13.44 | -27.3537
1130 | R-113 | 12.8 | 1.27 | -13.43 | -27.3475
1131 | R-113 | 12.9 | 1.27 | -13.43 | -27.3394
1132 | R-113 | 13 | 1.28 | -13.42 | -27.3313
1133 | R-113 | 13.1 | 1.28 | -13.42 | -27.3231
1134 | R-113 | 13.2 | 1.28 | -13.42 | -27.317
1135 | R-113 | 13.3 | 1.29 | -13.41 | -27.3089
1136 | R-113 | 13.4 | 1.29 | -13.41 | -27.3007
1137 | R-113 | 13.5 | 1.29 | -13.41 | -27.2926
1138 | R-113 | 13.6 | 1.3 | -13.4 | -27.2844
1139 | R-113 | 13.7 | 1.3 | -13.4 | -27.2763
1140 | R-113 | 13.8 | 1.31 | -13.39 | -27.2702
1141 | R-113 | 13.9 | 1.31 | -13.39 | -27.262
1142 | R-113 | 14 | 1.31 | -13.39 | -27.2539
1143 | R-113 | 14.1 | 1.32 | -13.38 | -27.2458
1144 | R-113 | 14.2 | 1.32 | -13.38 | -27.2376
1145 | R-113 | 14.3 | 1.33 | -13.37 | -27.2295
1146 | R-113 | 14.4 | 1.33 | -13.37 | -27.2213
1147 | R-113 | 14.5 | 1.33 | -13.37 | -27.2132
1148 | R-113 | 14.6 | 1.34 | -13.36 | -27.2071
1149 | R-113 | 14.7 | 1.34 | -13.36 | -27.1989
1150 | R-113 | 14.8 | 1.35 | -13.36 | -27.1908
1151 | R-113 | 14.9 | 1.35 | -13.35 | -27.1826
1152 | R-113 | 15 | 1.35 | -13.35 | -27.1745
1153 | R-113 | 15.1 | 1.36 | -13.34 | -27.1664
1154 | R-113 | 15.2 | 1.36 | -13.34 | -27.1582
1155 | R-113 | 15.3 | 1.37 | -13.34 | -27.1501
1156 | R-113 | 15.4 | 1.37 | -13.33 | -27.1419
1157 | R-113 | 15.5 | 1.37 | -13.33 | -27.1338
1158 | R-113 | 15.6 | 1.38 | -13.32 | -27.1256
1159 | R-113 | 15.7 | 1.38 | -13.32 | -27.1175
1160 | R-113 | 15.8 | 1.39 | -13.31 | -27.1093
1161 | R-113 | 15.9 | 1.39 | -13.31 | -27.1012
1162 | R-113 | 16 | 1.39 | -13.31 | -27.0931
1163 | R-113 | 16.1 | 1.4 | -13.3 | -27.0849
1164 | R-113 | 16.2 | 1.4 | -13.3 | -27.0747
1165 | R-113 | 16.3 | 1.41 | -13.29 | -27.0666
1166 | R-113 | 16.4 | 1.41 | -13.29 | -27.0584
1167 | R-113 | 16.5 | 1.41 | -13.29 | -27.0503
1168 | R-113 | 16.6 | 1.42 | -13.28 | -27.0421
1169 | R-113 | 16.7 | 1.42 | -13.28 | -27.034
1170 | R-113 | 16.8 | 1.43 | -13.27 | -27.0259
1171 | R-113 | 16.9 | 1.43 | -13.27 | -27.0177
1172 | R-113 | 17 | 1.44 | -13.27 | -27.0075
1173 | R-113 | 17.1 | 1.44 | -13.26 | -26.9994
1174 | R-113 | 17.2 | 1.44 | -13.26 | -26.9913
1175 | R-113 | 17.3 | 1.45 | -13.25 | -26.9831
1176 | R-113 | 17.4 | 1.45 | -13.25 | -26.975
1177 | R-113 | 17.5 | 1.46 | -13.25 | -26.9668
1178 | R-113 | 17.6 | 1.46 | -13.24 | -26.9566
1179 | R-113 | 17.7 | 1.46 | -13.24 | -26.9485
1180 | R-113 | 17.8 | 1.47 | -13.23 | -26.9403
1181 | R-113 | 17.9 | 1.47 | -13.23 | -26.9322
1182 | R-113 | 18 | 1.48 | -13.22 | -26.922
1183 | R-113 | 18.1 | 1.48 | -13.22 | -26.9139
1184 | R-113 | 18.2 | 1.49 | -13.21 | -26.9057
1185 | R-113 | 18.3 | 1.49 | -13.21 | -26.8976
1186 | R-113 | 18.4 | 1.49 | -13.21 | -26.8874
1187 | R-113 | 18.5 | 1.5 | -13.2 | -26.8793
1188 | R-113 | 18.6 | 1.5 | -13.2 | -26.8711
1189 | R-113 | 18.7 | 1.51 | -13.19 | -26.8609
1190 | R-113 | 18.8 | 1.51 | -13.19 | -26.8528
1191 | R-113 | 18.9 | 1.52 | -13.19 | -26.8447
1192 | R-113 | 19 | 1.52 | -13.18 | -26.8345
1193 | R-113 | 19.1 | 1.52 | -13.18 | -26.8263
1194 | R-113 | 19.2 | 1.53 | -13.17 | -26.8162
1195 | R-113 | 19.3 | 1.53 | -13.17 | -26.808
1196 | R-113 | 19.4 | 1.54 | -13.16 | -26.7999
1197 | R-113 | 19.5 | 1.54 | -13.16 | -26.7897
1198 | R-113 | 19.6 | 1.55 | -13.15 | -26.7815
1199 | R-113 | 19.7 | 1.55 | -13.15 | -26.7714
1200 | R-113 | 19.8 | 1.55 | -13.14 | -26.7632
1201 | R-113 | 19.9 | 1.56 | -13.14 | -26.7551
1202 | R-113 | 20 | 1.56 | -13.14 | -26.7449
1203 | R-113 | 20.1 | 1.57 | -13.13 | -26.7368
1204 | R-113 | 20.2 | 1.57 | -13.13 | -26.7266
1205 | R-113 | 20.3 | 1.58 | -13.12 | -26.7184
1206 | R-113 | 20.4 | 1.58 | -13.12 | -26.7082
1207 | R-113 | 20.5 | 1.59 | -13.11 | -26.7001
1208 | R-113 | 20.6 | 1.59 | -13.11 | -26.6899
1209 | R-113 | 20.7 | 1.6 | -13.11 | -26.6818
1210 | R-113 | 20.8 | 1.6 | -13.1 | -26.6716
1211 | R-113 | 20.9 | 1.61 | -13.1 | -26.6614
1212 | R-113 | 21 | 1.61 | -13.09 | -26.6533
1213 | R-113 | 21.1 | 1.61 | -13.09 | -26.6431
1214 | R-113 | 21.2 | 1.62 | -13.08 | -26.6349
1215 | R-113 | 21.3 | 1.62 | -13.08 | -26.6248
1216 | R-113 | 21.4 | 1.63 | -13.07 | -26.6146
1217 | R-113 | 21.5 | 1.63 | -13.07 | -26.6064
1218 | R-113 | 21.6 | 1.64 | -13.06 | -26.5963
1219 | R-113 | 21.7 | 1.64 | -13.06 | -26.5881
1220 | R-113 | 21.8 | 1.65 | -13.05 | -26.5779
1221 | R-113 | 21.9 | 1.65 | -13.05 | -26.5678
1222 | R-113 | 22 | 1.66 | -13.04 | -26.5596
1223 | R-113 | 22.1 | 1.66 | -13.04 | -26.5494
1224 | R-113 | 22.2 | 1.67 | -13.04 | -26.5393
1225 | R-113 | 22.3 | 1.67 | -13.03 | -26.5291
1226 | R-113 | 22.4 | 1.67 | -13.03 | -26.5209
1227 | R-113 | 22.5 | 1.68 | -13.02 | -26.5108
1228 | R-113 | 22.6 | 1.68 | -13.02 | -26.5006
1229 | R-113 | 22.7 | 1.69 | -13.01 | -26.4904
1230 | R-113 | 22.8 | 1.69 | -13.01 | -26.4823
1231 | R-113 | 22.9 | 1.7 | -13 | -26.4721
1232 | R-113 | 23 | 1.7 | -13 | -26.4619
1233 | R-113 | 23.1 | 1.71 | -12.99 | -26.4517
1234 | R-113 | 23.2 | 1.71 | -12.99 | -26.4436
1235 | R-113 | 23.3 | 1.72 | -12.98 | -26.4334
1236 | R-113 | 23.4 | 1.72 | -12.98 | -26.4232
1237 | R-113 | 23.5 | 1.73 | -12.97 | -26.413
1238 | R-113 | 23.6 | 1.73 | -12.97 | -26.4029
1239 | R-113 | 23.7 | 1.74 | -12.96 | -26.3927
1240 | R-113 | 23.8 | 1.74 | -12.96 | -26.3825
1241 | R-113 | 23.9 | 1.75 | -12.95 | -26.3743
1242 | R-113 | 24 | 1.75 | -12.95 | -26.3642
1243 | R-113 | 24.1 | 1.76 | -12.94 | -26.354
1244 | R-113 | 24.2 | 1.76 | -12.94 | -26.3438
1245 | R-113 | 24.3 | 1.77 | -12.93 | -26.3336
1246 | R-113 | 24.4 | 1.77 | -12.93 | -26.3234
1247 | R-113 | 24.5 | 1.78 | -12.92 | -26.3133
1248 | R-113 | 24.6 | 1.78 | -12.92 | -26.3031
1249 | R-113 | 24.7 | 1.79 | -12.91 | -26.2929
1250 | R-113 | 24.8 | 1.79 | -12.91 | -26.2827
1251 | R-113 | 24.9 | 1.8 | -12.9 | -26.2725
1252 | R-113 | 25 | 1.8 | -12.9 | -26.2624
1253 | R-113 | 25.1 | 1.81 | -12.89 | -26.2522
1254 | R-113 | 25.2 | 1.81 | -12.89 | -26.242
1255 | R-113 | 25.3 | 1.82 | -12.88 | -26.2318
1256 | R-113 | 25.4 | 1.82 | -12.88 | -26.2216
1257 | R-113 | 25.5 | 1.83 | -12.87 | -26.2115
1258 | R-113 | 25.6 | 1.83 | -12.87 | -26.2013
1259 | R-113 | 25.7 | 1.84 | -12.86 | -26.1911
1260 | R-113 | 25.8 | 1.84 | -12.86 | -26.1789
1261 | R-113 | 25.9 | 1.85 | -12.85 | -26.1687
1262 | R-113 | 26 | 1.85 | -12.85 | -26.1585
1263 | R-113 | 26.1 | 1.86 | -12.84 | -26.1484
1264 | R-113 | 26.2 | 1.86 | -12.84 | -26.1382
1265 | R-113 | 26.3 | 1.87 | -12.83 | -26.128
1266 | R-113 | 26.4 | 1.87 | -12.83 | -26.1178
1267 | R-113 | 26.5 | 1.88 | -12.82 | -26.1056
1268 | R-113 | 26.6 | 1.88 | -12.82 | -26.0954
1269 | R-113 | 26.7 | 1.89 | -12.81 | -26.0852
1270 | R-113 | 26.8 | 1.89 | -12.81 | -26.0751
1271 | R-113 | 26.9 | 1.9 | -12.8 | -26.0649
1272 | R-113 | 27 | 1.9 | -12.8 | -26.0527
1273 | R-113 | 27.1 | 1.91 | -12.79 | -26.0425
1274 | R-113 | 27.2 | 1.91 | -12.79 | -26.0323
1275 | R-113 | 27.3 | 1.92 | -12.78 | -26.0201
1276 | R-113 | 27.4 | 1.93 | -12.78 | -26.0099
1277 | R-113 | 27.5 | 1.93 | -12.77 | -25.9997
1278 | R-113 | 27.6 | 1.94 | -12.77 | -25.9895
1279 | R-113 | 27.7 | 1.94 | -12.76 | -25.9773
1280 | R-113 | 27.8 | 1.95 | -12.75 | -25.9671
1281 | R-113 | 27.9 | 1.95 | -12.75 | -25.957
1282 | R-113 | 28 | 1.96 | -12.74 | -25.9447
1283 | R-113 | 28.1 | 1.96 | -12.74 | -25.9346
1284 | R-113 | 28.2 | 1.97 | -12.73 | -25.9224
1285 | R-113 | 28.3 | 1.97 | -12.73 | -25.9122
1286 | R-113 | 28.4 | 1.98 | -12.72 | -25.902
1287 | R-113 | 28.5 | 1.98 | -12.72 | -25.8898
1288 | R-113 | 28.6 | 1.99 | -12.71 | -25.8796
1289 | R-113 | 28.7 | 2 | -12.71 | -25.8674
1290 | R-113 | 28.8 | 2 | -12.7 | -25.8572
1291 | R-113 | 28.9 | 2.01 | -12.69 | -25.845
1292 | R-113 | 29 | 2.01 | -12.69 | -25.8348
1293 | R-113 | 29.1 | 2.02 | -12.68 | -25.8226
1294 | R-113 | 29.2 | 2.02 | -12.68 | -25.8124
1295 | R-113 | 29.3 | 2.03 | -12.67 | -25.8002
1296 | R-113 | 29.4 | 2.03 | -12.67 | -25.79
1297 | R-113 | 29.5 | 2.04 | -12.66 | -25.7778
1298 | R-113 | 29.6 | 2.04 | -12.66 | -25.7676
1299 | R-113 | 29.7 | 2.05 | -12.65 | -25.7554
1300 | R-113 | 29.8 | 2.06 | -12.64 | -25.7432
1301 | R-113 | 29.9 | 2.06 | -12.64 | -25.733
1302 | R-113 | 30 | 2.07 | -12.63 | -25.7208
1303 | R-113 | 30.1 | 2.07 | -12.63 | -25.7106
1304 | R-113 | 30.2 | 2.08 | -12.62 | -25.6984
1305 | R-113 | 30.3 | 2.08 | -12.62 | -25.6862
1306 | R-113 | 30.4 | 2.09 | -12.61 | -25.676
1307 | R-113 | 30.5 | 2.1 | -12.61 | -25.6638
1308 | R-113 | 30.6 | 2.1 | -12.6 | -25.6516
1309 | R-113 | 30.7 | 2.11 | -12.59 | -25.6414
1310 | R-113 | 30.8 | 2.11 | -12.59 | -25.6292
1311 | R-113 | 30.9 | 2.12 | -12.58 | -25.6169
1312 | R-113 | 31 | 2.12 | -12.58 | -25.6047
1313 | R-113 | 31.1 | 2.13 | -12.57 | -25.5946
1314 | R-113 | 31.2 | 2.14 | -12.56 | -25.5823
1315 | R-113 | 31.3 | 2.14 | -12.56 | -25.5701
1316 | R-113 | 31.4 | 2.15 | -12.55 | -25.5579
1317 | R-113 | 31.5 | 2.15 | -12.55 | -25.5457
1318 | R-113 | 31.6 | 2.16 | -12.54 | -25.5355
1319 | R-113 | 31.7 | 2.16 | -12.54 | -25.5233
1320 | R-113 | 31.8 | 2.17 | -12.53 | -25.5111
1321 | R-113 | 31.9 | 2.18 | -12.52 | -25.4989
1322 | R-113 | 32 | 2.18 | -12.52 | -25.4867
1323 | R-113 | 32.1 | 2.19 | -12.51 | -25.4744
1324 | R-113 | 32.2 | 2.19 | -12.51 | -25.4622
1325 | R-113 | 32.3 | 2.2 | -12.5 | -25.452
1326 | R-113 | 32.4 | 2.21 | -12.5 | -25.4398
1327 | R-113 | 32.5 | 2.21 | -12.49 | -25.4276
1328 | R-113 | 32.6 | 2.22 | -12.48 | -25.4154
1329 | R-113 | 32.7 | 2.22 | -12.48 | -25.4032
1330 | R-113 | 32.8 | 2.23 | -12.47 | -25.391
1331 | R-113 | 32.9 | 2.23 | -12.46 | -25.3787
1332 | R-113 | 33 | 2.24 | -12.46 | -25.3665
1333 | R-113 | 33.1 | 2.25 | -12.45 | -25.3543
1334 | R-113 | 33.2 | 2.25 | -12.45 | -25.3421
1335 | R-113 | 33.3 | 2.26 | -12.44 | -25.3299
1336 | R-113 | 33.4 | 2.27 | -12.44 | -25.3177
1337 | R-113 | 33.5 | 2.27 | -12.43 | -25.3054
1338 | R-113 | 33.6 | 2.28 | -12.42 | -25.2932
1339 | R-113 | 33.7 | 2.28 | -12.42 | -25.279
1340 | R-113 | 33.8 | 2.29 | -12.41 | -25.2668
1341 | R-113 | 33.9 | 2.3 | -12.4 | -25.2545
1342 | R-113 | 34 | 2.3 | -12.4 | -25.2423
1343 | R-113 | 34.1 | 2.31 | -12.39 | -25.2301
1344 | R-113 | 34.2 | 2.31 | -12.39 | -25.2179
1345 | R-113 | 34.3 | 2.32 | -12.38 | -25.2057
1346 | R-113 | 34.4 | 2.33 | -12.37 | -25.1914
1347 | R-113 | 34.5 | 2.33 | -12.37 | -25.1792
1348 | R-113 | 34.6 | 2.34 | -12.36 | -25.167
1349 | R-113 | 34.7 | 2.35 | -12.36 | -25.1548
1350 | R-113 | 34.8 | 2.35 | -12.35 | -25.1426
1351 | R-113 | 34.9 | 2.36 | -12.34 | -25.1283
1352 | R-113 | 35 | 2.36 | -12.34 | -25.1161
1353 | R-113 | 35.1 | 2.37 | -12.33 | -25.1039
1354 | R-113 | 35.2 | 2.38 | -12.32 | -25.0896
1355 | R-113 | 35.3 | 2.38 | -12.32 | -25.0774
1356 | R-113 | 35.4 | 2.39 | -12.31 | -25.0652
1357 | R-113 | 35.5 | 2.4 | -12.3 | -25.0509
1358 | R-113 | 35.6 | 2.4 | -12.3 | -25.0387
1359 | R-113 | 35.7 | 2.41 | -12.29 | -25.0265
1360 | R-113 | 35.8 | 2.42 | -12.29 | -25.0123
1361 | R-113 | 35.9 | 2.42 | -12.28 | -25
1362 | R-113 | 36 | 2.43 | -12.27 | -24.9878
1363 | R-113 | 36.1 | 2.43 | -12.27 | -24.9736
1364 | R-113 | 36.2 | 2.44 | -12.26 | -24.9614
1365 | R-113 | 36.3 | 2.45 | -12.25 | -24.9471
1366 | R-113 | 36.4 | 2.45 | -12.25 | -24.9349
1367 | R-113 | 36.5 | 2.46 | -12.24 | -24.9206
1368 | R-113 | 36.6 | 2.47 | -12.23 | -24.9084
1369 | R-113 | 36.7 | 2.47 | -12.23 | -24.8942
1370 | R-113 | 36.8 | 2.48 | -12.22 | -24.882
1371 | R-113 | 36.9 | 2.49 | -12.21 | -24.8677
1372 | R-113 | 37 | 2.49 | -12.21 | -24.8555
1373 | R-113 | 37.1 | 2.5 | -12.2 | -24.8412
1374 | R-113 | 37.2 | 2.5 | -12.2 | -24.829
1375 | R-113 | 37.3 | 2.51 | -12.19 | -24.8148
1376 | R-113 | 37.4 | 2.52 | -12.18 | -24.8005
1377 | R-113 | 37.5 | 2.52 | -12.18 | -24.7883
1378 | R-113 | 37.6 | 2.53 | -12.17 | -24.774
1379 | R-113 | 37.7 | 2.54 | -12.16 | -24.7618
1380 | R-113 | 37.8 | 2.54 | -12.16 | -24.7476
1381 | R-113 | 37.9 | 2.55 | -12.15 | -24.7333
1382 | R-113 | 38 | 2.56 | -12.14 | -24.7211
1383 | R-113 | 38.1 | 2.56 | -12.13 | -24.7069
1384 | R-113 | 38.2 | 2.57 | -12.13 | -24.6926
1385 | R-113 | 38.3 | 2.58 | -12.12 | -24.6784
1386 | R-113 | 38.4 | 2.59 | -12.12 | -24.6661
1387 | R-113 | 38.5 | 2.59 | -12.11 | -24.6519
1388 | R-113 | 38.6 | 2.6 | -12.1 | -24.6376
1389 | R-113 | 38.7 | 2.61 | -12.09 | -24.6234
1390 | R-113 | 38.8 | 2.61 | -12.09 | -24.6112
1391 | R-113 | 38.9 | 2.62 | -12.08 | -24.5969
1392 | R-113 | 39 | 2.63 | -12.07 | -24.5827
1393 | R-113 | 39.1 | 2.63 | -12.07 | -24.5684
1394 | R-113 | 39.2 | 2.64 | -12.06 | -24.5542
1395 | R-113 | 39.3 | 2.65 | -12.05 | -24.5399
1396 | R-113 | 39.4 | 2.65 | -12.05 | -24.5257
1397 | R-113 | 39.5 | 2.66 | -12.04 | -24.5134
1398 | R-113 | 39.6 | 2.67 | -12.03 | -24.4992
1399 | R-113 | 39.7 | 2.67 | -12.03 | -24.4849
1400 | R-113 | 39.8 | 2.68 | -12.02 | -24.4707
1401 | R-113 | 39.9 | 2.69 | -12.01 | -24.4564
1402 | R-113 | 40 | 2.69 | -12.01 | -24.4422
1403 | R-113 | 40.1 | 2.7 | -12 | -24.4279
1404 | R-113 | 40.2 | 2.71 | -11.99 | -24.4137
1405 | R-113 | 40.3 | 2.72 | -11.98 | -24.3994
1406 | R-113 | 40.4 | 2.72 | -11.98 | -24.3852
1407 | R-113 | 40.5 | 2.73 | -11.97 | -24.3709
1408 | R-113 | 40.6 | 2.74 | -11.96 | -24.3567
1409 | R-113 | 40.7 | 2.74 | -11.96 | -24.3424
1410 | R-113 | 40.8 | 2.75 | -11.95 | -24.3261
1411 | R-113 | 40.9 | 2.76 | -11.94 | -24.3119
1412 | R-113 | 41 | 2.77 | -11.93 | -24.2976
1413 | R-113 | 41.1 | 2.77 | -11.93 | -24.2834
1414 | R-113 | 41.2 | 2.78 | -11.92 | -24.2691
1415 | R-113 | 41.3 | 2.79 | -11.91 | -24.2549
1416 | R-113 | 41.4 | 2.79 | -11.91 | -24.2406
1417 | R-113 | 41.5 | 2.8 | -11.9 | -24.2243
1418 | R-113 | 41.6 | 2.81 | -11.89 | -24.2101
1419 | R-113 | 41.7 | 2.82 | -11.88 | -24.1958
1420 | R-113 | 41.8 | 2.82 | -11.88 | -24.1816
1421 | R-113 | 41.9 | 2.83 | -11.87 | -24.1653
1422 | R-113 | 42 | 2.84 | -11.86 | -24.151
1423 | R-113 | 42.1 | 2.85 | -11.86 | -24.1368
1424 | R-113 | 42.2 | 2.85 | -11.85 | -24.1225
1425 | R-113 | 42.3 | 2.86 | -11.84 | -24.1062
1426 | R-113 | 42.4 | 2.87 | -11.83 | -24.092
1427 | R-113 | 42.5 | 2.88 | -11.83 | -24.0757
1428 | R-113 | 42.6 | 2.88 | -11.82 | -24.0615
1429 | R-113 | 42.7 | 2.89 | -11.81 | -24.0472
1430 | R-113 | 42.8 | 2.9 | -11.8 | -24.0309
1431 | R-113 | 42.9 | 2.9 | -11.8 | -24.0167
1432 | R-113 | 43 | 2.91 | -11.79 | -24.0024
1433 | R-113 | 43.1 | 2.92 | -11.78 | -23.9861
1434 | R-113 | 43.2 | 2.93 | -11.77 | -23.9719
1435 | R-113 | 43.3 | 2.93 | -11.77 | -23.9556
1436 | R-113 | 43.4 | 2.94 | -11.76 | -23.9413
1437 | R-113 | 43.5 | 2.95 | -11.75 | -23.925
1438 | R-113 | 43.6 | 2.96 | -11.74 | -23.9108
1439 | R-113 | 43.7 | 2.96 | -11.74 | -23.8945
1440 | R-113 | 43.8 | 2.97 | -11.73 | -23.8802
1441 | R-113 | 43.9 | 2.98 | -11.72 | -23.864
1442 | R-113 | 44 | 2.99 | -11.71 | -23.8477
1443 | R-113 | 44.1 | 2.99 | -11.71 | -23.8334
1444 | R-113 | 44.2 | 3 | -11.7 | -23.8171
1445 | R-113 | 44.3 | 3.01 | -11.69 | -23.8029
1446 | R-113 | 44.4 | 3.02 | -11.68 | -23.7866
1447 | R-113 | 44.5 | 3.02 | -11.68 | -23.7703
1448 | R-113 | 44.6 | 3.03 | -11.67 | -23.756
1449 | R-113 | 44.7 | 3.04 | -11.66 | -23.7398
1450 | R-113 | 44.8 | 3.05 | -11.65 | -23.7235
1451 | R-113 | 44.9 | 3.06 | -11.64 | -23.7072
1452 | R-113 | 45 | 3.06 | -11.64 | -23.6929
1453 | R-113 | 45.1 | 3.07 | -11.63 | -23.6766
1454 | R-113 | 45.2 | 3.08 | -11.62 | -23.6604
1455 | R-113 | 45.3 | 3.09 | -11.61 | -23.6441
1456 | R-113 | 45.4 | 3.1 | -11.61 | -23.6278
1457 | R-113 | 45.5 | 3.1 | -11.6 | -23.6135
1458 | R-113 | 45.6 | 3.11 | -11.59 | -23.5972
1459 | R-113 | 45.7 | 3.12 | -11.58 | -23.581
1460 | R-113 | 45.8 | 3.13 | -11.57 | -23.5647
1461 | R-113 | 45.9 | 3.13 | -11.57 | -23.5484
1462 | R-113 | 46 | 3.14 | -11.56 | -23.5321
1463 | R-113 | 46.1 | 3.15 | -11.55 | -23.5158
1464 | R-113 | 46.2 | 3.16 | -11.54 | -23.4995
1465 | R-113 | 46.3 | 3.17 | -11.54 | -23.4853
1466 | R-113 | 46.4 | 3.17 | -11.53 | -23.469
1467 | R-113 | 46.5 | 3.18 | -11.52 | -23.4527
1468 | R-113 | 46.6 | 3.19 | -11.51 | -23.4364
1469 | R-113 | 46.7 | 3.2 | -11.5 | -23.4201
1470 | R-113 | 46.8 | 3.21 | -11.49 | -23.4018
1471 | R-113 | 46.9 | 3.21 | -11.49 | -23.3855
1472 | R-113 | 47 | 3.22 | -11.48 | -23.3692
1473 | R-113 | 47.1 | 3.23 | -11.47 | -23.3529
1474 | R-113 | 47.2 | 3.24 | -11.46 | -23.3366
1475 | R-113 | 47.3 | 3.25 | -11.45 | -23.3203
1476 | R-113 | 47.4 | 3.25 | -11.45 | -23.3041
1477 | R-113 | 47.5 | 3.26 | -11.44 | -23.2878
1478 | R-113 | 47.6 | 3.27 | -11.43 | -23.2715
1479 | R-113 | 47.7 | 3.28 | -11.42 | -23.2532
1480 | R-113 | 47.8 | 3.29 | -11.41 | -23.2369
1481 | R-113 | 47.9 | 3.29 | -11.4 | -23.2206
1482 | R-113 | 48 | 3.3 | -11.4 | -23.2043
1483 | R-113 | 48.1 | 3.31 | -11.39 | -23.188
1484 | R-113 | 48.2 | 3.32 | -11.38 | -23.1697
1485 | R-113 | 48.3 | 3.33 | -11.37 | -23.1534
1486 | R-113 | 48.4 | 3.34 | -11.36 | -23.1371
1487 | R-113 | 48.5 | 3.35 | -11.36 | -23.1188
1488 | R-113 | 48.6 | 3.35 | -11.35 | -23.1025
1489 | R-113 | 48.7 | 3.36 | -11.34 | -23.0862
1490 | R-113 | 48.8 | 3.37 | -11.33 | -23.0679
1491 | R-113 | 48.9 | 3.38 | -11.32 | -23.0516
1492 | R-113 | 49 | 3.39 | -11.31 | -23.0353
1493 | R-113 | 49.1 | 3.4 | -11.3 | -23.017
1494 | R-113 | 49.2 | 3.4 | -11.3 | -23.0007
1495 | R-113 | 49.3 | 3.41 | -11.29 | -22.9824
1496 | R-113 | 49.4 | 3.42 | -11.28 | -22.9661
1497 | R-113 | 49.5 | 3.43 | -11.27 | -22.9478
1498 | R-113 | 49.6 | 3.44 | -11.26 | -22.9315
1499 | R-113 | 49.7 | 3.45 | -11.25 | -22.9131
1500 | R-113 | 49.8 | 3.45 | -11.25 | -22.8969
1501 | R-113 | 49.9 | 3.46 | -11.24 | -22.8785
1502 | R-113 | 50 | 3.47 | -11.23 | -22.8622
1503 | R-113 | 50.1 | 3.48 | -11.22 | -22.8439
1504 | R-113 | 50.2 | 3.49 | -11.21 | -22.8256
1505 | R-113 | 50.3 | 3.5 | -11.2 | -22.8093
1506 | R-113 | 50.4 | 3.51 | -11.19 | -22.791
1507 | R-113 | 50.5 | 3.51 | -11.19 | -22.7747
1508 | R-113 | 50.6 | 3.52 | -11.18 | -22.7564
1509 | R-113 | 50.7 | 3.53 | -11.17 | -22.7381
1510 | R-113 | 50.8 | 3.54 | -11.16 | -22.7197
1511 | R-113 | 50.9 | 3.55 | -11.15 | -22.7034
1512 | R-113 | 51 | 3.56 | -11.14 | -22.6851
1513 | R-113 | 51.1 | 3.57 | -11.13 | -22.6668
1514 | R-113 | 51.2 | 3.58 | -11.12 | -22.6485
1515 | R-113 | 51.3 | 3.58 | -11.12 | -22.6322
1516 | R-113 | 51.4 | 3.59 | -11.11 | -22.6138
1517 | R-113 | 51.5 | 3.6 | -11.1 | -22.5955
1518 | R-113 | 51.6 | 3.61 | -11.09 | -22.5772
1519 | R-113 | 51.7 | 3.62 | -11.08 | -22.5589
1520 | R-113 | 51.8 | 3.63 | -11.07 | -22.5406
1521 | R-113 | 51.9 | 3.64 | -11.06 | -22.5222
1522 | R-113 | 52 | 3.65 | -11.05 | -22.5059
1523 | R-113 | 52.1 | 3.66 | -11.04 | -22.4876
1524 | R-113 | 52.2 | 3.66 | -11.04 | -22.4693
1525 | R-113 | 52.3 | 3.67 | -11.03 | -22.451
1526 | R-113 | 52.4 | 3.68 | -11.02 | -22.4326
1527 | R-113 | 52.5 | 3.69 | -11.01 | -22.4143
1528 | R-113 | 52.6 | 3.7 | -11 | -22.396
1529 | R-113 | 52.7 | 3.71 | -10.99 | -22.3777
1530 | R-113 | 52.8 | 3.72 | -10.98 | -22.3593
1531 | R-113 | 52.9 | 3.73 | -10.97 | -22.339
1532 | R-113 | 53 | 3.74 | -10.96 | -22.3207
1533 | R-113 | 53.1 | 3.75 | -10.95 | -22.3023
1534 | R-113 | 53.2 | 3.75 | -10.95 | -22.284
1535 | R-113 | 53.3 | 3.76 | -10.94 | -22.2657
1536 | R-113 | 53.4 | 3.77 | -10.93 | -22.2474
1537 | R-113 | 53.5 | 3.78 | -10.92 | -22.2291
1538 | R-113 | 53.6 | 3.79 | -10.91 | -22.2087
1539 | R-113 | 53.7 | 3.8 | -10.9 | -22.1904
1540 | R-113 | 53.8 | 3.81 | -10.89 | -22.172
1541 | R-113 | 53.9 | 3.82 | -10.88 | -22.1537
1542 | R-113 | 54 | 3.83 | -10.87 | -22.1334
1543 | R-113 | 54.1 | 3.84 | -10.86 | -22.115
1544 | R-113 | 54.2 | 3.85 | -10.85 | -22.0967
1545 | R-113 | 54.3 | 3.86 | -10.84 | -22.0764
1546 | R-113 | 54.4 | 3.87 | -10.83 | -22.058
1547 | R-113 | 54.5 | 3.88 | -10.83 | -22.0397
1548 | R-113 | 54.6 | 3.89 | -10.81 | -22.0193
1549 | R-113 | 54.7 | 3.89 | -10.81 | -22.001
1550 | R-113 | 54.8 | 3.9 | -10.8 | -21.9827
1551 | R-113 | 54.9 | 3.91 | -10.79 | -21.9623
1552 | R-113 | 55 | 3.92 | -10.78 | -21.944
1553 | R-113 | 55.1 | 3.93 | -10.77 | -21.9236
1554 | R-113 | 55.2 | 3.94 | -10.76 | -21.9053
1555 | R-113 | 55.3 | 3.95 | -10.75 | -21.885
1556 | R-113 | 55.4 | 3.96 | -10.74 | -21.8666
1557 | R-113 | 55.5 | 3.97 | -10.73 | -21.8463
1558 | R-113 | 55.6 | 3.98 | -10.72 | -21.8259
1559 | R-113 | 55.7 | 3.99 | -10.71 | -21.8076
1560 | R-113 | 55.8 | 4 | -10.7 | -21.7872
1561 | R-113 | 55.9 | 4.01 | -10.69 | -21.7689
1562 | R-113 | 56 | 4.02 | -10.68 | -21.7486
1563 | R-113 | 56.1 | 4.03 | -10.67 | -21.7282
1564 | R-113 | 56.2 | 4.04 | -10.66 | -21.7099
1565 | R-113 | 56.3 | 4.05 | -10.65 | -21.6895
1566 | R-113 | 56.4 | 4.06 | -10.64 | -21.6691
1567 | R-113 | 56.5 | 4.07 | -10.63 | -21.6488
1568 | R-113 | 56.6 | 4.08 | -10.62 | -21.6305
1569 | R-113 | 56.7 | 4.09 | -10.61 | -21.6101
1570 | R-113 | 56.8 | 4.1 | -10.6 | -21.5897
1571 | R-113 | 56.9 | 4.11 | -10.59 | -21.5694
1572 | R-113 | 57 | 4.12 | -10.58 | -21.549
1573 | R-113 | 57.1 | 4.13 | -10.58 | -21.5307
1574 | R-113 | 57.2 | 4.13 | -10.56 | -21.5103
1575 | R-113 | 57.3 | 4.15 | -10.55 | -21.49
1576 | R-113 | 57.4 | 4.16 | -10.54 | -21.4696
1577 | R-113 | 57.5 | 4.17 | -10.54 | -21.4493
1578 | R-113 | 57.6 | 4.17 | -10.53 | -21.4289
1579 | R-113 | 57.7 | 4.19 | -10.52 | -21.4085
1580 | R-113 | 57.8 | 4.2 | -10.51 | -21.3882
1581 | R-113 | 57.9 | 4.21 | -10.5 | -21.3678
1582 | R-113 | 58 | 4.21 | -10.48 | -21.3475
1583 | R-113 | 58.1 | 4.22 | -10.47 | -21.3271
1584 | R-113 | 58.2 | 4.24 | -10.46 | -21.3067
1585 | R-113 | 58.3 | 4.25 | -10.46 | -21.2864
1586 | R-113 | 58.4 | 4.25 | -10.45 | -21.266
1587 | R-113 | 58.5 | 4.26 | -10.44 | -21.2457
1588 | R-113 | 58.6 | 4.28 | -10.42 | -21.2233
1589 | R-113 | 58.7 | 4.29 | -10.41 | -21.2029
1590 | R-113 | 58.8 | 4.3 | -10.4 | -21.1825
1591 | R-113 | 58.9 | 4.31 | -10.39 | -21.1622
1592 | R-113 | 59 | 4.32 | -10.38 | -21.1418
1593 | R-113 | 59.1 | 4.33 | -10.37 | -21.1194
1594 | R-113 | 59.2 | 4.34 | -10.36 | -21.0991
1595 | R-113 | 59.3 | 4.35 | -10.35 | -21.0787
1596 | R-113 | 59.4 | 4.36 | -10.34 | -21.0584
1597 | R-113 | 59.5 | 4.37 | -10.33 | -21.0359
1598 | R-113 | 59.6 | 4.38 | -10.32 | -21.0156
1599 | R-113 | 59.7 | 4.39 | -10.31 | -20.9952
1600 | R-113 | 59.8 | 4.4 | -10.3 | -20.9728
1601 | R-113 | 59.9 | 4.41 | -10.29 | -20.9525
1602 | R-113 | 60 | 4.42 | -10.28 | -20.9301
1603 | R-113 | 60.1 | 4.43 | -10.27 | -20.9097
1604 | R-113 | 60.2 | 4.44 | -10.26 | -20.8894
1605 | R-113 | 60.3 | 4.45 | -10.25 | -20.867
1606 | R-113 | 60.4 | 4.46 | -10.24 | -20.8466
1607 | R-113 | 60.5 | 4.47 | -10.23 | -20.8242
1608 | R-113 | 60.6 | 4.48 | -10.22 | -20.8018
1609 | R-113 | 60.7 | 4.49 | -10.21 | -20.7814
1610 | R-113 | 60.8 | 4.5 | -10.2 | -20.7591
1611 | R-113 | 60.9 | 4.51 | -10.19 | -20.7387
1612 | R-113 | 61 | 4.53 | -10.18 | -20.7163
1613 | R-113 | 61.1 | 4.54 | -10.16 | -20.6939
1614 | R-113 | 61.2 | 4.55 | -10.15 | -20.6735
1615 | R-113 | 61.3 | 4.56 | -10.14 | -20.6512
1616 | R-113 | 61.4 | 4.57 | -10.13 | -20.6288
1617 | R-113 | 61.5 | 4.58 | -10.12 | -20.6084
1618 | R-113 | 61.6 | 4.59 | -10.11 | -20.586
1619 | R-113 | 61.7 | 4.6 | -10.1 | -20.5636
1620 | R-113 | 61.8 | 4.61 | -10.09 | -20.5412
1621 | R-113 | 61.9 | 4.62 | -10.08 | -20.5208
1622 | R-113 | 62 | 4.63 | -10.07 | -20.4984
1623 | R-113 | 62.1 | 4.64 | -10.06 | -20.4761
1624 | R-113 | 62.2 | 4.65 | -10.05 | -20.4537
1625 | R-113 | 62.3 | 4.67 | -10.04 | -20.4313
1626 | R-113 | 62.4 | 4.68 | -10.02 | -20.4089
1627 | R-113 | 62.5 | 4.69 | -10.01 | -20.3865
1628 | R-113 | 62.6 | 4.7 | -10 | -20.3641
1629 | R-113 | 62.7 | 4.71 | -9.99 | -20.3437
1630 | R-113 | 62.8 | 4.72 | -9.98 | -20.3213
1631 | R-113 | 62.9 | 4.73 | -9.97 | -20.2989
1632 | R-113 | 63 | 4.74 | -9.96 | -20.2765
1633 | R-113 | 63.1 | 4.75 | -9.95 | -20.2521
1634 | R-113 | 63.2 | 4.76 | -9.94 | -20.2297
1635 | R-113 | 63.3 | 4.78 | -9.93 | -20.2073
1636 | R-113 | 63.4 | 4.79 | -9.91 | -20.1849
1637 | R-113 | 63.5 | 4.8 | -9.9 | -20.1625
1638 | R-113 | 63.6 | 4.81 | -9.89 | -20.1401
1639 | R-113 | 63.7 | 4.82 | -9.88 | -20.1177
1640 | R-113 | 63.8 | 4.83 | -9.87 | -20.0953
1641 | R-113 | 63.9 | 4.84 | -9.86 | -20.0709
1642 | R-113 | 64 | 4.85 | -9.85 | -20.0485
1643 | R-113 | 64.1 | 4.86 | -9.84 | -20.0261
1644 | R-113 | 64.2 | 4.88 | -9.83 | -20.0037
1645 | R-113 | 64.3 | 4.89 | -9.81 | -19.9793
1646 | R-113 | 64.4 | 4.9 | -9.8 | -19.9569
1647 | R-113 | 64.5 | 4.91 | -9.79 | -19.9345
1648 | R-113 | 64.6 | 4.92 | -9.78 | -19.91
1649 | R-113 | 64.7 | 4.93 | -9.77 | -19.8877
1650 | R-113 | 64.8 | 4.94 | -9.76 | -19.8632
1651 | R-113 | 64.9 | 4.96 | -9.75 | -19.8408
1652 | R-113 | 65 | 4.97 | -9.73 | -19.8184
1653 | R-113 | 65.1 | 4.98 | -9.72 | -19.794
1654 | R-113 | 65.2 | 4.99 | -9.71 | -19.7716
1655 | R-113 | 65.3 | 5 | -9.7 | -19.7472
1656 | R-113 | 65.4 | 5.01 | -9.69 | -19.7248
1657 | R-113 | 65.5 | 5.02 | -9.68 | -19.7003
1658 | R-113 | 65.6 | 5.04 | -9.67 | -19.6779
1659 | R-113 | 65.7 | 5.05 | -9.65 | -19.6535
1660 | R-113 | 65.8 | 5.06 | -9.64 | -19.6291
1661 | R-113 | 65.9 | 5.07 | -9.63 | -19.6067
1662 | R-113 | 66 | 5.08 | -9.62 | -19.5822
1663 | R-113 | 66.1 | 5.09 | -9.61 | -19.5578
1664 | R-113 | 66.2 | 5.11 | -9.6 | -19.5354
1665 | R-113 | 66.3 | 5.12 | -9.58 | -19.511
1666 | R-113 | 66.4 | 5.13 | -9.57 | -19.4866
1667 | R-113 | 66.5 | 5.14 | -9.56 | -19.4621
1668 | R-113 | 66.6 | 5.15 | -9.55 | -19.4397
1669 | R-113 | 66.7 | 5.16 | -9.54 | -19.4153
1670 | R-113 | 66.8 | 5.18 | -9.52 | -19.3909
1671 | R-113 | 66.9 | 5.19 | -9.51 | -19.3664
1672 | R-113 | 67 | 5.2 | -9.5 | -19.342
1673 | R-113 | 67.1 | 5.21 | -9.49 | -19.3176
1674 | R-113 | 67.2 | 5.22 | -9.48 | -19.2931
1675 | R-113 | 67.3 | 5.24 | -9.46 | -19.2687
1676 | R-113 | 67.4 | 5.25 | -9.45 | -19.2463
1677 | R-113 | 67.5 | 5.26 | -9.44 | -19.2219
1678 | R-113 | 67.6 | 5.27 | -9.43 | -19.1974
1679 | R-113 | 67.7 | 5.28 | -9.42 | -19.173
1680 | R-113 | 67.8 | 5.3 | -9.4 | -19.1465
1681 | R-113 | 67.9 | 5.31 | -9.39 | -19.1221
1682 | R-113 | 68 | 5.32 | -9.38 | -19.0977
1683 | R-113 | 68.1 | 5.33 | -9.37 | -19.0733
1684 | R-113 | 68.2 | 5.34 | -9.36 | -19.0488
1685 | R-113 | 68.3 | 5.36 | -9.34 | -19.0244
1686 | R-113 | 68.4 | 5.37 | -9.33 | -18.9999
1687 | R-113 | 68.5 | 5.38 | -9.32 | -18.9735
1688 | R-113 | 68.6 | 5.39 | -9.31 | -18.949
1689 | R-113 | 68.7 | 5.41 | -9.29 | -18.9246
1690 | R-113 | 68.8 | 5.42 | -9.28 | -18.9002
1691 | R-113 | 68.9 | 5.43 | -9.27 | -18.8737
1692 | R-113 | 69 | 5.44 | -9.26 | -18.8493
1693 | R-113 | 69.1 | 5.45 | -9.25 | -18.8249
1694 | R-113 | 69.2 | 5.47 | -9.23 | -18.7984
1695 | R-113 | 69.3 | 5.48 | -9.22 | -18.774
1696 | R-113 | 69.4 | 5.49 | -9.21 | -18.7495
1697 | R-113 | 69.5 | 5.5 | -9.2 | -18.7231
1698 | R-113 | 69.6 | 5.52 | -9.18 | -18.6986
1699 | R-113 | 69.7 | 5.53 | -9.17 | -18.6722
1700 | R-113 | 69.8 | 5.54 | -9.16 | -18.6477
1701 | R-113 | 69.9 | 5.55 | -9.15 | -18.6213
1702 | R-113 | 70 | 5.57 | -9.13 | -18.5968
1703 | R-113 | 70.1 | 5.58 | -9.12 | -18.5704
1704 | R-113 | 70.2 | 5.59 | -9.11 | -18.5459
1705 | R-113 | 70.3 | 5.6 | -9.1 | -18.5195
1706 | R-113 | 70.4 | 5.62 | -9.08 | -18.493
1707 | R-113 | 70.5 | 5.63 | -9.07 | -18.4686
1708 | R-113 | 70.6 | 5.64 | -9.06 | -18.4421
1709 | R-113 | 70.7 | 5.66 | -9.04 | -18.4156
1710 | R-113 | 70.8 | 5.67 | -9.03 | -18.3912
1711 | R-113 | 70.9 | 5.68 | -9.02 | -18.3647
1712 | R-113 | 71 | 5.69 | -9.01 | -18.3382
1713 | R-113 | 71.1 | 5.71 | -8.99 | -18.3118
1714 | R-113 | 71.2 | 5.72 | -8.98 | -18.2853
1715 | R-113 | 71.3 | 5.73 | -8.97 | -18.2609
1716 | R-113 | 71.4 | 5.74 | -8.96 | -18.2344
1717 | R-113 | 71.5 | 5.76 | -8.94 | -18.208
1718 | R-113 | 71.6 | 5.77 | -8.93 | -18.1815
1719 | R-113 | 71.7 | 5.78 | -8.92 | -18.155
1720 | R-113 | 71.8 | 5.8 | -8.9 | -18.1285
1721 | R-113 | 71.9 | 5.81 | -8.89 | -18.1021
1722 | R-113 | 72 | 5.82 | -8.88 | -18.0756
1723 | R-113 | 72.1 | 5.84 | -8.87 | -18.0491
1724 | R-113 | 72.2 | 5.85 | -8.85 | -18.0227
1725 | R-113 | 72.3 | 5.86 | -8.84 | -17.9962
1726 | R-113 | 72.4 | 5.87 | -8.83 | -17.9697
1727 | R-113 | 72.5 | 5.89 | -8.81 | -17.9433
1728 | R-113 | 72.6 | 5.9 | -8.8 | -17.9168
1729 | R-113 | 72.7 | 5.91 | -8.79 | -17.8883
1730 | R-113 | 72.8 | 5.93 | -8.77 | -17.8618
1731 | R-113 | 72.9 | 5.94 | -8.76 | -17.8354
1732 | R-113 | 73 | 5.95 | -8.75 | -17.8089
1733 | R-113 | 73.1 | 5.97 | -8.73 | -17.7824
1734 | R-113 | 73.2 | 5.98 | -8.72 | -17.7539
1735 | R-113 | 73.3 | 5.99 | -8.71 | -17.7275
1736 | R-113 | 73.4 | 6.01 | -8.69 | -17.701
1737 | R-113 | 73.5 | 6.02 | -8.68 | -17.6725
1738 | R-113 | 73.6 | 6.03 | -8.67 | -17.646
1739 | R-113 | 73.7 | 6.05 | -8.65 | -17.6195
1740 | R-113 | 73.8 | 6.06 | -8.64 | -17.591
1741 | R-113 | 73.9 | 6.07 | -8.63 | -17.5646
1742 | R-113 | 74 | 6.09 | -8.61 | -17.5361
1743 | R-113 | 74.1 | 6.1 | -8.6 | -17.5096
1744 | R-113 | 74.2 | 6.11 | -8.59 | -17.4811
1745 | R-113 | 74.3 | 6.13 | -8.57 | -17.4546
1746 | R-113 | 74.4 | 6.14 | -8.56 | -17.4261
1747 | R-113 | 74.5 | 6.16 | -8.54 | -17.3976
1748 | R-113 | 74.6 | 6.17 | -8.53 | -17.3712
1749 | R-113 | 74.7 | 6.18 | -8.52 | -17.3426
1750 | R-113 | 74.8 | 6.2 | -8.51 | -17.3162
1751 | R-113 | 74.9 | 6.21 | -8.49 | -17.2877
1752 | R-113 | 75 | 6.22 | -8.48 | -17.2592
1753 | R-113 | 75.1 | 6.24 | -8.46 | -17.2307
1754 | R-113 | 75.2 | 6.25 | -8.45 | -17.2042
1755 | R-113 | 75.3 | 6.26 | -8.44 | -17.1757
1756 | R-113 | 75.4 | 6.28 | -8.42 | -17.1472
1757 | R-113 | 75.5 | 6.29 | -8.41 | -17.1187
1758 | R-113 | 75.6 | 6.31 | -8.39 | -17.0902
1759 | R-113 | 75.7 | 6.32 | -8.38 | -17.0637
1760 | R-113 | 75.8 | 6.33 | -8.37 | -17.0352
1761 | R-113 | 75.9 | 6.35 | -8.35 | -17.0067
1762 | R-113 | 76 | 6.36 | -8.34 | -16.9782
1763 | R-113 | 76.1 | 6.38 | -8.32 | -16.9497
1764 | R-113 | 76.2 | 6.39 | -8.31 | -16.9212
1765 | R-113 | 76.3 | 6.4 | -8.3 | -16.8927
1766 | R-113 | 76.4 | 6.42 | -8.28 | -16.8642
1767 | R-113 | 76.5 | 6.43 | -8.27 | -16.8357
1768 | R-113 | 76.6 | 6.45 | -8.25 | -16.8051
1769 | R-113 | 76.7 | 6.46 | -8.24 | -16.7766
1770 | R-113 | 76.8 | 6.47 | -8.23 | -16.7481
1771 | R-113 | 76.9 | 6.49 | -8.21 | -16.7196
1772 | R-113 | 77 | 6.5 | -8.2 | -16.6911
1773 | R-113 | 77.1 | 6.52 | -8.18 | -16.6626
1774 | R-113 | 77.2 | 6.53 | -8.17 | -16.6321
1775 | R-113 | 77.3 | 6.54 | -8.15 | -16.6036
1776 | R-113 | 77.4 | 6.56 | -8.14 | -16.5751
1777 | R-113 | 77.5 | 6.57 | -8.13 | -16.5445
1778 | R-113 | 77.6 | 6.59 | -8.11 | -16.516
1779 | R-113 | 77.7 | 6.6 | -8.1 | -16.4875
1780 | R-113 | 77.8 | 6.62 | -8.08 | -16.457
1781 | R-113 | 77.9 | 6.63 | -8.07 | -16.4285
1782 | R-113 | 78 | 6.65 | -8.05 | -16.3979
1783 | R-113 | 78.1 | 6.66 | -8.04 | -16.3694
1784 | R-113 | 78.2 | 6.67 | -8.03 | -16.3389
1785 | R-113 | 78.3 | 6.69 | -8.01 | -16.3104
1786 | R-113 | 78.4 | 6.7 | -8 | -16.2799
1787 | R-113 | 78.5 | 6.72 | -7.98 | -16.2513
1788 | R-113 | 78.6 | 6.73 | -7.97 | -16.2208
1789 | R-113 | 78.7 | 6.75 | -7.95 | -16.1923
1790 | R-113 | 78.8 | 6.76 | -7.94 | -16.1618
1791 | R-113 | 78.9 | 6.78 | -7.92 | -16.1312
1792 | R-113 | 79 | 6.79 | -7.91 | -16.1027
1793 | R-113 | 79.1 | 6.81 | -7.89 | -16.0722
1794 | R-113 | 79.2 | 6.82 | -7.88 | -16.0416
1795 | R-113 | 79.3 | 6.84 | -7.86 | -16.0111
1796 | R-113 | 79.4 | 6.85 | -7.85 | -15.9826
1797 | R-113 | 79.5 | 6.87 | -7.84 | -15.9521
1798 | R-113 | 79.6 | 6.88 | -7.82 | -15.9215
1799 | R-113 | 79.7 | 6.9 | -7.81 | -15.891
1800 | R-113 | 79.8 | 6.91 | -7.79 | -15.8604
1801 | R-113 | 79.9 | 6.92 | -7.78 | -15.8299
1802 | R-113 | 80 | 6.94 | -7.76 | -15.7994
1803 | R-113 | 80.1 | 6.96 | -7.75 | -15.7688
1804 | R-113 | 80.2 | 6.97 | -7.73 | -15.7383
1805 | R-113 | 80.3 | 6.99 | -7.71 | -15.7077
1806 | R-113 | 80.4 | 7 | -7.7 | -15.6772
1807 | R-113 | 80.5 | 7.02 | -7.69 | -15.6467
1808 | R-113 | 80.6 | 7.03 | -7.67 | -15.6161
1809 | R-113 | 80.7 | 7.04 | -7.66 | -15.5856
1810 | R-113 | 80.8 | 7.06 | -7.64 | -15.555
1811 | R-113 | 80.9 | 7.08 | -7.62 | -15.5225
1812 | R-113 | 81 | 7.09 | -7.61 | -15.4919
1813 | R-113 | 81.1 | 7.11 | -7.59 | -15.4614
1814 | R-113 | 81.2 | 7.12 | -7.58 | -15.4308
1815 | R-113 | 81.3 | 7.14 | -7.56 | -15.3983
1816 | R-113 | 81.4 | 7.15 | -7.55 | -15.3677
1817 | R-113 | 81.5 | 7.17 | -7.53 | -15.3372
1818 | R-113 | 81.6 | 7.18 | -7.52 | -15.3046
1819 | R-113 | 81.7 | 7.2 | -7.5 | -15.2741
1820 | R-113 | 81.8 | 7.21 | -7.49 | -15.2415
1821 | R-113 | 81.9 | 7.23 | -7.47 | -15.211
1822 | R-113 | 82 | 7.24 | -7.46 | -15.1804
1823 | R-113 | 82.1 | 7.26 | -7.44 | -15.1478
1824 | R-113 | 82.2 | 7.28 | -7.42 | -15.1173
1825 | R-113 | 82.3 | 7.29 | -7.41 | -15.0847
1826 | R-113 | 82.4 | 7.31 | -7.39 | -15.0521
1827 | R-113 | 82.5 | 7.32 | -7.38 | -15.0216
1828 | R-113 | 82.6 | 7.34 | -7.36 | -14.989
1829 | R-113 | 82.7 | 7.35 | -7.35 | -14.9565
1830 | R-113 | 82.8 | 7.37 | -7.33 | -14.9259
1831 | R-113 | 82.9 | 7.38 | -7.32 | -14.8933
1832 | R-113 | 83 | 7.4 | -7.3 | -14.8608
1833 | R-113 | 83.1 | 7.42 | -7.28 | -14.8302
1834 | R-113 | 83.2 | 7.43 | -7.27 | -14.7977
1835 | R-113 | 83.3 | 7.45 | -7.25 | -14.7651
1836 | R-113 | 83.4 | 7.46 | -7.24 | -14.7325
1837 | R-113 | 83.5 | 7.48 | -7.22 | -14.6999
1838 | R-113 | 83.6 | 7.5 | -7.2 | -14.6673
1839 | R-113 | 83.7 | 7.51 | -7.19 | -14.6348
1840 | R-113 | 83.8 | 7.53 | -7.17 | -14.6022
1841 | R-113 | 83.9 | 7.54 | -7.16 | -14.5696
1842 | R-113 | 84 | 7.56 | -7.14 | -14.537
1843 | R-113 | 84.1 | 7.58 | -7.12 | -14.5045
1844 | R-113 | 84.2 | 7.59 | -7.11 | -14.4719
1845 | R-113 | 84.3 | 7.61 | -7.09 | -14.4393
1846 | R-113 | 84.4 | 7.62 | -7.08 | -14.4067
1847 | R-113 | 84.5 | 7.64 | -7.06 | -14.3742
1848 | R-113 | 84.6 | 7.66 | -7.04 | -14.3416
1849 | R-113 | 84.7 | 7.67 | -7.03 | -14.309
1850 | R-113 | 84.8 | 7.69 | -7.01 | -14.2744
1851 | R-113 | 84.9 | 7.71 | -7 | -14.2418
1852 | R-113 | 85 | 7.72 | -6.98 | -14.2092
1853 | R-113 | 85.1 | 7.74 | -6.96 | -14.1746
1854 | R-113 | 85.2 | 7.75 | -6.95 | -14.1421
1855 | R-113 | 85.3 | 7.77 | -6.93 | -14.1095
1856 | R-113 | 85.4 | 7.79 | -6.91 | -14.0749
1857 | R-113 | 85.5 | 7.8 | -6.9 | -14.0423
1858 | R-113 | 85.6 | 7.82 | -6.88 | -14.0097
1859 | R-113 | 85.7 | 7.84 | -6.86 | -13.9751
1860 | R-113 | 85.8 | 7.85 | -6.85 | -13.9425
1861 | R-113 | 85.9 | 7.87 | -6.83 | -13.9079
1862 | R-113 | 86 | 7.89 | -6.81 | -13.8733
1863 | R-113 | 86.1 | 7.9 | -6.8 | -13.8407
1864 | R-113 | 86.2 | 7.92 | -6.78 | -13.8061
1865 | R-113 | 86.3 | 7.94 | -6.77 | -13.7735
1866 | R-113 | 86.4 | 7.95 | -6.75 | -13.7389
1867 | R-113 | 86.5 | 7.97 | -6.73 | -13.7043
1868 | R-113 | 86.6 | 7.99 | -6.71 | -13.6717
1869 | R-113 | 86.7 | 8 | -6.7 | -13.6371
1870 | R-113 | 86.8 | 8.02 | -6.68 | -13.6025
1871 | R-113 | 86.9 | 8.04 | -6.66 | -13.5679
1872 | R-113 | 87 | 8.05 | -6.65 | -13.5333
1873 | R-113 | 87.1 | 8.07 | -6.63 | -13.4987
1874 | R-113 | 87.2 | 8.09 | -6.61 | -13.4661
1875 | R-113 | 87.3 | 8.1 | -6.6 | -13.4315
1876 | R-113 | 87.4 | 8.12 | -6.58 | -13.3969
1877 | R-113 | 87.5 | 8.14 | -6.56 | -13.3623
1878 | R-113 | 87.6 | 8.15 | -6.55 | -13.3277
1879 | R-113 | 87.7 | 8.17 | -6.53 | -13.293
1880 | R-113 | 87.8 | 8.19 | -6.51 | -13.2584
1881 | R-113 | 87.9 | 8.21 | -6.5 | -13.2238
1882 | R-113 | 88 | 8.22 | -6.48 | -13.1872
1883 | R-113 | 88.1 | 8.24 | -6.46 | -13.1526
1884 | R-113 | 88.2 | 8.26 | -6.44 | -13.118
1885 | R-113 | 88.3 | 8.27 | -6.43 | -13.0833
1886 | R-113 | 88.4 | 8.29 | -6.41 | -13.0487
1887 | R-113 | 88.5 | 8.31 | -6.39 | -13.0121
1888 | R-113 | 88.6 | 8.33 | -6.37 | -12.9775
1889 | R-113 | 88.7 | 8.34 | -6.36 | -12.9428
1890 | R-113 | 88.8 | 8.36 | -6.34 | -12.9082
1891 | R-113 | 88.9 | 8.38 | -6.32 | -12.8716
1892 | R-113 | 89 | 8.39 | -6.3 | -12.837
1893 | R-113 | 89.1 | 8.41 | -6.29 | -12.8003
1894 | R-113 | 89.2 | 8.43 | -6.27 | -12.7657
1895 | R-113 | 89.3 | 8.45 | -6.25 | -12.7291
1896 | R-113 | 89.4 | 8.46 | -6.24 | -12.6945
1897 | R-113 | 89.5 | 8.48 | -6.22 | -12.6578
1898 | R-113 | 89.6 | 8.5 | -6.2 | -12.6232
1899 | R-113 | 89.7 | 8.52 | -6.18 | -12.5866
1900 | R-113 | 89.8 | 8.54 | -6.16 | -12.5499
1901 | R-113 | 89.9 | 8.55 | -6.15 | -12.5153
1902 | R-113 | 90 | 8.57 | -6.13 | -12.4786
1903 | R-113 | 90.1 | 8.59 | -6.11 | -12.442
1904 | R-113 | 90.2 | 8.61 | -6.09 | -12.4074
1905 | R-113 | 90.3 | 8.62 | -6.08 | -12.3707
1906 | R-113 | 90.4 | 8.64 | -6.06 | -12.3341
1907 | R-113 | 90.5 | 8.66 | -6.04 | -12.2974
1908 | R-113 | 90.6 | 8.68 | -6.02 | -12.2608
1909 | R-113 | 90.7 | 8.7 | -6 | -12.2262
1910 | R-113 | 90.8 | 8.71 | -5.99 | -12.1895
1911 | R-113 | 90.9 | 8.73 | -5.97 | -12.1529
1912 | R-113 | 91 | 8.75 | -5.95 | -12.1162
1913 | R-113 | 91.1 | 8.77 | -5.93 | -12.0796
1914 | R-113 | 91.2 | 8.79 | -5.92 | -12.0429
1915 | R-113 | 91.3 | 8.8 | -5.9 | -12.0063
1916 | R-113 | 91.4 | 8.82 | -5.88 | -11.9676
1917 | R-113 | 91.5 | 8.84 | -5.86 | -11.931
1918 | R-113 | 91.6 | 8.86 | -5.84 | -11.8943
1919 | R-113 | 91.7 | 8.88 | -5.82 | -11.8577
1920 | R-113 | 91.8 | 8.89 | -5.81 | -11.821
1921 | R-113 | 91.9 | 8.91 | -5.79 | -11.7844
1922 | R-113 | 92 | 8.93 | -5.77 | -11.7457
1923 | R-113 | 92.1 | 8.95 | -5.75 | -11.709
1924 | R-113 | 92.2 | 8.97 | -5.73 | -11.6724
1925 | R-113 | 92.3 | 8.99 | -5.71 | -11.6337
1926 | R-113 | 92.4 | 9 | -5.7 | -11.5971
1927 | R-113 | 92.5 | 9.02 | -5.68 | -11.5584
1928 | R-113 | 92.6 | 9.04 | -5.66 | -11.5217
1929 | R-113 | 92.7 | 9.06 | -5.64 | -11.483
1930 | R-113 | 92.8 | 9.08 | -5.62 | -11.4464
1931 | R-113 | 92.9 | 9.1 | -5.6 | -11.4077
1932 | R-113 | 93 | 9.12 | -5.59 | -11.3711
1933 | R-113 | 93.1 | 9.13 | -5.57 | -11.3324
1934 | R-113 | 93.2 | 9.15 | -5.55 | -11.2957
1935 | R-113 | 93.3 | 9.17 | -5.53 | -11.257
1936 | R-113 | 93.4 | 9.19 | -5.51 | -11.2184
1937 | R-113 | 93.5 | 9.21 | -5.49 | -11.1817
1938 | R-113 | 93.6 | 9.23 | -5.47 | -11.143
1939 | R-113 | 93.7 | 9.25 | -5.45 | -11.1043
1940 | R-113 | 93.8 | 9.27 | -5.44 | -11.0657
1941 | R-113 | 93.9 | 9.28 | -5.42 | -11.027
1942 | R-113 | 94 | 9.3 | -5.4 | -10.9883
1943 | R-113 | 94.1 | 9.32 | -5.38 | -10.9516
1944 | R-113 | 94.2 | 9.34 | -5.36 | -10.913
1945 | R-113 | 94.3 | 9.36 | -5.34 | -10.8743
1946 | R-113 | 94.4 | 9.38 | -5.32 | -10.8356
1947 | R-113 | 94.5 | 9.4 | -5.3 | -10.7969
1948 | R-113 | 94.6 | 9.42 | -5.28 | -10.7582
1949 | R-113 | 94.7 | 9.44 | -5.26 | -10.7175
1950 | R-113 | 94.8 | 9.46 | -5.25 | -10.6788
1951 | R-113 | 94.9 | 9.47 | -5.23 | -10.6401
1952 | R-113 | 95 | 9.49 | -5.21 | -10.6014
1953 | R-113 | 95.1 | 9.51 | -5.19 | -10.5628
1954 | R-113 | 95.2 | 9.53 | -5.17 | -10.5241
1955 | R-113 | 95.3 | 9.55 | -5.15 | -10.4834
1956 | R-113 | 95.4 | 9.57 | -5.13 | -10.4447
1957 | R-113 | 95.5 | 9.59 | -5.11 | -10.406
1958 | R-113 | 95.6 | 9.61 | -5.09 | -10.3653
1959 | R-113 | 95.7 | 9.63 | -5.07 | -10.3266
1960 | R-113 | 95.8 | 9.65 | -5.05 | -10.2879
1961 | R-113 | 95.9 | 9.67 | -5.03 | -10.2472
1962 | R-113 | 96 | 9.69 | -5.01 | -10.2085
1963 | R-113 | 96.1 | 9.71 | -4.99 | -10.1678
1964 | R-113 | 96.2 | 9.72 | -4.98 | -10.1291
1965 | R-113 | 96.3 | 9.75 | -4.96 | -10.0884
1966 | R-113 | 96.4 | 9.77 | -4.94 | -10.0477
1967 | R-113 | 96.5 | 9.78 | -4.92 | -10.009
1968 | R-113 | 96.6 | 9.8 | -4.9 | -9.9683
1969 | R-113 | 96.7 | 9.82 | -4.88 | -9.9275
1970 | R-113 | 96.8 | 9.84 | -4.86 | -9.8888
1971 | R-113 | 96.9 | 9.86 | -4.84 | -9.8481
1972 | R-113 | 97 | 9.88 | -4.82 | -9.8074
1973 | R-113 | 97.1 | 9.9 | -4.8 | -9.7667
1974 | R-113 | 97.2 | 9.92 | -4.78 | -9.726
1975 | R-113 | 97.3 | 9.94 | -4.76 | -9.6852
1976 | R-113 | 97.4 | 9.96 | -4.74 | -9.6445
1977 | R-113 | 97.5 | 9.98 | -4.72 | -9.6059
1978 | R-113 | 97.6 | 10 | -4.7 | -9.5692
1979 | R-113 | 97.7 | 10.02 | -4.68 | -9.5285
1980 | R-113 | 97.8 | 10.04 | -4.66 | -9.4878
1981 | R-113 | 97.9 | 10.06 | -4.64 | -9.447
1982 | R-113 | 98 | 10.08 | -4.62 | -9.4063
1983 | R-113 | 98.1 | 10.1 | -4.6 | -9.3656
1984 | R-113 | 98.2 | 10.12 | -4.58 | -9.3249
1985 | R-113 | 98.3 | 10.14 | -4.56 | -9.2842
1986 | R-113 | 98.4 | 10.16 | -4.54 | -9.2434
1987 | R-113 | 98.5 | 10.18 | -4.52 | -9.2027
1988 | R-113 | 98.6 | 10.2 | -4.5 | -9.162
1989 | R-113 | 98.7 | 10.22 | -4.48 | -9.1213
1990 | R-113 | 98.8 | 10.24 | -4.46 | -9.0806
1991 | R-113 | 98.9 | 10.27 | -4.43 | -9.0195
1992 | R-113 | 99 | 10.29 | -4.41 | -8.9788
1993 | R-113 | 99.1 | 10.31 | -4.39 | -8.938
1994 | R-113 | 99.2 | 10.33 | -4.37 | -8.8973
1995 | R-113 | 99.3 | 10.35 | -4.35 | -8.8566
1996 | R-113 | 99.4 | 10.37 | -4.33 | -8.8159
1997 | R-113 | 99.5 | 10.39 | -4.31 | -8.7752
1998 | R-113 | 99.6 | 10.41 | -4.29 | -8.7344
1999 | R-113 | 99.7 | 10.43 | -4.27 | -8.6937
2000 | R-113 | 99.8 | 10.45 | -4.25 | -8.653
2001 | R-113 | 99.9 | 10.47 | -4.23 | -8.6123
2002 | R-113 | 100 | 10.49 | -4.21 | -8.5716
2003 | R-113 | 100.1 | 10.51 | -4.19 | -8.5308
2004 | R-113 | 100.2 | 10.53 | -4.17 | -8.4901
2005 | R-113 | 100.3 | 10.55 | -4.15 | -8.4494
2006 | R-113 | 100.4 | 10.58 | -4.12 | -8.3883
2007 | R-113 | 100.5 | 10.6 | -4.1 | -8.3476
2008 | R-113 | 100.6 | 10.62 | -4.08 | -8.3069
2009 | R-113 | 100.7 | 10.64 | -4.06 | -8.2662
2010 | R-113 | 100.8 | 10.66 | -4.04 | -8.2254
2011 | R-113 | 100.9 | 10.68 | -4.02 | -8.1847
2012 | R-113 | 101 | 10.7 | -4 | -8.144
2013 | R-113 | 101.1 | 10.72 | -3.98 | -8.1033
2014 | R-113 | 101.2 | 10.74 | -3.96 | -8.0626
2015 | R-113 | 101.3 | 10.76 | -3.94 | -8.0218
2016 | R-113 | 101.4 | 10.79 | -3.91 | -7.9608
2017 | R-113 | 101.5 | 10.81 | -3.89 | -7.92
2018 | R-113 | 101.6 | 10.83 | -3.87 | -7.8793
2019 | R-113 | 101.7 | 10.85 | -3.85 | -7.8386
2020 | R-113 | 101.8 | 10.87 | -3.83 | -7.7979
2021 | R-113 | 101.9 | 10.89 | -3.81 | -7.7572
2022 | R-113 | 102 | 10.91 | -3.79 | -7.7164
2023 | R-113 | 102.1 | 10.94 | -3.76 | -7.6554
2024 | R-113 | 102.2 | 10.96 | -3.74 | -7.6146
2025 | R-113 | 102.3 | 10.98 | -3.72 | -7.5739
2026 | R-113 | 102.4 | 11 | -3.7 | -7.5332
2027 | R-113 | 102.5 | 11.02 | -3.68 | -7.4925
2028 | R-113 | 102.6 | 11.04 | -3.66 | -7.4518
2029 | R-113 | 102.7 | 11.06 | -3.64 | -7.411
2030 | R-113 | 102.8 | 11.09 | -3.61 | -7.35
2031 | R-113 | 102.9 | 11.11 | -3.59 | -7.3092
2032 | R-113 | 103 | 11.13 | -3.57 | -7.2685
2033 | R-113 | 103.1 | 11.15 | -3.55 | -7.2278
2034 | R-113 | 103.2 | 11.17 | -3.53 | -7.1871
2035 | R-113 | 103.3 | 11.19 | -3.51 | -7.1464
2036 | R-113 | 103.4 | 11.22 | -3.48 | -7.0853
2037 | R-113 | 103.5 | 11.24 | -3.46 | -7.0446
2038 | R-113 | 103.6 | 11.26 | -3.44 | -7.0038
2039 | R-113 | 103.7 | 11.28 | -3.42 | -6.9631
2040 | R-113 | 103.8 | 11.3 | -3.4 | -6.9224
2041 | R-113 | 103.9 | 11.33 | -3.37 | -6.8613
2042 | R-113 | 104 | 11.35 | -3.35 | -6.8206
2043 | R-113 | 104.1 | 11.37 | -3.33 | -6.7799
2044 | R-113 | 104.2 | 11.39 | -3.31 | -6.7392
2045 | R-113 | 104.3 | 11.42 | -3.28 | -6.6781
2046 | R-113 | 104.4 | 11.44 | -3.26 | -6.6374
2047 | R-113 | 104.5 | 11.46 | -3.24 | -6.5966
2048 | R-113 | 104.6 | 11.48 | -3.22 | -6.5559
2049 | R-113 | 104.7 | 11.5 | -3.2 | -6.5152
2050 | R-113 | 104.8 | 11.53 | -3.17 | -6.4541
2051 | R-113 | 104.9 | 11.55 | -3.15 | -6.4134
2052 | R-113 | 105 | 11.57 | -3.13 | -6.3727
2053 | R-113 | 105.1 | 11.59 | -3.11 | -6.332
2054 | R-113 | 105.2 | 11.62 | -3.08 | -6.2709
2055 | R-113 | 105.3 | 11.64 | -3.06 | -6.2302
2056 | R-113 | 105.4 | 11.66 | -3.04 | -6.1894
2057 | R-113 | 105.5 | 11.68 | -3.02 | -6.1487
2058 | R-113 | 105.6 | 11.71 | -2.99 | -6.0876
2059 | R-113 | 105.7 | 11.73 | -2.97 | -6.0469
2060 | R-113 | 105.8 | 11.75 | -2.95 | -6.0062
2061 | R-113 | 105.9 | 11.77 | -2.93 | -5.9655
2062 | R-113 | 106 | 11.8 | -2.9 | -5.9044
2063 | R-113 | 106.1 | 11.82 | -2.88 | -5.8637
2064 | R-113 | 106.2 | 11.84 | -2.86 | -5.823
2065 | R-113 | 106.3 | 11.87 | -2.83 | -5.7619
2066 | R-113 | 106.4 | 11.89 | -2.81 | -5.7212
2067 | R-113 | 106.5 | 11.91 | -2.79 | -5.6804
2068 | R-113 | 106.6 | 11.93 | -2.77 | -5.6397
2069 | R-113 | 106.7 | 11.96 | -2.74 | -5.5786
2070 | R-113 | 106.8 | 11.98 | -2.72 | -5.5379
2071 | R-113 | 106.9 | 12 | -2.7 | -5.4972
2072 | R-113 | 107 | 12.03 | -2.67 | -5.4361
2073 | R-113 | 107.1 | 12.05 | -2.65 | -5.3954
2074 | R-113 | 107.2 | 12.07 | -2.63 | -5.3547
2075 | R-113 | 107.3 | 12.1 | -2.6 | -5.2936
2076 | R-113 | 107.4 | 12.12 | -2.58 | -5.2529
2077 | R-113 | 107.5 | 12.14 | -2.56 | -5.2122
2078 | R-113 | 107.6 | 12.17 | -2.53 | -5.1511
2079 | R-113 | 107.7 | 12.19 | -2.51 | -5.1104
2080 | R-113 | 107.8 | 12.21 | -2.49 | -5.0696
2081 | R-113 | 107.9 | 12.24 | -2.46 | -5.0086
2082 | R-113 | 108 | 12.26 | -2.44 | -4.9678
2083 | R-113 | 108.1 | 12.28 | -2.42 | -4.9271
2084 | R-113 | 108.2 | 12.31 | -2.39 | -4.866
2085 | R-113 | 108.3 | 12.33 | -2.37 | -4.8253
2086 | R-113 | 108.4 | 12.35 | -2.35 | -4.7846
2087 | R-113 | 108.5 | 12.38 | -2.32 | -4.7235
2088 | R-113 | 108.6 | 12.4 | -2.3 | -4.6828
2089 | R-113 | 108.7 | 12.43 | -2.27 | -4.6217
2090 | R-113 | 108.8 | 12.45 | -2.25 | -4.581
2091 | R-113 | 108.9 | 12.47 | -2.23 | -4.5403
2092 | R-113 | 109 | 12.5 | -2.2 | -4.4792
2093 | R-113 | 109.1 | 12.52 | -2.18 | -4.4385
2094 | R-113 | 109.2 | 12.54 | -2.16 | -4.3978
2095 | R-113 | 109.3 | 12.57 | -2.13 | -4.3367
2096 | R-113 | 109.4 | 12.59 | -2.11 | -4.296
2097 | R-113 | 109.5 | 12.62 | -2.08 | -4.2349
2098 | R-113 | 109.6 | 12.64 | -2.06 | -4.1942
2099 | R-113 | 109.7 | 12.66 | -2.04 | -4.1534
2100 | R-113 | 109.8 | 12.69 | -2.01 | -4.0924
2101 | R-113 | 109.9 | 12.71 | -1.99 | -4.0516
2102 | R-113 | 110 | 12.74 | -1.96 | -3.9906
2103 | R-113 | 110.1 | 12.76 | -1.94 | -3.9498
2104 | R-113 | 110.2 | 12.79 | -1.91 | -3.8888
2105 | R-113 | 110.3 | 12.81 | -1.89 | -3.848
2106 | R-113 | 110.4 | 12.83 | -1.87 | -3.8073
2107 | R-113 | 110.5 | 12.86 | -1.84 | -3.7462
2108 | R-113 | 110.6 | 12.88 | -1.82 | -3.7055
2109 | R-113 | 110.7 | 12.91 | -1.79 | -3.6444
2110 | R-113 | 110.8 | 12.93 | -1.77 | -3.6037
2111 | R-113 | 110.9 | 12.96 | -1.74 | -3.5426
2112 | R-113 | 111 | 12.98 | -1.72 | -3.5019
2113 | R-113 | 111.1 | 13 | -1.7 | -3.4612
2114 | R-113 | 111.2 | 13.03 | -1.67 | -3.4001
2115 | R-113 | 111.3 | 13.05 | -1.65 | -3.3594
2116 | R-113 | 111.4 | 13.08 | -1.62 | -3.2983
2117 | R-113 | 111.5 | 13.1 | -1.6 | -3.2576
2118 | R-113 | 111.6 | 13.13 | -1.57 | -3.1965
2119 | R-113 | 111.7 | 13.15 | -1.55 | -3.1558
2120 | R-113 | 111.8 | 13.18 | -1.52 | -3.0947
2121 | R-113 | 111.9 | 13.2 | -1.5 | -3.054
2122 | R-113 | 112 | 13.23 | -1.47 | -2.9929
2123 | R-113 | 112.1 | 13.25 | -1.45 | -2.9522
2124 | R-113 | 112.2 | 13.28 | -1.42 | -2.8911
2125 | R-113 | 112.3 | 13.3 | -1.4 | -2.8504
2126 | R-113 | 112.4 | 13.33 | -1.37 | -2.7893
2127 | R-113 | 112.5 | 13.35 | -1.35 | -2.7486
2128 | R-113 | 112.6 | 13.38 | -1.32 | -2.6875
2129 | R-113 | 112.7 | 13.4 | -1.3 | -2.6468
2130 | R-113 | 112.8 | 13.43 | -1.27 | -2.5857
2131 | R-113 | 112.9 | 13.45 | -1.25 | -2.545
2132 | R-113 | 113 | 13.48 | -1.22 | -2.4839
2133 | R-113 | 113.1 | 13.5 | -1.2 | -2.4432
2134 | R-113 | 113.2 | 13.53 | -1.17 | -2.3821
2135 | R-113 | 113.3 | 13.55 | -1.15 | -2.3414
2136 | R-113 | 113.4 | 13.58 | -1.12 | -2.2803
2137 | R-113 | 113.5 | 13.61 | -1.09 | -2.2192
2138 | R-113 | 113.6 | 13.63 | -1.07 | -2.1785
2139 | R-113 | 113.7 | 13.66 | -1.04 | -2.1174
2140 | R-113 | 113.8 | 13.68 | -1.02 | -2.0767
2141 | R-113 | 113.9 | 13.71 | -0.99 | -2.0156
2142 | R-113 | 114 | 13.73 | -0.97 | -1.9749
2143 | R-113 | 114.1 | 13.76 | -0.94 | -1.9138
2144 | R-113 | 114.2 | 13.78 | -0.92 | -1.8731
2145 | R-113 | 114.3 | 13.81 | -0.89 | -1.812
2146 | R-113 | 114.4 | 13.84 | -0.86 | -1.751
2147 | R-113 | 114.5 | 13.86 | -0.84 | -1.7102
2148 | R-113 | 114.6 | 13.89 | -0.81 | -1.6492
2149 | R-113 | 114.7 | 13.91 | -0.79 | -1.6084
2150 | R-113 | 114.8 | 13.94 | -0.76 | -1.5474
2151 | R-113 | 114.9 | 13.97 | -0.73 | -1.4863
2152 | R-113 | 115 | 13.99 | -0.71 | -1.4456
2153 | R-113 | 115.1 | 14.02 | -0.68 | -1.3845
2154 | R-113 | 115.2 | 14.04 | -0.66 | -1.3438
2155 | R-113 | 115.3 | 14.07 | -0.63 | -1.2827
2156 | R-113 | 115.4 | 14.1 | -0.6 | -1.2216
2157 | R-113 | 115.5 | 14.12 | -0.58 | -1.1809
2158 | R-113 | 115.6 | 14.15 | -0.55 | -1.1198
2159 | R-113 | 115.7 | 14.17 | -0.53 | -1.0791
2160 | R-113 | 115.8 | 14.2 | -0.5 | -1.018
2161 | R-113 | 115.9 | 14.23 | -0.47 | -0.95692
2162 | R-113 | 116 | 14.25 | -0.45 | -0.9162
2163 | R-113 | 116.1 | 14.28 | -0.42 | -0.85512
2164 | R-113 | 116.2 | 14.31 | -0.39 | -0.79404
2165 | R-113 | 116.3 | 14.33 | -0.37 | -0.75332
2166 | R-113 | 116.4 | 14.36 | -0.34 | -0.69224
2167 | R-113 | 116.5 | 14.39 | -0.31 | -0.63116
2168 | R-113 | 116.6 | 14.41 | -0.29 | -0.59044
2169 | R-113 | 116.7 | 14.44 | -0.26 | -0.52936
2170 | R-113 | 116.8 | 14.47 | -0.23 | -0.46828
2171 | R-113 | 116.9 | 14.49 | -0.21 | -0.42756
2172 | R-113 | 117 | 14.52 | -0.18 | -0.36648
2173 | R-113 | 117.1 | 14.55 | -0.15 | -0.3054
2174 | R-113 | 117.2 | 14.57 | -0.13 | -0.26468
2175 | R-113 | 117.3 | 14.6 | -0.1 | -0.2036
2176 | R-113 | 117.4 | 14.63 | -0.07 | -0.14252
2177 | R-113 | 117.5 | 14.65 | -0.05 | -0.1018
2178 | R-113 | 117.6 | 14.68 | -0.02 | -0.04072
2179 | R-113 | 117.7 | 14.71 | 0.01 | 0.02036
2180 | R-113 | 117.8 | 14.74 | 0.04 | 0.08144
2181 | R-113 | 117.9 | 14.76 | 0.06 | 0.12216
2182 | R-113 | 118 | 14.79 | 0.09 | 0.18324
2183 | R-113 | 118.1 | 14.82 | 0.12 | 0.24432
2184 | R-113 | 118.2 | 14.84 | 0.14 | 0.28504
2185 | R-113 | 118.3 | 14.87 | 0.17 | 0.34612
2186 | R-113 | 118.4 | 14.9 | 0.2 | 0.4072
2187 | R-113 | 118.5 | 14.93 | 0.23 | 0.46828
2188 | R-113 | 118.6 | 14.95 | 0.25 | 0.509
2189 | R-113 | 118.7 | 14.98 | 0.28 | 0.57008
2190 | R-113 | 118.8 | 15.01 | 0.31 | 0.63116
2191 | R-113 | 118.9 | 15.04 | 0.34 | 0.69224
2192 | R-113 | 119 | 15.06 | 0.36 | 0.73296
2193 | R-113 | 119.1 | 15.09 | 0.39 | 0.79404
2194 | R-113 | 119.2 | 15.12 | 0.42 | 0.85512
2195 | R-113 | 119.3 | 15.15 | 0.45 | 0.9162
2196 | R-113 | 119.4 | 15.17 | 0.47 | 0.95692
2197 | R-113 | 119.5 | 15.2 | 0.5 | 1.018
2198 | R-113 | 119.6 | 15.23 | 0.53 | 1.0791
2199 | R-113 | 119.7 | 15.26 | 0.56 | 1.1402
2200 | R-113 | 119.8 | 15.29 | 0.59 | 1.2012
2201 | R-113 | 119.9 | 15.31 | 0.61 | 1.242
2202 | R-113 | 120 | 15.34 | 0.64 | 1.303
2203 | 3 | 35 | 13.65 | -1.05 | -2.1378
2204 | 3 | 35.1 | 13.68 | -1.02 | -2.0767
2205 | 3 | 35.2 | 13.71 | -0.99 | -2.0156
2206 | 3 | 35.3 | 13.74 | -0.96 | -1.9546
2207 | 3 | 35.4 | 13.77 | -0.93 | -1.8935
2208 | 3 | 35.5 | 13.79 | -0.91 | -1.8528
2209 | 3 | 35.6 | 13.82 | -0.88 | -1.7917
2210 | 3 | 35.7 | 13.85 | -0.85 | -1.7306
2211 | 3 | 35.8 | 13.88 | -0.82 | -1.6695
2212 | 3 | 35.9 | 13.91 | -0.79 | -1.6084
2213 | 3 | 36 | 13.94 | -0.76 | -1.5474
2214 | 3 | 36.1 | 13.97 | -0.73 | -1.4863
2215 | 3 | 36.2 | 14 | -0.7 | -1.4252
2216 | 3 | 36.3 | 14.03 | -0.67 | -1.3641
2217 | 3 | 36.4 | 14.06 | -0.64 | -1.303
2218 | 3 | 36.5 | 14.09 | -0.61 | -1.242
2219 | 3 | 36.6 | 14.12 | -0.58 | -1.1809
2220 | 3 | 36.7 | 14.15 | -0.55 | -1.1198
2221 | 3 | 36.8 | 14.18 | -0.52 | -1.0587
2222 | 3 | 36.9 | 14.21 | -0.49 | -0.99764
2223 | 3 | 37 | 14.25 | -0.45 | -0.9162
2224 | 3 | 37.1 | 14.28 | -0.42 | -0.85512
2225 | 3 | 37.2 | 14.31 | -0.39 | -0.79404
2226 | 3 | 37.3 | 14.34 | -0.36 | -0.73296
2227 | 3 | 37.4 | 14.37 | -0.33 | -0.67188
2228 | 3 | 37.5 | 14.4 | -0.3 | -0.6108
2229 | 3 | 37.6 | 14.43 | -0.27 | -0.54972
2230 | 3 | 37.7 | 14.46 | -0.24 | -0.48864
2231 | 3 | 37.8 | 14.49 | -0.21 | -0.42756
2232 | 3 | 37.9 | 14.52 | -0.18 | -0.36648
2233 | 3 | 38 | 14.55 | -0.15 | -0.3054
2234 | 3 | 38.1 | 14.58 | -0.12 | -0.24432
2235 | 3 | 38.2 | 14.61 | -0.09 | -0.18324
2236 | 3 | 38.3 | 14.64 | -0.06 | -0.12216
2237 | 3 | 38.4 | 14.68 | -0.02 | -0.04072
2238 | 3 | 38.5 | 14.71 | 0.01 | 0.02036
2239 | 3 | 38.6 | 14.74 | 0.04 | 0.08144
2240 | 3 | 38.7 | 14.77 | 0.07 | 0.14252
2241 | 3 | 38.8 | 14.8 | 0.1 | 0.2036
2242 | 3 | 38.9 | 14.83 | 0.13 | 0.26468
2243 | 3 | 39 | 14.86 | 0.16 | 0.32576
2244 | 3 | 39.1 | 14.89 | 0.19 | 0.38684
2245 | 3 | 39.2 | 14.93 | 0.23 | 0.46828
2246 | 3 | 39.3 | 14.96 | 0.26 | 0.52936
2247 | 3 | 39.4 | 14.99 | 0.29 | 0.59044
2248 | 3 | 39.5 | 15.02 | 0.32 | 0.65152
2249 | 3 | 39.6 | 15.05 | 0.35 | 0.7126
2250 | 3 | 39.7 | 15.08 | 0.38 | 0.77368
2251 | 3 | 39.8 | 15.12 | 0.42 | 0.85512
2252 | 3 | 39.9 | 15.15 | 0.45 | 0.9162
2253 | 3 | 40 | 15.18 | 0.48 | 0.97728
2254 | 3 | 40.1 | 15.21 | 0.51 | 1.0384
2255 | 3 | 40.2 | 15.24 | 0.54 | 1.0994
2256 | 3 | 40.3 | 15.28 | 0.58 | 1.1809
2257 | 3 | 40.4 | 15.31 | 0.61 | 1.242
2258 | 3 | 40.5 | 15.34 | 0.64 | 1.303
2259 | 3 | 40.6 | 15.37 | 0.67 | 1.3641
2260 | 3 | 40.7 | 15.41 | 0.71 | 1.4456
2261 | 3 | 40.8 | 15.44 | 0.74 | 1.5066
2262 | 3 | 40.9 | 15.47 | 0.77 | 1.5677
2263 | 3 | 41 | 15.5 | 0.8 | 1.6288
2264 | 3 | 41.1 | 15.53 | 0.83 | 1.6899
2265 | 3 | 41.2 | 15.57 | 0.87 | 1.7713
2266 | 3 | 41.3 | 15.6 | 0.9 | 1.8324
2267 | 3 | 41.4 | 15.63 | 0.93 | 1.8935
2268 | 3 | 41.5 | 15.67 | 0.97 | 1.9749
2269 | 3 | 41.6 | 15.7 | 1 | 2.036
2270 | 3 | 41.7 | 15.73 | 1.03 | 2.0971
2271 | 3 | 41.8 | 15.76 | 1.06 | 2.1582
2272 | 3 | 41.9 | 15.8 | 1.1 | 2.2396
2273 | 3 | 42 | 15.83 | 1.13 | 2.3007
2274 | 3 | 42.1 | 15.86 | 1.16 | 2.3618
2275 | 3 | 42.2 | 15.9 | 1.2 | 2.4432
2276 | 3 | 42.3 | 15.93 | 1.23 | 2.5043
2277 | 3 | 42.4 | 15.96 | 1.26 | 2.5654
2278 | 3 | 42.5 | 16 | 1.3 | 2.6468
2279 | 3 | 42.6 | 16.03 | 1.33 | 2.7079
2280 | 3 | 42.7 | 16.06 | 1.36 | 2.769
2281 | 3 | 42.8 | 16.1 | 1.4 | 2.8504
2282 | 3 | 42.9 | 16.13 | 1.43 | 2.9115
2283 | 3 | 43 | 16.16 | 1.46 | 2.9726
2284 | 3 | 43.1 | 16.2 | 1.5 | 3.054
2285 | 3 | 43.2 | 16.23 | 1.53 | 3.1151
2286 | 3 | 43.3 | 16.26 | 1.56 | 3.1762
2287 | 3 | 43.4 | 16.3 | 1.6 | 3.2576
2288 | 3 | 43.5 | 16.33 | 1.63 | 3.3187
2289 | 3 | 43.6 | 16.36 | 1.66 | 3.3798
2290 | 3 | 43.7 | 16.4 | 1.7 | 3.4612
2291 | 3 | 43.8 | 16.43 | 1.73 | 3.5223
2292 | 3 | 43.9 | 16.47 | 1.77 | 3.6037
2293 | 3 | 44 | 16.5 | 1.8 | 3.6648
2294 | 3 | 44.1 | 16.53 | 1.83 | 3.7259
2295 | 3 | 44.2 | 16.57 | 1.87 | 3.8073
2296 | 3 | 44.3 | 16.6 | 1.9 | 3.8684
2297 | 3 | 44.4 | 16.64 | 1.94 | 3.9498
2298 | 3 | 44.5 | 16.67 | 1.97 | 4.0109
2299 | 3 | 44.6 | 16.71 | 2.01 | 4.0924
2300 | 3 | 44.7 | 16.74 | 2.04 | 4.1534
2301 | 3 | 44.8 | 16.78 | 2.08 | 4.2349
2302 | 3 | 44.9 | 16.81 | 2.11 | 4.296
2303 | 3 | 45 | 16.84 | 2.14 | 4.357
2304 | 3 | 45.1 | 16.88 | 2.18 | 4.4385
2305 | 3 | 45.2 | 16.91 | 2.21 | 4.4996
2306 | 3 | 45.3 | 16.95 | 2.25 | 4.581
2307 | 3 | 45.4 | 16.98 | 2.28 | 4.6421
2308 | 3 | 45.5 | 17.02 | 2.32 | 4.7235
2309 | 3 | 45.6 | 17.05 | 2.35 | 4.7846
2310 | 3 | 45.7 | 17.09 | 2.39 | 4.866
2311 | 3 | 45.8 | 17.12 | 2.42 | 4.9271
2312 | 3 | 45.9 | 17.16 | 2.46 | 5.0086
2313 | 3 | 46 | 17.19 | 2.49 | 5.0696
2314 | 3 | 46.1 | 17.23 | 2.53 | 5.1511
2315 | 3 | 46.2 | 17.26 | 2.56 | 5.2122
2316 | 3 | 46.3 | 17.3 | 2.6 | 5.2936
2317 | 3 | 46.4 | 17.33 | 2.63 | 5.3547
2318 | 3 | 46.5 | 17.37 | 2.67 | 5.4361
2319 | 3 | 46.6 | 17.41 | 2.71 | 5.5176
2320 | 3 | 46.7 | 17.44 | 2.74 | 5.5786
2321 | 3 | 46.8 | 17.48 | 2.78 | 5.6601
2322 | 3 | 46.9 | 17.51 | 2.81 | 5.7212
2323 | 3 | 47 | 17.55 | 2.85 | 5.8026
2324 | 3 | 47.1 | 17.58 | 2.88 | 5.8637
2325 | 3 | 47.2 | 17.62 | 2.92 | 5.9451
2326 | 3 | 47.3 | 17.66 | 2.96 | 6.0266
2327 | 3 | 47.4 | 17.69 | 2.99 | 6.0876
2328 | 3 | 47.5 | 17.73 | 3.03 | 6.1691
2329 | 3 | 47.6 | 17.76 | 3.06 | 6.2302
2330 | 3 | 47.7 | 17.8 | 3.1 | 6.3116
2331 | 3 | 47.8 | 17.84 | 3.14 | 6.393
2332 | 3 | 47.9 | 17.87 | 3.17 | 6.4541
2333 | 3 | 48 | 17.91 | 3.21 | 6.5356
2334 | 3 | 48.1 | 17.95 | 3.25 | 6.617
2335 | 3 | 48.2 | 17.98 | 3.28 | 6.6781
2336 | 3 | 48.3 | 18.02 | 3.32 | 6.7595
2337 | 3 | 48.4 | 18.05 | 3.35 | 6.8206
2338 | 3 | 48.5 | 18.09 | 3.39 | 6.902
2339 | 3 | 48.6 | 18.13 | 3.43 | 6.9835
2340 | 3 | 48.7 | 18.16 | 3.46 | 7.0446
2341 | 3 | 48.8 | 18.2 | 3.5 | 7.126
2342 | 3 | 48.9 | 18.24 | 3.54 | 7.2074
2343 | 3 | 49 | 18.28 | 3.58 | 7.2889
2344 | 3 | 49.1 | 18.31 | 3.61 | 7.35
2345 | 3 | 49.2 | 18.35 | 3.65 | 7.4314
2346 | 3 | 49.3 | 18.39 | 3.69 | 7.5128
2347 | 3 | 49.4 | 18.42 | 3.72 | 7.5739
2348 | 3 | 49.5 | 18.46 | 3.76 | 7.6554
2349 | 3 | 49.6 | 18.5 | 3.8 | 7.7368
2350 | 3 | 49.7 | 18.53 | 3.83 | 7.7979
2351 | 3 | 49.8 | 18.57 | 3.87 | 7.8793
2352 | 3 | 49.9 | 18.61 | 3.91 | 7.9608
2353 | 3 | 50 | 18.65 | 3.95 | 8.0422
2354 | 3 | 50.1 | 18.68 | 3.98 | 8.1033
2355 | 3 | 50.2 | 18.72 | 4.02 | 8.1847
2356 | 3 | 50.3 | 18.76 | 4.06 | 8.2662
2357 | 3 | 50.4 | 18.8 | 4.1 | 8.3476
2358 | 3 | 50.5 | 18.84 | 4.14 | 8.429
2359 | 3 | 50.6 | 18.87 | 4.17 | 8.4901
2360 | 3 | 50.7 | 18.91 | 4.21 | 8.5716
2361 | 3 | 50.8 | 18.95 | 4.25 | 8.653
2362 | 3 | 50.9 | 18.99 | 4.29 | 8.7344
2363 | 3 | 51 | 19.02 | 4.32 | 8.7955
2364 | 3 | 51.1 | 19.06 | 4.36 | 8.877
2365 | 3 | 51.2 | 19.1 | 4.4 | 8.9584
2366 | 3 | 51.3 | 19.14 | 4.44 | 9.0398
2367 | 3 | 51.4 | 19.18 | 4.48 | 9.1213
2368 | 3 | 51.5 | 19.22 | 4.52 | 9.2027
2369 | 3 | 51.6 | 19.25 | 4.55 | 9.2638
2370 | 3 | 51.7 | 19.29 | 4.59 | 9.3452
2371 | 3 | 51.8 | 19.33 | 4.63 | 9.4267
2372 | 3 | 51.9 | 19.37 | 4.67 | 9.5081
2373 | 3 | 52 | 19.41 | 4.71 | 9.5896
2374 | 3 | 52.1 | 19.45 | 4.75 | 9.671
2375 | 3 | 52.2 | 19.49 | 4.79 | 9.7524
2376 | 3 | 52.3 | 19.52 | 4.82 | 9.8135
2377 | 3 | 52.4 | 19.56 | 4.86 | 9.895
2378 | 3 | 52.5 | 19.6 | 4.9 | 9.9764
2379 | 3 | 52.6 | 19.64 | 4.94 | 10.0578
2380 | 3 | 52.7 | 19.68 | 4.98 | 10.1393
2381 | 3 | 52.8 | 19.72 | 5.02 | 10.2207
2382 | 3 | 52.9 | 19.76 | 5.06 | 10.3022
2383 | 3 | 53 | 19.8 | 5.1 | 10.3836
2384 | 3 | 53.1 | 19.84 | 5.14 | 10.465
2385 | 3 | 53.2 | 19.88 | 5.18 | 10.5465
2386 | 3 | 53.3 | 19.92 | 5.22 | 10.6279
2387 | 3 | 53.4 | 19.96 | 5.26 | 10.7094
2388 | 3 | 53.5 | 19.99 | 5.29 | 10.7704
2389 | 3 | 53.6 | 20.03 | 5.33 | 10.8519
2390 | 3 | 53.7 | 20.07 | 5.37 | 10.9333
2391 | 3 | 53.8 | 20.11 | 5.41 | 11.0148
2392 | 3 | 53.9 | 20.15 | 5.45 | 11.0962
2393 | 3 | 54 | 20.19 | 5.49 | 11.1776
2394 | 3 | 54.1 | 20.23 | 5.53 | 11.2591
2395 | 3 | 54.2 | 20.27 | 5.57 | 11.3405
2396 | 3 | 54.3 | 20.31 | 5.61 | 11.422
2397 | 3 | 54.4 | 20.35 | 5.65 | 11.5034
2398 | 3 | 54.5 | 20.39 | 5.69 | 11.5848
2399 | 3 | 54.6 | 20.43 | 5.73 | 11.6663
2400 | 3 | 54.7 | 20.47 | 5.77 | 11.7477
2401 | 3 | 54.8 | 20.51 | 5.81 | 11.8292
2402 | 3 | 54.9 | 20.55 | 5.85 | 11.9106
2403 | 3 | 55 | 20.6 | 5.9 | 12.0124
2404 | 3 | 55.1 | 20.64 | 5.94 | 12.0938
2405 | 3 | 55.2 | 20.68 | 5.98 | 12.1753
2406 | 3 | 55.3 | 20.72 | 6.02 | 12.2567
2407 | 3 | 55.4 | 20.76 | 6.06 | 12.3382
2408 | 3 | 55.5 | 20.8 | 6.1 | 12.4196
2409 | 3 | 55.6 | 20.84 | 6.14 | 12.501
2410 | 3 | 55.7 | 20.88 | 6.18 | 12.5825
2411 | 3 | 55.8 | 20.92 | 6.22 | 12.6639
2412 | 3 | 55.9 | 20.96 | 6.26 | 12.7454
2413 | 3 | 56 | 21 | 6.3 | 12.8268
2414 | 3 | 56.1 | 21.04 | 6.34 | 12.9082
2415 | 3 | 56.2 | 21.09 | 6.39 | 13.01
2416 | 3 | 56.3 | 21.13 | 6.43 | 13.0915
2417 | 3 | 56.4 | 21.17 | 6.47 | 13.1729
2418 | 3 | 56.5 | 21.21 | 6.51 | 13.2544
2419 | 3 | 56.6 | 21.25 | 6.55 | 13.3358
2420 | 3 | 56.7 | 21.29 | 6.59 | 13.4172
2421 | 3 | 56.8 | 21.33 | 6.63 | 13.4987
2422 | 3 | 56.9 | 21.38 | 6.68 | 13.6005
2423 | 3 | 57 | 21.42 | 6.72 | 13.6819
2424 | 3 | 57.1 | 21.46 | 6.76 | 13.7634
2425 | 3 | 57.2 | 21.5 | 6.8 | 13.8448
2426 | 3 | 57.3 | 21.54 | 6.84 | 13.9262
2427 | 3 | 57.4 | 21.58 | 6.88 | 14.0077
2428 | 3 | 57.5 | 21.63 | 6.93 | 14.1095
2429 | 3 | 57.6 | 21.67 | 6.97 | 14.1909
2430 | 3 | 57.7 | 21.71 | 7.01 | 14.2724
2431 | 3 | 57.8 | 21.75 | 7.05 | 14.3538
2432 | 3 | 57.9 | 21.79 | 7.09 | 14.4352
2433 | 3 | 58 | 21.84 | 7.14 | 14.537
2434 | 3 | 58.1 | 21.88 | 7.18 | 14.6185
2435 | 3 | 58.2 | 21.92 | 7.22 | 14.6999
2436 | 3 | 58.3 | 21.96 | 7.26 | 14.7814
2437 | 3 | 58.4 | 22.01 | 7.31 | 14.8832
2438 | 3 | 58.5 | 22.05 | 7.35 | 14.9646
2439 | 3 | 58.6 | 22.09 | 7.39 | 15.046
2440 | 3 | 58.7 | 22.14 | 7.44 | 15.1478
2441 | 3 | 58.8 | 22.18 | 7.48 | 15.2293
2442 | 3 | 58.9 | 22.22 | 7.52 | 15.3107
2443 | 3 | 59 | 22.26 | 7.56 | 15.3922
2444 | 3 | 59.1 | 22.31 | 7.61 | 15.494
2445 | 3 | 59.2 | 22.35 | 7.65 | 15.5754
2446 | 3 | 59.3 | 22.39 | 7.69 | 15.6568
2447 | 3 | 59.4 | 22.44 | 7.74 | 15.7586
2448 | 3 | 59.5 | 22.48 | 7.78 | 15.8401
2449 | 3 | 59.6 | 22.52 | 7.82 | 15.9215
2450 | 3 | 59.7 | 22.57 | 7.87 | 16.0233
2451 | 3 | 59.8 | 22.61 | 7.91 | 16.1048
2452 | 3 | 59.9 | 22.65 | 7.95 | 16.1862
2453 | 3 | 60 | 22.7 | 8 | 16.288
2454 | 3 | 60.1 | 22.74 | 8.04 | 16.3694
2455 | 3 | 60.2 | 22.78 | 8.08 | 16.4509
2456 | 3 | 60.3 | 22.83 | 8.13 | 16.5527
2457 | 3 | 60.4 | 22.87 | 8.17 | 16.6341
2458 | 3 | 60.5 | 22.92 | 8.22 | 16.7359
2459 | 3 | 60.6 | 22.96 | 8.26 | 16.8174
2460 | 3 | 60.7 | 23 | 8.3 | 16.8988
2461 | 3 | 60.8 | 23.05 | 8.35 | 17.0006
2462 | 3 | 60.9 | 23.09 | 8.39 | 17.082
2463 | 3 | 61 | 23.14 | 8.44 | 17.1838
2464 | 3 | 61.1 | 23.18 | 8.48 | 17.2653
2465 | 3 | 61.2 | 23.22 | 8.52 | 17.3467
2466 | 3 | 61.3 | 23.27 | 8.57 | 17.4485
2467 | 3 | 61.4 | 23.31 | 8.61 | 17.53
2468 | 3 | 61.5 | 23.36 | 8.66 | 17.6318
2469 | 3 | 61.6 | 23.4 | 8.7 | 17.7132
2470 | 3 | 61.7 | 23.45 | 8.75 | 17.815
2471 | 3 | 61.8 | 23.49 | 8.79 | 17.8964
2472 | 3 | 61.9 | 23.54 | 8.84 | 17.9982
2473 | 3 | 62 | 23.58 | 8.88 | 18.0797
2474 | 3 | 62.1 | 23.63 | 8.93 | 18.1815
2475 | 3 | 62.2 | 23.67 | 8.97 | 18.2629
2476 | 3 | 62.3 | 23.72 | 9.02 | 18.3647
2477 | 3 | 62.4 | 23.76 | 9.06 | 18.4462
2478 | 3 | 62.5 | 23.81 | 9.11 | 18.548
2479 | 3 | 62.6 | 23.85 | 9.15 | 18.6294
2480 | 3 | 62.7 | 23.9 | 9.2 | 18.7312
2481 | 3 | 62.8 | 23.94 | 9.24 | 18.8126
2482 | 3 | 62.9 | 23.99 | 9.29 | 18.9144
2483 | 3 | 63 | 24.03 | 9.33 | 18.9959
2484 | 3 | 63.1 | 24.08 | 9.38 | 19.0977
2485 | 3 | 63.2 | 24.13 | 9.43 | 19.1995
2486 | 3 | 63.3 | 24.17 | 9.47 | 19.2809
2487 | 3 | 63.4 | 24.22 | 9.52 | 19.3827
2488 | 3 | 63.5 | 24.26 | 9.56 | 19.4642
2489 | 3 | 63.6 | 24.31 | 9.61 | 19.566
2490 | 3 | 63.7 | 24.36 | 9.66 | 19.6678
2491 | 3 | 63.8 | 24.4 | 9.7 | 19.7492
2492 | 3 | 63.9 | 24.45 | 9.75 | 19.851
2493 | 3 | 64 | 24.49 | 9.79 | 19.9324
2494 | 3 | 64.1 | 24.54 | 9.84 | 20.0342
2495 | 3 | 64.2 | 24.59 | 9.89 | 20.136
2496 | 3 | 64.3 | 24.63 | 9.93 | 20.2175
2497 | 3 | 64.4 | 24.68 | 9.98 | 20.3193
2498 | 3 | 64.5 | 24.73 | 10.03 | 20.4211
2499 | 3 | 64.6 | 24.77 | 10.07 | 20.5025
2500 | 3 | 64.7 | 24.82 | 10.12 | 20.6043
2501 | 3 | 64.8 | 24.87 | 10.17 | 20.7061
2502 | 3 | 64.9 | 24.91 | 10.21 | 20.7876
2503 | 3 | 65 | 24.96 | 10.26 | 20.8894
2504 | 3 | 65.1 | 25.01 | 10.31 | 20.9912
2505 | 3 | 65.2 | 25.05 | 10.35 | 21.0726
2506 | 3 | 65.3 | 25.1 | 10.4 | 21.1744
2507 | 3 | 65.4 | 25.15 | 10.45 | 21.2762
2508 | 3 | 65.5 | 25.2 | 10.5 | 21.378
2509 | 3 | 65.6 | 25.24 | 10.54 | 21.4594
2510 | 3 | 65.7 | 25.29 | 10.59 | 21.5612
2511 | 3 | 65.8 | 25.34 | 10.64 | 21.663
2512 | 3 | 65.9 | 25.39 | 10.69 | 21.7648
2513 | 3 | 66 | 25.43 | 10.73 | 21.8463
2514 | 3 | 66.1 | 25.48 | 10.78 | 21.9481
2515 | 3 | 66.2 | 25.53 | 10.83 | 22.0499
2516 | 3 | 66.3 | 25.58 | 10.88 | 22.1517
2517 | 3 | 66.4 | 25.62 | 10.92 | 22.2331
2518 | 3 | 66.5 | 25.67 | 10.97 | 22.3349
2519 | 3 | 66.6 | 25.72 | 11.02 | 22.4367
2520 | 3 | 66.7 | 25.77 | 11.07 | 22.5385
2521 | 3 | 66.8 | 25.82 | 11.12 | 22.6403
2522 | 3 | 66.9 | 25.86 | 11.16 | 22.7218
2523 | 3 | 67 | 25.91 | 11.21 | 22.8236
2524 | 3 | 67.1 | 25.96 | 11.26 | 22.9254
2525 | 3 | 67.2 | 26.01 | 11.31 | 23.0272
2526 | 3 | 67.3 | 26.06 | 11.36 | 23.129
2527 | 3 | 67.4 | 26.11 | 11.41 | 23.2308
2528 | 3 | 67.5 | 26.15 | 11.45 | 23.3122
2529 | 3 | 67.6 | 26.2 | 11.5 | 23.414
2530 | 3 | 67.7 | 26.25 | 11.55 | 23.5158
2531 | 3 | 67.8 | 26.3 | 11.6 | 23.6176
2532 | 3 | 67.9 | 26.35 | 11.65 | 23.7194
2533 | 3 | 68 | 26.4 | 11.7 | 23.8212
2534 | 3 | 68.1 | 26.45 | 11.75 | 23.923
2535 | 3 | 68.2 | 26.5 | 11.8 | 24.0248
2536 | 3 | 68.3 | 26.55 | 11.85 | 24.1266
2537 | 3 | 68.4 | 26.6 | 11.9 | 24.2284
2538 | 3 | 68.5 | 26.64 | 11.94 | 24.3098
2539 | 3 | 68.6 | 26.69 | 11.99 | 24.4116
2540 | 3 | 68.7 | 26.74 | 12.04 | 24.5134
2541 | 3 | 68.8 | 26.79 | 12.09 | 24.6152
2542 | 3 | 68.9 | 26.84 | 12.14 | 24.717
2543 | 3 | 69 | 26.89 | 12.19 | 24.8188
2544 | 3 | 69.1 | 26.94 | 12.24 | 24.9206
2545 | 3 | 69.2 | 26.99 | 12.29 | 25.0224
2546 | 3 | 69.3 | 27.04 | 12.34 | 25.1242
2547 | 3 | 69.4 | 27.09 | 12.39 | 25.226
2548 | 3 | 69.5 | 27.14 | 12.44 | 25.3278
2549 | 3 | 69.6 | 27.19 | 12.49 | 25.4296
2550 | 3 | 69.7 | 27.24 | 12.54 | 25.5314
2551 | 3 | 69.8 | 27.29 | 12.59 | 25.6332
2552 | 3 | 69.9 | 27.34 | 12.64 | 25.735
2553 | 3 | 70 | 27.39 | 12.69 | 25.8368
2554 | 3 | 70.1 | 27.44 | 12.74 | 25.9386
2555 | 3 | 70.2 | 27.49 | 12.79 | 26.0404
2556 | 3 | 70.3 | 27.54 | 12.84 | 26.1422
2557 | 3 | 70.4 | 27.59 | 12.89 | 26.244
2558 | 3 | 70.5 | 27.65 | 12.95 | 26.3662
2559 | 3 | 70.6 | 27.7 | 13 | 26.468
2560 | 3 | 70.7 | 27.75 | 13.05 | 26.5698
2561 | 3 | 70.8 | 27.8 | 13.1 | 26.6716
2562 | 3 | 70.9 | 27.85 | 13.15 | 26.7734
2563 | 3 | 71 | 27.9 | 13.2 | 26.8752
2564 | 3 | 71.1 | 27.95 | 13.25 | 26.977
2565 | 3 | 71.2 | 28 | 13.3 | 27.0788
2566 | 3 | 71.3 | 28.05 | 13.35 | 27.1806
2567 | 3 | 71.4 | 28.1 | 13.4 | 27.2824
2568 | 3 | 71.5 | 28.16 | 13.46 | 27.4046
2569 | 3 | 71.6 | 28.21 | 13.51 | 27.5064
2570 | 3 | 71.7 | 28.26 | 13.56 | 27.6082
2571 | 3 | 71.8 | 28.31 | 13.61 | 27.71
2572 | 3 | 71.9 | 28.36 | 13.66 | 27.8118
2573 | 3 | 72 | 28.41 | 13.71 | 27.9136
2574 | 3 | 72.1 | 28.47 | 13.77 | 28.0357
2575 | 3 | 72.2 | 28.52 | 13.82 | 28.1375
2576 | 3 | 72.3 | 28.57 | 13.87 | 28.2393
2577 | 3 | 72.4 | 28.62 | 13.92 | 28.3411
2578 | 3 | 72.5 | 28.67 | 13.97 | 28.4429
2579 | 3 | 72.6 | 28.73 | 14.03 | 28.5651
2580 | 3 | 72.7 | 28.78 | 14.08 | 28.6669
2581 | 3 | 72.8 | 28.83 | 14.13 | 28.7687
2582 | 3 | 72.9 | 28.88 | 14.18 | 28.8705
2583 | 3 | 73 | 28.94 | 14.24 | 28.9926
2584 | 3 | 73.1 | 28.99 | 14.29 | 29.0944
2585 | 3 | 73.2 | 29.04 | 14.34 | 29.1962
2586 | 3 | 73.3 | 29.09 | 14.39 | 29.298
2587 | 3 | 73.4 | 29.15 | 14.45 | 29.4202
2588 | 3 | 73.5 | 29.2 | 14.5 | 29.522
2589 | 3 | 73.6 | 29.25 | 14.55 | 29.6238
2590 | 3 | 73.7 | 29.31 | 14.61 | 29.746
2591 | 3 | 73.8 | 29.36 | 14.66 | 29.8478
2592 | 3 | 73.9 | 29.41 | 14.71 | 29.9496
2593 | 3 | 74 | 29.47 | 14.77 | 30.0717
2594 | 3 | 74.1 | 29.52 | 14.82 | 30.1735
2595 | 3 | 74.2 | 29.57 | 14.87 | 30.2753
2596 | 3 | 74.3 | 29.63 | 14.93 | 30.3975
2597 | 3 | 74.4 | 29.68 | 14.98 | 30.4993
2598 | 3 | 74.5 | 29.73 | 15.03 | 30.6011
2599 | 3 | 74.6 | 29.79 | 15.09 | 30.7232
2600 | 3 | 74.7 | 29.84 | 15.14 | 30.825
2601 | 3 | 74.8 | 29.89 | 15.19 | 30.9268
2602 | 3 | 74.9 | 29.95 | 15.25 | 31.049
2603 | 3 | 75 | 30 | 15.3 | 31.1508
2604 | 3 | 75.1 | 30.06 | 15.36 | 31.273
2605 | 3 | 75.2 | 30.11 | 15.41 | 31.3748
2606 | 3 | 75.3 | 30.16 | 15.46 | 31.4766
2607 | 3 | 75.4 | 30.22 | 15.52 | 31.5987
2608 | 3 | 75.5 | 30.27 | 15.57 | 31.7005
2609 | 3 | 75.6 | 30.33 | 15.63 | 31.8227
2610 | 3 | 75.7 | 30.38 | 15.68 | 31.9245
2611 | 3 | 75.8 | 30.44 | 15.74 | 32.0466
2612 | 3 | 75.9 | 30.49 | 15.79 | 32.1484
2613 | 3 | 76 | 30.55 | 15.85 | 32.2706
2614 | 3 | 76.1 | 30.6 | 15.9 | 32.3724
2615 | 3 | 76.2 | 30.66 | 15.96 | 32.4946
2616 | 3 | 76.3 | 30.71 | 16.01 | 32.5964
2617 | 3 | 76.4 | 30.77 | 16.07 | 32.7185
2618 | 3 | 76.5 | 30.82 | 16.12 | 32.8203
2619 | 3 | 76.6 | 30.88 | 16.18 | 32.9425
2620 | 3 | 76.7 | 30.93 | 16.23 | 33.0443
2621 | 3 | 76.8 | 30.99 | 16.29 | 33.1664
2622 | 3 | 76.9 | 31.04 | 16.34 | 33.2682
2623 | 3 | 77 | 31.1 | 16.4 | 33.3904
2624 | 3 | 77.1 | 31.15 | 16.45 | 33.4922
2625 | 3 | 77.2 | 31.21 | 16.51 | 33.6144
2626 | 3 | 77.3 | 31.26 | 16.56 | 33.7162
2627 | 3 | 77.4 | 31.32 | 16.62 | 33.8383
2628 | 3 | 77.5 | 31.38 | 16.68 | 33.9605
2629 | 3 | 77.6 | 31.43 | 16.73 | 34.0623
2630 | 3 | 77.7 | 31.49 | 16.79 | 34.1844
2631 | 3 | 77.8 | 31.54 | 16.84 | 34.2862
2632 | 3 | 77.9 | 31.6 | 16.9 | 34.4084
2633 | 3 | 78 | 31.66 | 16.96 | 34.5306
2634 | 3 | 78.1 | 31.71 | 17.01 | 34.6324
2635 | 3 | 78.2 | 31.77 | 17.07 | 34.7545
2636 | 3 | 78.3 | 31.83 | 17.13 | 34.8767
2637 | 3 | 78.4 | 31.88 | 17.18 | 34.9785
2638 | 3 | 78.5 | 31.94 | 17.24 | 35.1006
2639 | 3 | 78.6 | 32 | 17.3 | 35.2228
2640 | 3 | 78.7 | 32.05 | 17.35 | 35.3246
2641 | 3 | 78.8 | 32.11 | 17.41 | 35.4468
2642 | 3 | 78.9 | 32.17 | 17.47 | 35.5689
2643 | 3 | 79 | 32.22 | 17.52 | 35.6707
2644 | 3 | 79.1 | 32.28 | 17.58 | 35.7929
2645 | 3 | 79.2 | 32.34 | 17.64 | 35.915
2646 | 3 | 79.3 | 32.4 | 17.7 | 36.0372
2647 | 3 | 79.4 | 32.45 | 17.75 | 36.139
2648 | 3 | 79.5 | 32.51 | 17.81 | 36.2612
2649 | 3 | 79.6 | 32.57 | 17.87 | 36.3833
2650 | 3 | 79.7 | 32.63 | 17.93 | 36.5055
2651 | 3 | 79.8 | 32.68 | 17.98 | 36.6073
2652 | 3 | 79.9 | 32.74 | 18.04 | 36.7294
2653 | 3 | 80 | 32.8 | 18.1 | 36.8516
2654 | 3 | 80.1 | 32.86 | 18.16 | 36.9738
2655 | 3 | 80.2 | 32.91 | 18.21 | 37.0756
2656 | 3 | 80.3 | 32.97 | 18.27 | 37.1977
2657 | 3 | 80.4 | 33.03 | 18.33 | 37.3199
2658 | 3 | 80.5 | 33.09 | 18.39 | 37.442
2659 | 3 | 80.6 | 33.15 | 18.45 | 37.5642
2660 | 3 | 80.7 | 33.21 | 18.51 | 37.6864
2661 | 3 | 80.8 | 33.26 | 18.56 | 37.7882
2662 | 3 | 80.9 | 33.32 | 18.62 | 37.9103
2663 | 3 | 81 | 33.38 | 18.68 | 38.0325
2664 | 3 | 81.1 | 33.44 | 18.74 | 38.1546
2665 | 3 | 81.2 | 33.5 | 18.8 | 38.2768
2666 | 3 | 81.3 | 33.56 | 18.86 | 38.399
2667 | 3 | 81.4 | 33.62 | 18.92 | 38.5211
2668 | 3 | 81.5 | 33.67 | 18.97 | 38.6229
2669 | 3 | 81.6 | 33.73 | 19.03 | 38.7451
2670 | 3 | 81.7 | 33.79 | 19.09 | 38.8672
2671 | 3 | 81.8 | 33.85 | 19.15 | 38.9894
2672 | 3 | 81.9 | 33.91 | 19.21 | 39.1116
2673 | 3 | 82 | 33.97 | 19.27 | 39.2337
2674 | 3 | 82.1 | 34.03 | 19.33 | 39.3559
2675 | 3 | 82.2 | 34.09 | 19.39 | 39.478
2676 | 3 | 82.3 | 34.15 | 19.45 | 39.6002
2677 | 3 | 82.4 | 34.21 | 19.51 | 39.7224
2678 | 3 | 82.5 | 34.27 | 19.57 | 39.8445
2679 | 3 | 82.6 | 34.33 | 19.63 | 39.9667
2680 | 3 | 82.7 | 34.39 | 19.69 | 40.0888
2681 | 3 | 82.8 | 34.45 | 19.75 | 40.211
2682 | 3 | 82.9 | 34.51 | 19.81 | 40.3332
2683 | 3 | 83 | 34.57 | 19.87 | 40.4553
2684 | 3 | 83.1 | 34.63 | 19.93 | 40.5775
2685 | 3 | 83.2 | 34.69 | 19.99 | 40.6996
2686 | 3 | 83.3 | 34.75 | 20.05 | 40.8218
2687 | 3 | 83.4 | 34.81 | 20.11 | 40.944
2688 | 3 | 83.5 | 34.87 | 20.17 | 41.0661
2689 | 3 | 83.6 | 34.93 | 20.23 | 41.1883
2690 | 3 | 83.7 | 34.99 | 20.29 | 41.3104
2691 | 3 | 83.8 | 35.05 | 20.35 | 41.4326
2692 | 3 | 83.9 | 35.11 | 20.41 | 41.5548
2693 | 3 | 84 | 35.17 | 20.47 | 41.6769
2694 | 3 | 84.1 | 35.24 | 20.54 | 41.8194
2695 | 3 | 84.2 | 35.3 | 20.6 | 41.9416
2696 | 3 | 84.3 | 35.36 | 20.66 | 42.0638
2697 | 3 | 84.4 | 35.42 | 20.72 | 42.1859
2698 | 3 | 84.5 | 35.48 | 20.78 | 42.3081
2699 | 3 | 84.6 | 35.54 | 20.84 | 42.4302
2700 | 3 | 84.7 | 35.6 | 20.9 | 42.5524
2701 | 3 | 84.8 | 35.67 | 20.97 | 42.6949
2702 | 3 | 84.9 | 35.73 | 21.03 | 42.8171
2703 | 3 | 85 | 35.79 | 21.09 | 42.9392
2704 | 3 | 85.1 | 35.85 | 21.15 | 43.0614
2705 | 3 | 85.2 | 35.91 | 21.21 | 43.1836
2706 | 3 | 85.3 | 35.97 | 21.27 | 43.3057
2707 | 3 | 85.4 | 36.04 | 21.34 | 43.4482
2708 | 3 | 85.5 | 36.1 | 21.4 | 43.5704
2709 | 3 | 85.6 | 36.16 | 21.46 | 43.6926
2710 | 3 | 85.7 | 36.22 | 21.52 | 43.8147
2711 | 3 | 85.8 | 36.29 | 21.59 | 43.9572
2712 | 3 | 85.9 | 36.35 | 21.65 | 44.0794
2713 | 3 | 86 | 36.41 | 21.71 | 44.2016
2714 | 3 | 86.1 | 36.47 | 21.77 | 44.3237
2715 | 3 | 86.2 | 36.54 | 21.84 | 44.4662
2716 | 3 | 86.3 | 36.6 | 21.9 | 44.5884
2717 | 3 | 86.4 | 36.66 | 21.96 | 44.7106
2718 | 3 | 86.5 | 36.72 | 22.02 | 44.8327
2719 | 3 | 86.6 | 36.79 | 22.09 | 44.9752
2720 | 3 | 86.7 | 36.85 | 22.15 | 45.0974
2721 | 3 | 86.8 | 36.91 | 22.21 | 45.2196
2722 | 3 | 86.9 | 36.98 | 22.28 | 45.3621
2723 | 3 | 87 | 37.04 | 22.34 | 45.4842
2724 | 3 | 87.1 | 37.1 | 22.4 | 45.6064
2725 | 3 | 87.2 | 37.17 | 22.47 | 45.7489
2726 | 3 | 87.3 | 37.23 | 22.53 | 45.8711
2727 | 3 | 87.4 | 37.3 | 22.6 | 46.0136
2728 | 3 | 87.5 | 37.36 | 22.66 | 46.1358
2729 | 3 | 87.6 | 37.42 | 22.72 | 46.2579
2730 | 3 | 87.7 | 37.49 | 22.79 | 46.4004
2731 | 3 | 87.8 | 37.55 | 22.85 | 46.5226
2732 | 3 | 87.9 | 37.62 | 22.92 | 46.6651
2733 | 3 | 88 | 37.68 | 22.98 | 46.7873
2734 | 3 | 88.1 | 37.74 | 23.04 | 46.9094
2735 | 3 | 88.2 | 37.81 | 23.11 | 47.052
2736 | 3 | 88.3 | 37.87 | 23.17 | 47.1741
2737 | 3 | 88.4 | 37.94 | 23.24 | 47.3166
2738 | 3 | 88.5 | 38 | 23.3 | 47.4388
2739 | 3 | 88.6 | 38.07 | 23.37 | 47.5813
2740 | 3 | 88.7 | 38.13 | 23.43 | 47.7035
2741 | 3 | 88.8 | 38.2 | 23.5 | 47.846
2742 | 3 | 88.9 | 38.26 | 23.56 | 47.9682
2743 | 3 | 89 | 38.33 | 23.63 | 48.1107
2744 | 3 | 89.1 | 38.39 | 23.69 | 48.2328
2745 | 3 | 89.2 | 38.46 | 23.76 | 48.3754
2746 | 3 | 89.3 | 38.52 | 23.82 | 48.4975
2747 | 3 | 89.4 | 38.59 | 23.89 | 48.64
2748 | 3 | 89.5 | 38.65 | 23.95 | 48.7622
2749 | 3 | 89.6 | 38.72 | 24.02 | 48.9047
2750 | 3 | 89.7 | 38.78 | 24.08 | 49.0269
2751 | 3 | 89.8 | 38.85 | 24.15 | 49.1694
2752 | 3 | 89.9 | 38.92 | 24.22 | 49.3119
2753 | 3 | 90 | 38.98 | 24.28 | 49.4341
2754 | 3 | 90.1 | 39.05 | 24.35 | 49.5766
2755 | 3 | 90.2 | 39.11 | 24.41 | 49.6988
2756 | 3 | 90.3 | 39.18 | 24.48 | 49.8413
2757 | 3 | 90.4 | 39.25 | 24.55 | 49.9838
2758 | 3 | 90.5 | 39.31 | 24.61 | 50.106
2759 | 3 | 90.6 | 39.38 | 24.68 | 50.2485
2760 | 3 | 90.7 | 39.45 | 24.75 | 50.391
2761 | 3 | 90.8 | 39.51 | 24.81 | 50.5132
2762 | 3 | 90.9 | 39.58 | 24.88 | 50.6557
2763 | 3 | 91 | 39.65 | 24.95 | 50.7982
2764 | 3 | 91.1 | 39.71 | 25.01 | 50.9204
2765 | 3 | 91.2 | 39.78 | 25.08 | 51.0629
2766 | 3 | 91.3 | 39.85 | 25.15 | 51.2054
2767 | 3 | 91.4 | 39.91 | 25.21 | 51.3276
2768 | 3 | 91.5 | 39.98 | 25.28 | 51.4701
2769 | 3 | 91.6 | 40.05 | 25.35 | 51.6126
2770 | 3 | 91.7 | 40.12 | 25.42 | 51.7551
2771 | 3 | 91.8 | 40.18 | 25.48 | 51.8773
2772 | 3 | 91.9 | 40.25 | 25.55 | 52.0198
2773 | 3 | 92 | 40.32 | 25.62 | 52.1623
2774 | 3 | 92.1 | 40.39 | 25.69 | 52.3048
2775 | 3 | 92.2 | 40.45 | 25.75 | 52.427
2776 | 3 | 92.3 | 40.52 | 25.82 | 52.5695
2777 | 3 | 92.4 | 40.59 | 25.89 | 52.712
2778 | 3 | 92.5 | 40.66 | 25.96 | 52.8546
2779 | 3 | 92.6 | 40.73 | 26.03 | 52.9971
2780 | 3 | 92.7 | 40.79 | 26.09 | 53.1192
2781 | 3 | 92.8 | 40.86 | 26.16 | 53.2618
2782 | 3 | 92.9 | 40.93 | 26.23 | 53.4043
2783 | 3 | 93 | 41 | 26.3 | 53.5468
2784 | 3 | 93.1 | 41.07 | 26.37 | 53.6893
2785 | 3 | 93.2 | 41.14 | 26.44 | 53.8318
2786 | 3 | 93.3 | 41.2 | 26.5 | 53.954
2787 | 3 | 93.4 | 41.27 | 26.57 | 54.0965
2788 | 3 | 93.5 | 41.34 | 26.64 | 54.239
2789 | 3 | 93.6 | 41.41 | 26.71 | 54.3816
2790 | 3 | 93.7 | 41.48 | 26.78 | 54.5241
2791 | 3 | 93.8 | 41.55 | 26.85 | 54.6666
2792 | 3 | 93.9 | 41.62 | 26.92 | 54.8091
2793 | 3 | 94 | 41.69 | 26.99 | 54.9516
2794 | 3 | 94.1 | 41.76 | 27.06 | 55.0942
2795 | 3 | 94.2 | 41.83 | 27.13 | 55.2367
2796 | 3 | 94.3 | 41.9 | 27.2 | 55.3792
2797 | 3 | 94.4 | 41.97 | 27.27 | 55.5217
2798 | 3 | 94.5 | 42.04 | 27.34 | 55.6642
2799 | 3 | 94.6 | 42.11 | 27.41 | 55.8068
2800 | 3 | 94.7 | 42.18 | 27.48 | 55.9493
2801 | 3 | 94.8 | 42.25 | 27.55 | 56.0918
2802 | 3 | 94.9 | 42.32 | 27.62 | 56.2343
2803 | 3 | 95 | 42.39 | 27.69 | 56.3768
2804 | 3 | 95.1 | 42.46 | 27.76 | 56.5194
2805 | 3 | 95.2 | 42.53 | 27.83 | 56.6619
2806 | 3 | 95.3 | 42.6 | 27.9 | 56.8044
2807 | 3 | 95.4 | 42.67 | 27.97 | 56.9469
2808 | 3 | 95.5 | 42.74 | 28.04 | 57.0894
2809 | 3 | 95.6 | 42.81 | 28.11 | 57.232
2810 | 3 | 95.7 | 42.88 | 28.18 | 57.3745
2811 | 3 | 95.8 | 42.95 | 28.25 | 57.517
2812 | 3 | 95.9 | 43.02 | 28.32 | 57.6595
2813 | 3 | 96 | 43.09 | 28.39 | 57.802
2814 | 3 | 96.1 | 43.17 | 28.47 | 57.9649
2815 | 3 | 96.2 | 43.24 | 28.54 | 58.1074
2816 | 3 | 96.3 | 43.31 | 28.61 | 58.25
2817 | 3 | 96.4 | 43.38 | 28.68 | 58.3925
2818 | 3 | 96.5 | 43.45 | 28.75 | 58.535
2819 | 3 | 96.6 | 43.52 | 28.82 | 58.6775
2820 | 3 | 96.7 | 43.59 | 28.89 | 58.82
2821 | 3 | 96.8 | 43.67 | 28.97 | 58.9829
2822 | 3 | 96.9 | 43.74 | 29.04 | 59.1254
2823 | 3 | 97 | 43.81 | 29.11 | 59.268
2824 | 3 | 97.1 | 43.88 | 29.18 | 59.4105
2825 | 3 | 97.2 | 43.95 | 29.25 | 59.553
2826 | 3 | 97.3 | 44.03 | 29.33 | 59.7159
2827 | 3 | 97.4 | 44.1 | 29.4 | 59.8584
2828 | 3 | 97.5 | 44.17 | 29.47 | 60.0009
2829 | 3 | 97.6 | 44.24 | 29.54 | 60.1434
2830 | 3 | 97.7 | 44.32 | 29.62 | 60.3063
2831 | 3 | 97.8 | 44.39 | 29.69 | 60.4488
2832 | 3 | 97.9 | 44.46 | 29.76 | 60.5914
2833 | 3 | 98 | 44.53 | 29.83 | 60.7339
2834 | 3 | 98.1 | 44.61 | 29.91 | 60.8968
2835 | 3 | 98.2 | 44.68 | 29.98 | 61.0393
2836 | 3 | 98.3 | 44.75 | 30.05 | 61.1818
2837 | 3 | 98.4 | 44.83 | 30.13 | 61.3447
2838 | 3 | 98.5 | 44.9 | 30.2 | 61.4872
2839 | 3 | 98.6 | 44.97 | 30.27 | 61.6297
2840 | 3 | 98.7 | 45.05 | 30.35 | 61.7926
2841 | 3 | 98.8 | 45.12 | 30.42 | 61.9351
2842 | 3 | 98.9 | 45.2 | 30.5 | 62.098
2843 | 3 | 99 | 45.27 | 30.57 | 62.2405
2844 | 3 | 99.1 | 45.34 | 30.64 | 62.383
2845 | 3 | 99.2 | 45.42 | 30.72 | 62.5459
2846 | 3 | 99.3 | 45.49 | 30.79 | 62.6884
2847 | 3 | 99.4 | 45.57 | 30.87 | 62.8513
2848 | 3 | 99.5 | 45.64 | 30.94 | 62.9938
2849 | 3 | 99.6 | 45.71 | 31.01 | 63.1364
2850 | 3 | 99.7 | 45.79 | 31.09 | 63.2992
2851 | 3 | 99.8 | 45.86 | 31.16 | 63.4418
2852 | 3 | 99.9 | 45.94 | 31.24 | 63.6046
2853 | 3 | 100 | 46.01 | 31.31 | 63.7472
2854 | 3 | 100.1 | 46.09 | 31.39 | 63.91
2855 | 3 | 100.2 | 46.16 | 31.46 | 64.0526
2856 | 3 | 100.3 | 46.24 | 31.54 | 64.2154
2857 | 3 | 100.4 | 46.31 | 31.61 | 64.358
2858 | 3 | 100.5 | 46.39 | 31.69 | 64.5208
2859 | 3 | 100.6 | 46.46 | 31.76 | 64.6634
2860 | 3 | 100.7 | 46.54 | 31.84 | 64.8262
2861 | 3 | 100.8 | 46.61 | 31.91 | 64.9688
2862 | 3 | 100.9 | 46.69 | 31.99 | 65.1316
2863 | 3 | 101 | 46.76 | 32.06 | 65.2742
2864 | 3 | 101.1 | 46.84 | 32.14 | 65.437
2865 | 3 | 101.2 | 46.92 | 32.22 | 65.5999
2866 | 3 | 101.3 | 46.99 | 32.29 | 65.7424
2867 | 3 | 101.4 | 47.07 | 32.37 | 65.9053
2868 | 3 | 101.5 | 47.14 | 32.44 | 66.0478
2869 | 3 | 101.6 | 47.22 | 32.52 | 66.2107
2870 | 3 | 101.7 | 47.3 | 32.6 | 66.3736
2871 | 3 | 101.8 | 47.37 | 32.67 | 66.5161
2872 | 3 | 101.9 | 47.45 | 32.75 | 66.679
2873 | 3 | 102 | 47.53 | 32.83 | 66.8419
2874 | 3 | 102.1 | 47.6 | 32.9 | 66.9844
2875 | 3 | 102.2 | 47.68 | 32.98 | 67.1473
2876 | 3 | 102.3 | 47.76 | 33.06 | 67.3102
2877 | 3 | 102.4 | 47.83 | 33.13 | 67.4527
2878 | 3 | 102.5 | 47.91 | 33.21 | 67.6156
2879 | 3 | 102.6 | 47.99 | 33.29 | 67.7784
2880 | 3 | 102.7 | 48.06 | 33.36 | 67.921
2881 | 3 | 102.8 | 48.14 | 33.44 | 68.0838
2882 | 3 | 102.9 | 48.22 | 33.52 | 68.2467
2883 | 3 | 103 | 48.3 | 33.6 | 68.4096
2884 | 3 | 103.1 | 48.37 | 33.67 | 68.5521
2885 | 3 | 103.2 | 48.45 | 33.75 | 68.715
2886 | 3 | 103.3 | 48.53 | 33.83 | 68.8779
2887 | 3 | 103.4 | 48.61 | 33.91 | 69.0408
2888 | 3 | 103.5 | 48.69 | 33.99 | 69.2036
2889 | 3 | 103.6 | 48.76 | 34.06 | 69.3462
2890 | 3 | 103.7 | 48.84 | 34.14 | 69.509
2891 | 3 | 103.8 | 48.92 | 34.22 | 69.6719
2892 | 3 | 103.9 | 49 | 34.3 | 69.8348
2893 | 3 | 104 | 49.08 | 34.38 | 69.9977
2894 | 3 | 104.1 | 49.16 | 34.46 | 70.1606
2895 | 3 | 104.2 | 49.23 | 34.53 | 70.3031
2896 | 3 | 104.3 | 49.31 | 34.61 | 70.466
2897 | 3 | 104.4 | 49.39 | 34.69 | 70.6288
2898 | 3 | 104.5 | 49.47 | 34.77 | 70.7917
2899 | 3 | 104.6 | 49.55 | 34.85 | 70.9546
2900 | 3 | 104.7 | 49.63 | 34.93 | 71.1175
2901 | 3 | 104.8 | 49.71 | 35.01 | 71.2804
2902 | 3 | 104.9 | 49.79 | 35.09 | 71.4432
2903 | 3 | 105 | 49.87 | 35.17 | 71.6061
2904 | 3 | 105.1 | 49.95 | 35.25 | 71.769
2905 | 3 | 105.2 | 50.03 | 35.33 | 71.9319
2906 | 3 | 105.3 | 50.11 | 35.41 | 72.0948
2907 | 3 | 105.4 | 50.19 | 35.49 | 72.2576
2908 | 3 | 105.5 | 50.27 | 35.57 | 72.4205
2909 | 3 | 105.6 | 50.35 | 35.65 | 72.5834
2910 | 3 | 105.7 | 50.43 | 35.73 | 72.7463
2911 | 3 | 105.8 | 50.51 | 35.81 | 72.9092
2912 | 3 | 105.9 | 50.59 | 35.89 | 73.072
2913 | 3 | 106 | 50.67 | 35.97 | 73.2349
2914 | 3 | 106.1 | 50.75 | 36.05 | 73.3978
2915 | 3 | 106.2 | 50.83 | 36.13 | 73.5607
2916 | 3 | 106.3 | 50.91 | 36.21 | 73.7236
2917 | 3 | 106.4 | 50.99 | 36.29 | 73.8864
2918 | 3 | 106.5 | 51.07 | 36.37 | 74.0493
2919 | 3 | 106.6 | 51.15 | 36.45 | 74.2122
2920 | 3 | 106.7 | 51.23 | 36.53 | 74.3751
2921 | 3 | 106.8 | 51.31 | 36.61 | 74.538
2922 | 3 | 106.9 | 51.39 | 36.69 | 74.7008
2923 | 3 | 107 | 51.48 | 36.78 | 74.8841
2924 | 3 | 107.1 | 51.56 | 36.86 | 75.047
2925 | 3 | 107.2 | 51.64 | 36.94 | 75.2098
2926 | 3 | 107.3 | 51.72 | 37.02 | 75.3727
2927 | 3 | 107.4 | 51.8 | 37.1 | 75.5356
2928 | 3 | 107.5 | 51.88 | 37.18 | 75.6985
2929 | 3 | 107.6 | 51.97 | 37.27 | 75.8817
2930 | 3 | 107.7 | 52.05 | 37.35 | 76.0446
2931 | 3 | 107.8 | 52.13 | 37.43 | 76.2075
2932 | 3 | 107.9 | 52.21 | 37.51 | 76.3704
2933 | 3 | 108 | 52.29 | 37.59 | 76.5332
2934 | 3 | 108.1 | 52.38 | 37.68 | 76.7165
2935 | 3 | 108.2 | 52.46 | 37.76 | 76.8794
2936 | 3 | 108.3 | 52.54 | 37.84 | 77.0422
2937 | 3 | 108.4 | 52.62 | 37.92 | 77.2051
2938 | 3 | 108.5 | 52.71 | 38.01 | 77.3884
2939 | 3 | 108.6 | 52.79 | 38.09 | 77.5512
2940 | 3 | 108.7 | 52.87 | 38.17 | 77.7141
2941 | 3 | 108.8 | 52.96 | 38.26 | 77.8974
2942 | 3 | 108.9 | 53.04 | 38.34 | 78.0602
2943 | 3 | 109 | 53.12 | 38.42 | 78.2231
2944 | 3 | 109.1 | 53.21 | 38.51 | 78.4064
2945 | 3 | 109.2 | 53.29 | 38.59 | 78.5692
2946 | 3 | 109.3 | 53.37 | 38.67 | 78.7321
2947 | 3 | 109.4 | 53.46 | 38.76 | 78.9154
2948 | 3 | 109.5 | 53.54 | 38.84 | 79.0782
2949 | 3 | 109.6 | 53.62 | 38.92 | 79.2411
2950 | 3 | 109.7 | 53.71 | 39.01 | 79.4244
2951 | 3 | 109.8 | 53.79 | 39.09 | 79.5872
2952 | 3 | 109.9 | 53.88 | 39.18 | 79.7705
2953 | 3 | 110 | 53.96 | 39.26 | 79.9334
2954 | 3 | 110.1 | 54.05 | 39.35 | 80.1166
2955 | 3 | 110.2 | 54.13 | 39.43 | 80.2795
2956 | 3 | 110.3 | 54.21 | 39.51 | 80.4424
2957 | 3 | 110.4 | 54.3 | 39.6 | 80.6256
2958 | 3 | 110.5 | 54.38 | 39.68 | 80.7885
2959 | 3 | 110.6 | 54.47 | 39.77 | 80.9717
2960 | 3 | 110.7 | 54.55 | 39.85 | 81.1346
2961 | 3 | 110.8 | 54.64 | 39.94 | 81.3178
2962 | 3 | 110.9 | 54.72 | 40.02 | 81.4807
2963 | 3 | 111 | 54.81 | 40.11 | 81.664
2964 | 3 | 111.1 | 54.89 | 40.19 | 81.8268
2965 | 3 | 111.2 | 54.98 | 40.28 | 82.0101
2966 | 3 | 111.3 | 55.07 | 40.37 | 82.1933
2967 | 3 | 111.4 | 55.15 | 40.45 | 82.3562
2968 | 3 | 111.5 | 55.24 | 40.54 | 82.5394
2969 | 3 | 111.6 | 55.32 | 40.62 | 82.7023
2970 | 3 | 111.7 | 55.41 | 40.71 | 82.8856
2971 | 3 | 111.8 | 55.5 | 40.8 | 83.0688
2972 | 3 | 111.9 | 55.58 | 40.88 | 83.2317
2973 | 3 | 112 | 55.67 | 40.97 | 83.4149
2974 | 3 | 112.1 | 55.75 | 41.05 | 83.5778
2975 | 3 | 112.2 | 55.84 | 41.14 | 83.761
2976 | 3 | 112.3 | 55.93 | 41.23 | 83.9443
2977 | 3 | 112.4 | 56.01 | 41.31 | 84.1072
2978 | 3 | 112.5 | 56.1 | 41.4 | 84.2904
2979 | 3 | 112.6 | 56.19 | 41.49 | 84.4736
2980 | 3 | 112.7 | 56.27 | 41.57 | 84.6365
2981 | 3 | 112.8 | 56.36 | 41.66 | 84.8198
2982 | 3 | 112.9 | 56.45 | 41.75 | 85.003
2983 | 3 | 113 | 56.54 | 41.84 | 85.1862
2984 | 3 | 113.1 | 56.62 | 41.92 | 85.3491
2985 | 3 | 113.2 | 56.71 | 42.01 | 85.5324
2986 | 3 | 113.3 | 56.8 | 42.1 | 85.7156
2987 | 3 | 113.4 | 56.89 | 42.19 | 85.8988
2988 | 3 | 113.5 | 56.97 | 42.27 | 86.0617
2989 | 3 | 113.6 | 57.06 | 42.36 | 86.245
2990 | 3 | 113.7 | 57.15 | 42.45 | 86.4282
2991 | 3 | 113.8 | 57.24 | 42.54 | 86.6114
2992 | 3 | 113.9 | 57.33 | 42.63 | 86.7947
2993 | 3 | 114 | 57.41 | 42.71 | 86.9576
2994 | 3 | 114.1 | 57.5 | 42.8 | 87.1408
2995 | 3 | 114.2 | 57.59 | 42.89 | 87.324
2996 | 3 | 114.3 | 57.68 | 42.98 | 87.5073
2997 | 3 | 114.4 | 57.77 | 43.07 | 87.6905
2998 | 3 | 114.5 | 57.86 | 43.16 | 87.8738
2999 | 3 | 114.6 | 57.95 | 43.25 | 88.057
3000 | 3 | 114.7 | 58.04 | 43.34 | 88.2402
3001 | 3 | 114.8 | 58.12 | 43.42 | 88.4031
3002 | 3 | 114.9 | 58.21 | 43.51 | 88.5864
3003 | 3 | 115 | 58.3 | 43.6 | 88.7696
3004 | 3 | 115.1 | 58.39 | 43.69 | 88.9528
3005 | 3 | 115.2 | 58.48 | 43.78 | 89.1361
3006 | 3 | 115.3 | 58.57 | 43.87 | 89.3193
3007 | 3 | 115.4 | 58.66 | 43.96 | 89.5026
3008 | 3 | 115.5 | 58.75 | 44.05 | 89.6858
3009 | 3 | 115.6 | 58.84 | 44.14 | 89.869
3010 | 3 | 115.7 | 58.93 | 44.23 | 90.0523
3011 | 3 | 115.8 | 59.02 | 44.32 | 90.2355
3012 | 3 | 115.9 | 59.11 | 44.41 | 90.4188
3013 | 3 | 116 | 59.2 | 44.5 | 90.602
3014 | 3 | 116.1 | 59.29 | 44.59 | 90.7852
3015 | 3 | 116.2 | 59.38 | 44.68 | 90.9685
3016 | 3 | 116.3 | 59.47 | 44.77 | 91.1517
3017 | 3 | 116.4 | 59.56 | 44.86 | 91.335
3018 | 3 | 116.5 | 59.66 | 44.96 | 91.5386
3019 | 3 | 116.6 | 59.75 | 45.05 | 91.7218
3020 | 3 | 116.7 | 59.84 | 45.14 | 91.905
3021 | 3 | 116.8 | 59.93 | 45.23 | 92.0883
3022 | 3 | 116.9 | 60.02 | 45.32 | 92.2715
3023 | 3 | 117 | 60.11 | 45.41 | 92.4548
3024 | 3 | 117.1 | 60.2 | 45.5 | 92.638
3025 | 3 | 117.2 | 60.29 | 45.59 | 92.8212
3026 | 3 | 117.3 | 60.39 | 45.69 | 93.0248
3027 | 3 | 117.4 | 60.48 | 45.78 | 93.2081
3028 | 3 | 117.5 | 60.57 | 45.87 | 93.3913
3029 | 3 | 117.6 | 60.66 | 45.96 | 93.5746
3030 | 3 | 117.7 | 60.75 | 46.05 | 93.7578
3031 | 3 | 117.8 | 60.85 | 46.15 | 93.9614
3032 | 3 | 117.9 | 60.94 | 46.24 | 94.1446
3033 | 3 | 118 | 61.03 | 46.33 | 94.3279
3034 | 3 | 118.1 | 61.12 | 46.42 | 94.5111
3035 | 3 | 118.2 | 61.22 | 46.52 | 94.7147
3036 | 3 | 118.3 | 61.31 | 46.61 | 94.898
3037 | 3 | 118.4 | 61.4 | 46.7 | 95.0812
3038 | 3 | 118.5 | 61.49 | 46.79 | 95.2644
3039 | 3 | 118.6 | 61.59 | 46.89 | 95.468
3040 | 3 | 118.7 | 61.68 | 46.98 | 95.6513
3041 | 3 | 118.8 | 61.77 | 47.07 | 95.8345
3042 | 3 | 118.9 | 61.87 | 47.17 | 96.0381
3043 | 3 | 119 | 61.96 | 47.26 | 96.2214
3044 | 3 | 119.1 | 62.05 | 47.35 | 96.4046
3045 | 3 | 119.2 | 62.15 | 47.45 | 96.6082
3046 | 3 | 119.3 | 62.24 | 47.54 | 96.7914
3047 | 3 | 119.4 | 62.34 | 47.64 | 96.995
3048 | 3 | 119.5 | 62.43 | 47.73 | 97.1783
3049 | 3 | 119.6 | 62.52 | 47.82 | 97.3615
3050 | 3 | 119.7 | 62.62 | 47.92 | 97.5651
3051 | 3 | 119.8 | 62.71 | 48.01 | 97.7484
3052 | 3 | 119.9 | 62.81 | 48.11 | 97.952
3053 | 3 | 120 | 62.9 | 48.2 | 98.1352
3054 | 3 | 120.1 | 63 | 48.3 | 98.3388
3055 | 3 | 120.2 | 63.09 | 48.39 | 98.522
3056 | 3 | 120.3 | 63.19 | 48.49 | 98.7256
3057 | 3 | 120.4 | 63.28 | 48.58 | 98.9089
3058 | 3 | 120.5 | 63.38 | 48.68 | 99.1125
3059 | 3 | 120.6 | 63.47 | 48.77 | 99.2957
3060 | 3 | 120.7 | 63.57 | 48.87 | 99.4993
3061 | 3 | 120.8 | 63.66 | 48.96 | 99.6826
3062 | 3 | 120.9 | 63.76 | 49.06 | 99.8862
3063 | 3 | 121 | 63.85 | 49.15 | 100.0694
3064 | 3 | 121.1 | 63.95 | 49.25 | 100.273
3065 | 3 | 121.2 | 64.05 | 49.35 | 100.4766
3066 | 3 | 121.3 | 64.14 | 49.44 | 100.6598
3067 | 3 | 121.4 | 64.24 | 49.54 | 100.8634
3068 | 3 | 121.5 | 64.33 | 49.63 | 101.0467
3069 | 3 | 121.6 | 64.43 | 49.73 | 101.2503
3070 | 3 | 121.7 | 64.53 | 49.83 | 101.4539
3071 | 3 | 121.8 | 64.62 | 49.92 | 101.6371
3072 | 3 | 121.9 | 64.72 | 50.02 | 101.8407
3073 | 3 | 122 | 64.82 | 50.12 | 102.0443
3074 | 3 | 122.1 | 64.91 | 50.21 | 102.2276
3075 | 3 | 122.2 | 65.01 | 50.31 | 102.4312
3076 | 3 | 122.3 | 65.11 | 50.41 | 102.6348
3077 | 3 | 122.4 | 65.2 | 50.5 | 102.818
3078 | 3 | 122.5 | 65.3 | 50.6 | 103.0216
3079 | 3 | 122.6 | 65.4 | 50.7 | 103.2252
3080 | 3 | 122.7 | 65.5 | 50.8 | 103.4288
3081 | 3 | 122.8 | 65.59 | 50.89 | 103.612
3082 | 3 | 122.9 | 65.69 | 50.99 | 103.8156
3083 | 3 | 123 | 65.79 | 51.09 | 104.0192
3084 | 3 | 123.1 | 65.89 | 51.19 | 104.2228
3085 | 3 | 123.2 | 65.99 | 51.29 | 104.4264
3086 | 3 | 123.3 | 66.08 | 51.38 | 104.6097
3087 | 3 | 123.4 | 66.18 | 51.48 | 104.8133
3088 | 3 | 123.5 | 66.28 | 51.58 | 105.0169
3089 | 3 | 123.6 | 66.38 | 51.68 | 105.2205
3090 | 3 | 123.7 | 66.48 | 51.78 | 105.4241
3091 | 3 | 123.8 | 66.58 | 51.88 | 105.6277
3092 | 3 | 123.9 | 66.67 | 51.97 | 105.8109
3093 | 3 | 124 | 66.77 | 52.07 | 106.0145
3094 | 3 | 124.1 | 66.87 | 52.17 | 106.2181
3095 | 3 | 124.2 | 66.97 | 52.27 | 106.4217
3096 | 3 | 124.3 | 67.07 | 52.37 | 106.6253
3097 | 3 | 124.4 | 67.17 | 52.47 | 106.8289
3098 | 3 | 124.5 | 67.27 | 52.57 | 107.0325
3099 | 3 | 124.6 | 67.37 | 52.67 | 107.2361
3100 | 3 | 124.7 | 67.47 | 52.77 | 107.4397
3101 | 3 | 124.8 | 67.57 | 52.87 | 107.6433
3102 | 3 | 124.9 | 67.67 | 52.97 | 107.8469
3103 | 3 | 125 | 67.77 | 53.07 | 108.0505
3104 | 3 | 125.1 | 67.87 | 53.17 | 108.2541
3105 | 3 | 125.2 | 67.97 | 53.27 | 108.4577
3106 | 3 | 125.3 | 68.07 | 53.37 | 108.6613
3107 | 3 | 125.4 | 68.17 | 53.47 | 108.8649
3108 | 3 | 125.5 | 68.27 | 53.57 | 109.0685
3109 | 3 | 125.6 | 68.37 | 53.67 | 109.2721
3110 | 3 | 125.7 | 68.47 | 53.77 | 109.4757
3111 | 3 | 125.8 | 68.57 | 53.87 | 109.6793
3112 | 3 | 125.9 | 68.67 | 53.97 | 109.8829
3113 | 3 | 126 | 68.77 | 54.07 | 110.0865
3114 | 3 | 126.1 | 68.88 | 54.18 | 110.3105
3115 | 3 | 126.2 | 68.98 | 54.28 | 110.5141
3116 | 3 | 126.3 | 69.08 | 54.38 | 110.7177
3117 | 3 | 126.4 | 69.18 | 54.48 | 110.9213
3118 | 3 | 126.5 | 69.28 | 54.58 | 111.1249
3119 | 3 | 126.6 | 69.38 | 54.68 | 111.3285
3120 | 3 | 126.7 | 69.49 | 54.79 | 111.5524
3121 | 3 | 126.8 | 69.59 | 54.89 | 111.756
3122 | 3 | 126.9 | 69.69 | 54.99 | 111.9596
3123 | 3 | 127 | 69.79 | 55.09 | 112.1632
3124 | 3 | 127.1 | 69.89 | 55.19 | 112.3668
3125 | 3 | 127.2 | 70 | 55.3 | 112.5908
3126 | 3 | 127.3 | 70.1 | 55.4 | 112.7944
3127 | 3 | 127.4 | 70.2 | 55.5 | 112.998
3128 | 3 | 127.5 | 70.3 | 55.6 | 113.2016
3129 | 3 | 127.6 | 70.41 | 55.71 | 113.4256
3130 | 3 | 127.7 | 70.51 | 55.81 | 113.6292
3131 | 3 | 127.8 | 70.61 | 55.91 | 113.8328
3132 | 3 | 127.9 | 70.72 | 56.02 | 114.0567
3133 | 3 | 128 | 70.82 | 56.12 | 114.2603
3134 | 3 | 128.1 | 70.92 | 56.22 | 114.4639
3135 | 3 | 128.2 | 71.03 | 56.33 | 114.6879
3136 | 3 | 128.3 | 71.13 | 56.43 | 114.8915
3137 | 3 | 128.4 | 71.23 | 56.53 | 115.0951
3138 | 3 | 128.5 | 71.34 | 56.64 | 115.319
3139 | 3 | 128.6 | 71.44 | 56.74 | 115.5226
3140 | 3 | 128.7 | 71.55 | 56.85 | 115.7466
3141 | 3 | 128.8 | 71.65 | 56.95 | 115.9502
3142 | 3 | 128.9 | 71.76 | 57.06 | 116.1742
3143 | 3 | 129 | 71.86 | 57.16 | 116.3778
3144 | 3 | 129.1 | 71.96 | 57.26 | 116.5814
3145 | 3 | 129.2 | 72.07 | 57.37 | 116.8053
3146 | 3 | 129.3 | 72.17 | 57.47 | 117.0089
3147 | 3 | 129.4 | 72.28 | 57.58 | 117.2329
3148 | 3 | 129.5 | 72.38 | 57.68 | 117.4365
3149 | 3 | 129.6 | 72.49 | 57.79 | 117.6604
3150 | 3 | 129.7 | 72.59 | 57.89 | 117.864
3151 | 3 | 129.8 | 72.7 | 58 | 118.088
3152 | 3 | 129.9 | 72.81 | 58.11 | 118.312
3153 | 3 | 130 | 72.91 | 58.21 | 118.5156
3154 | R-134a | 10 | 26.63 | 11.93 | 24.2895
3155 | R-134a | 10.1 | 26.69 | 11.99 | 24.4116
3156 | R-134a | 10.2 | 26.75 | 12.05 | 24.5338
3157 | R-134a | 10.3 | 26.81 | 12.11 | 24.656
3158 | R-134a | 10.4 | 26.87 | 12.17 | 24.7781
3159 | R-134a | 10.5 | 26.93 | 12.23 | 24.9003
3160 | R-134a | 10.6 | 26.99 | 12.29 | 25.0224
3161 | R-134a | 10.7 | 27.05 | 12.35 | 25.1446
3162 | R-134a | 10.8 | 27.11 | 12.41 | 25.2668
3163 | R-134a | 10.9 | 27.17 | 12.47 | 25.3889
3164 | R-134a | 11 | 27.23 | 12.53 | 25.5111
3165 | R-134a | 11.1 | 27.29 | 12.59 | 25.6332
3166 | R-134a | 11.2 | 27.35 | 12.65 | 25.7554
3167 | R-134a | 11.3 | 27.41 | 12.71 | 25.8776
3168 | R-134a | 11.4 | 27.47 | 12.77 | 25.9997
3169 | R-134a | 11.5 | 27.53 | 12.83 | 26.1219
3170 | R-134a | 11.6 | 27.59 | 12.89 | 26.244
3171 | R-134a | 11.7 | 27.66 | 12.96 | 26.3866
3172 | R-134a | 11.8 | 27.72 | 13.02 | 26.5087
3173 | R-134a | 11.9 | 27.78 | 13.08 | 26.6309
3174 | R-134a | 12 | 27.84 | 13.14 | 26.753
3175 | R-134a | 12.1 | 27.9 | 13.2 | 26.8752
3176 | R-134a | 12.2 | 27.96 | 13.26 | 26.9974
3177 | R-134a | 12.3 | 28.03 | 13.33 | 27.1399
3178 | R-134a | 12.4 | 28.09 | 13.39 | 27.262
3179 | R-134a | 12.5 | 28.15 | 13.45 | 27.3842
3180 | R-134a | 12.6 | 28.21 | 13.51 | 27.5064
3181 | R-134a | 12.7 | 28.27 | 13.57 | 27.6285
3182 | R-134a | 12.8 | 28.34 | 13.64 | 27.771
3183 | R-134a | 12.9 | 28.4 | 13.7 | 27.8932
3184 | R-134a | 13 | 28.46 | 13.76 | 28.0154
3185 | R-134a | 13.1 | 28.53 | 13.83 | 28.1579
3186 | R-134a | 13.2 | 28.59 | 13.89 | 28.28
3187 | R-134a | 13.3 | 28.65 | 13.95 | 28.4022
3188 | R-134a | 13.4 | 28.71 | 14.01 | 28.5244
3189 | R-134a | 13.5 | 28.78 | 14.08 | 28.6669
3190 | R-134a | 13.6 | 28.84 | 14.14 | 28.789
3191 | R-134a | 13.7 | 28.9 | 14.2 | 28.9112
3192 | R-134a | 13.8 | 28.97 | 14.27 | 29.0537
3193 | R-134a | 13.9 | 29.03 | 14.33 | 29.1759
3194 | R-134a | 14 | 29.1 | 14.4 | 29.3184
3195 | R-134a | 14.1 | 29.16 | 14.46 | 29.4406
3196 | R-134a | 14.2 | 29.22 | 14.52 | 29.5627
3197 | R-134a | 14.3 | 29.29 | 14.59 | 29.7052
3198 | R-134a | 14.4 | 29.35 | 14.65 | 29.8274
3199 | R-134a | 14.5 | 29.42 | 14.72 | 29.9699
3200 | R-134a | 14.6 | 29.48 | 14.78 | 30.0921
3201 | R-134a | 14.7 | 29.54 | 14.84 | 30.2142
3202 | R-134a | 14.8 | 29.61 | 14.91 | 30.3568
3203 | R-134a | 14.9 | 29.67 | 14.97 | 30.4789
3204 | R-134a | 15 | 29.74 | 15.04 | 30.6214
3205 | R-134a | 15.1 | 29.8 | 15.1 | 30.7436
3206 | R-134a | 15.2 | 29.87 | 15.17 | 30.8861
3207 | R-134a | 15.3 | 29.93 | 15.23 | 31.0083
3208 | R-134a | 15.4 | 30 | 15.3 | 31.1508
3209 | R-134a | 15.5 | 30.06 | 15.36 | 31.273
3210 | R-134a | 15.6 | 30.13 | 15.43 | 31.4155
3211 | R-134a | 15.7 | 30.2 | 15.5 | 31.558
3212 | R-134a | 15.8 | 30.26 | 15.56 | 31.6802
3213 | R-134a | 15.9 | 30.33 | 15.63 | 31.8227
3214 | R-134a | 16 | 30.39 | 15.69 | 31.9448
3215 | R-134a | 16.1 | 30.46 | 15.76 | 32.0874
3216 | R-134a | 16.2 | 30.53 | 15.83 | 32.2299
3217 | R-134a | 16.3 | 30.59 | 15.89 | 32.352
3218 | R-134a | 16.4 | 30.66 | 15.96 | 32.4946
3219 | R-134a | 16.5 | 30.72 | 16.02 | 32.6167
3220 | R-134a | 16.6 | 30.79 | 16.09 | 32.7592
3221 | R-134a | 16.7 | 30.86 | 16.16 | 32.9018
3222 | R-134a | 16.8 | 30.92 | 16.22 | 33.0239
3223 | R-134a | 16.9 | 30.99 | 16.29 | 33.1664
3224 | R-134a | 17 | 31.06 | 16.36 | 33.309
3225 | R-134a | 17.1 | 31.13 | 16.43 | 33.4515
3226 | R-134a | 17.2 | 31.19 | 16.49 | 33.5736
3227 | R-134a | 17.3 | 31.26 | 16.56 | 33.7162
3228 | R-134a | 17.4 | 31.33 | 16.63 | 33.8587
3229 | R-134a | 17.5 | 31.4 | 16.7 | 34.0012
3230 | R-134a | 17.6 | 31.46 | 16.76 | 34.1234
3231 | R-134a | 17.7 | 31.53 | 16.83 | 34.2659
3232 | R-134a | 17.8 | 31.6 | 16.9 | 34.4084
3233 | R-134a | 17.9 | 31.67 | 16.97 | 34.5509
3234 | R-134a | 18 | 31.74 | 17.04 | 34.6934
3235 | R-134a | 18.1 | 31.8 | 17.1 | 34.8156
3236 | R-134a | 18.2 | 31.87 | 17.17 | 34.9581
3237 | R-134a | 18.3 | 31.94 | 17.24 | 35.1006
3238 | R-134a | 18.4 | 32.01 | 17.31 | 35.2432
3239 | R-134a | 18.5 | 32.08 | 17.38 | 35.3857
3240 | R-134a | 18.6 | 32.15 | 17.45 | 35.5282
3241 | R-134a | 18.7 | 32.22 | 17.52 | 35.6707
3242 | R-134a | 18.8 | 32.29 | 17.59 | 35.8132
3243 | R-134a | 18.9 | 32.35 | 17.65 | 35.9354
3244 | R-134a | 19 | 32.42 | 17.72 | 36.0779
3245 | R-134a | 19.1 | 32.49 | 17.79 | 36.2204
3246 | R-134a | 19.2 | 32.56 | 17.86 | 36.363
3247 | R-134a | 19.3 | 32.63 | 17.93 | 36.5055
3248 | R-134a | 19.4 | 32.7 | 18 | 36.648
3249 | R-134a | 19.5 | 32.77 | 18.07 | 36.7905
3250 | R-134a | 19.6 | 32.84 | 18.14 | 36.933
3251 | R-134a | 19.7 | 32.91 | 18.21 | 37.0756
3252 | R-134a | 19.8 | 32.98 | 18.28 | 37.2181
3253 | R-134a | 19.9 | 33.05 | 18.35 | 37.3606
3254 | R-134a | 20 | 33.12 | 18.42 | 37.5031
3255 | R-134a | 20.1 | 33.19 | 18.49 | 37.6456
3256 | R-134a | 20.2 | 33.27 | 18.57 | 37.8085
3257 | R-134a | 20.3 | 33.34 | 18.64 | 37.951
3258 | R-134a | 20.4 | 33.41 | 18.71 | 38.0936
3259 | R-134a | 20.5 | 33.48 | 18.78 | 38.2361
3260 | R-134a | 20.6 | 33.55 | 18.85 | 38.3786
3261 | R-134a | 20.7 | 33.62 | 18.92 | 38.5211
3262 | R-134a | 20.8 | 33.69 | 18.99 | 38.6636
3263 | R-134a | 20.9 | 33.76 | 19.06 | 38.8062
3264 | R-134a | 21 | 33.84 | 19.14 | 38.969
3265 | R-134a | 21.1 | 33.91 | 19.21 | 39.1116
3266 | R-134a | 21.2 | 33.98 | 19.28 | 39.2541
3267 | R-134a | 21.3 | 34.05 | 19.35 | 39.3966
3268 | R-134a | 21.4 | 34.12 | 19.42 | 39.5391
3269 | R-134a | 21.5 | 34.2 | 19.5 | 39.702
3270 | R-134a | 21.6 | 34.27 | 19.57 | 39.8445
3271 | R-134a | 21.7 | 34.34 | 19.64 | 39.987
3272 | R-134a | 21.8 | 34.41 | 19.71 | 40.1296
3273 | R-134a | 21.9 | 34.49 | 19.79 | 40.2924
3274 | R-134a | 22 | 34.56 | 19.86 | 40.435
3275 | R-134a | 22.1 | 34.63 | 19.93 | 40.5775
3276 | R-134a | 22.2 | 34.7 | 20 | 40.72
3277 | R-134a | 22.3 | 34.78 | 20.08 | 40.8829
3278 | R-134a | 22.4 | 34.85 | 20.15 | 41.0254
3279 | R-134a | 22.5 | 34.92 | 20.22 | 41.1679
3280 | R-134a | 22.6 | 35 | 20.3 | 41.3308
3281 | R-134a | 22.7 | 35.07 | 20.37 | 41.4733
3282 | R-134a | 22.8 | 35.15 | 20.45 | 41.6362
3283 | R-134a | 22.9 | 35.22 | 20.52 | 41.7787
3284 | R-134a | 23 | 35.29 | 20.59 | 41.9212
3285 | R-134a | 23.1 | 35.37 | 20.67 | 42.0841
3286 | R-134a | 23.2 | 35.44 | 20.74 | 42.2266
3287 | R-134a | 23.3 | 35.52 | 20.82 | 42.3895
3288 | R-134a | 23.4 | 35.59 | 20.89 | 42.532
3289 | R-134a | 23.5 | 35.67 | 20.97 | 42.6949
3290 | R-134a | 23.6 | 35.74 | 21.04 | 42.8374
3291 | R-134a | 23.7 | 35.82 | 21.12 | 43.0003
3292 | R-134a | 23.8 | 35.89 | 21.19 | 43.1428
3293 | R-134a | 23.9 | 35.97 | 21.27 | 43.3057
3294 | R-134a | 24 | 36.04 | 21.34 | 43.4482
3295 | R-134a | 24.1 | 36.12 | 21.42 | 43.6111
3296 | R-134a | 24.2 | 36.19 | 21.49 | 43.7536
3297 | R-134a | 24.3 | 36.27 | 21.57 | 43.9165
3298 | R-134a | 24.4 | 36.34 | 21.64 | 44.059
3299 | R-134a | 24.5 | 36.42 | 21.72 | 44.2219
3300 | R-134a | 24.6 | 36.5 | 21.8 | 44.3848
3301 | R-134a | 24.7 | 36.57 | 21.87 | 44.5273
3302 | R-134a | 24.8 | 36.65 | 21.95 | 44.6902
3303 | R-134a | 24.9 | 36.72 | 22.02 | 44.8327
3304 | R-134a | 25 | 36.8 | 22.1 | 44.9956
3305 | R-134a | 25.1 | 36.88 | 22.18 | 45.1585
3306 | R-134a | 25.2 | 36.95 | 22.25 | 45.301
3307 | R-134a | 25.3 | 37.03 | 22.33 | 45.4639
3308 | R-134a | 25.4 | 37.11 | 22.41 | 45.6268
3309 | R-134a | 25.5 | 37.18 | 22.48 | 45.7693
3310 | R-134a | 25.6 | 37.26 | 22.56 | 45.9322
3311 | R-134a | 25.7 | 37.34 | 22.64 | 46.095
3312 | R-134a | 25.8 | 37.42 | 22.72 | 46.2579
3313 | R-134a | 25.9 | 37.49 | 22.79 | 46.4004
3314 | R-134a | 26 | 37.57 | 22.87 | 46.5633
3315 | R-134a | 26.1 | 37.65 | 22.95 | 46.7262
3316 | R-134a | 26.2 | 37.73 | 23.03 | 46.8891
3317 | R-134a | 26.3 | 37.81 | 23.11 | 47.052
3318 | R-134a | 26.4 | 37.88 | 23.18 | 47.1945
3319 | R-134a | 26.5 | 37.96 | 23.26 | 47.3574
3320 | R-134a | 26.6 | 38.04 | 23.34 | 47.5202
3321 | R-134a | 26.7 | 38.12 | 23.42 | 47.6831
3322 | R-134a | 26.8 | 38.2 | 23.5 | 47.846
3323 | R-134a | 26.9 | 38.28 | 23.58 | 48.0089
3324 | R-134a | 27 | 38.36 | 23.66 | 48.1718
3325 | R-134a | 27.1 | 38.44 | 23.74 | 48.3346
3326 | R-134a | 27.2 | 38.51 | 23.81 | 48.4772
3327 | R-134a | 27.3 | 38.59 | 23.89 | 48.64
3328 | R-134a | 27.4 | 38.67 | 23.97 | 48.8029
3329 | R-134a | 27.5 | 38.75 | 24.05 | 48.9658
3330 | R-134a | 27.6 | 38.83 | 24.13 | 49.1287
3331 | R-134a | 27.7 | 38.91 | 24.21 | 49.2916
3332 | R-134a | 27.8 | 38.99 | 24.29 | 49.4544
3333 | R-134a | 27.9 | 39.07 | 24.37 | 49.6173
3334 | R-134a | 28 | 39.15 | 24.45 | 49.7802
3335 | R-134a | 28.1 | 39.23 | 24.53 | 49.9431
3336 | R-134a | 28.2 | 39.31 | 24.61 | 50.106
3337 | R-134a | 28.3 | 39.39 | 24.69 | 50.2688
3338 | R-134a | 28.4 | 39.47 | 24.77 | 50.4317
3339 | R-134a | 28.5 | 39.56 | 24.86 | 50.615
3340 | R-134a | 28.6 | 39.64 | 24.94 | 50.7778
3341 | R-134a | 28.7 | 39.72 | 25.02 | 50.9407
3342 | R-134a | 28.8 | 39.8 | 25.1 | 51.1036
3343 | R-134a | 28.9 | 39.88 | 25.18 | 51.2665
3344 | R-134a | 29 | 39.96 | 25.26 | 51.4294
3345 | R-134a | 29.1 | 40.04 | 25.34 | 51.5922
3346 | R-134a | 29.2 | 40.13 | 25.43 | 51.7755
3347 | R-134a | 29.3 | 40.21 | 25.51 | 51.9384
3348 | R-134a | 29.4 | 40.29 | 25.59 | 52.1012
3349 | R-134a | 29.5 | 40.37 | 25.67 | 52.2641
3350 | R-134a | 29.6 | 40.45 | 25.75 | 52.427
3351 | R-134a | 29.7 | 40.54 | 25.84 | 52.6102
3352 | R-134a | 29.8 | 40.62 | 25.92 | 52.7731
3353 | R-134a | 29.9 | 40.7 | 26 | 52.936
3354 | R-134a | 30 | 40.78 | 26.08 | 53.0989
3355 | R-134a | 30.1 | 40.87 | 26.17 | 53.2821
3356 | R-134a | 30.2 | 40.95 | 26.25 | 53.445
3357 | R-134a | 30.3 | 41.03 | 26.33 | 53.6079
3358 | R-134a | 30.4 | 41.12 | 26.42 | 53.7911
3359 | R-134a | 30.5 | 41.2 | 26.5 | 53.954
3360 | R-134a | 30.6 | 41.28 | 26.58 | 54.1169
3361 | R-134a | 30.7 | 41.37 | 26.67 | 54.3001
3362 | R-134a | 30.8 | 41.45 | 26.75 | 54.463
3363 | R-134a | 30.9 | 41.54 | 26.84 | 54.6462
3364 | R-134a | 31 | 41.62 | 26.92 | 54.8091
3365 | R-134a | 31.1 | 41.7 | 27 | 54.972
3366 | R-134a | 31.2 | 41.79 | 27.09 | 55.1552
3367 | R-134a | 31.3 | 41.87 | 27.17 | 55.3181
3368 | R-134a | 31.4 | 41.96 | 27.26 | 55.5014
3369 | R-134a | 31.5 | 42.04 | 27.34 | 55.6642
3370 | R-134a | 31.6 | 42.13 | 27.43 | 55.8475
3371 | R-134a | 31.7 | 42.21 | 27.51 | 56.0104
3372 | R-134a | 31.8 | 42.3 | 27.6 | 56.1936
3373 | R-134a | 31.9 | 42.38 | 27.68 | 56.3565
3374 | R-134a | 32 | 42.47 | 27.77 | 56.5397
3375 | R-134a | 32.1 | 42.55 | 27.85 | 56.7026
3376 | R-134a | 32.2 | 42.64 | 27.94 | 56.8858
3377 | R-134a | 32.3 | 42.72 | 28.02 | 57.0487
3378 | R-134a | 32.4 | 42.81 | 28.11 | 57.232
3379 | R-134a | 32.5 | 42.9 | 28.2 | 57.4152
3380 | R-134a | 32.6 | 42.98 | 28.28 | 57.5781
3381 | R-134a | 32.7 | 43.07 | 28.37 | 57.7613
3382 | R-134a | 32.8 | 43.16 | 28.46 | 57.9446
3383 | R-134a | 32.9 | 43.24 | 28.54 | 58.1074
3384 | R-134a | 33 | 43.33 | 28.63 | 58.2907
3385 | R-134a | 33.1 | 43.42 | 28.72 | 58.4739
3386 | R-134a | 33.2 | 43.5 | 28.8 | 58.6368
3387 | R-134a | 33.3 | 43.59 | 28.89 | 58.82
3388 | R-134a | 33.4 | 43.68 | 28.98 | 59.0033
3389 | R-134a | 33.5 | 43.76 | 29.06 | 59.1662
3390 | R-134a | 33.6 | 43.85 | 29.15 | 59.3494
3391 | R-134a | 33.7 | 43.94 | 29.24 | 59.5326
3392 | R-134a | 33.8 | 44.03 | 29.33 | 59.7159
3393 | R-134a | 33.9 | 44.12 | 29.42 | 59.8991
3394 | R-134a | 34 | 44.2 | 29.5 | 60.062
3395 | R-134a | 34.1 | 44.29 | 29.59 | 60.2452
3396 | R-134a | 34.2 | 44.38 | 29.68 | 60.4285
3397 | R-134a | 34.3 | 44.47 | 29.77 | 60.6117
3398 | R-134a | 34.4 | 44.56 | 29.86 | 60.795
3399 | R-134a | 34.5 | 44.65 | 29.95 | 60.9782
3400 | R-134a | 34.6 | 44.74 | 30.04 | 61.1614
3401 | R-134a | 34.7 | 44.82 | 30.12 | 61.3243
3402 | R-134a | 34.8 | 44.91 | 30.21 | 61.5076
3403 | R-134a | 34.9 | 45 | 30.3 | 61.6908
3404 | R-134a | 35 | 45.09 | 30.39 | 61.874
3405 | R-134a | 35.1 | 45.18 | 30.48 | 62.0573
3406 | R-134a | 35.2 | 45.27 | 30.57 | 62.2405
3407 | R-134a | 35.3 | 45.36 | 30.66 | 62.4238
3408 | R-134a | 35.4 | 45.45 | 30.75 | 62.607
3409 | R-134a | 35.5 | 45.54 | 30.84 | 62.7902
3410 | R-134a | 35.6 | 45.63 | 30.93 | 62.9735
3411 | R-134a | 35.7 | 45.72 | 31.02 | 63.1567
3412 | R-134a | 35.8 | 45.81 | 31.11 | 63.34
3413 | R-134a | 35.9 | 45.9 | 31.2 | 63.5232
3414 | R-134a | 36 | 45.99 | 31.29 | 63.7064
3415 | R-134a | 36.1 | 46.09 | 31.39 | 63.91
3416 | R-134a | 36.2 | 46.18 | 31.48 | 64.0933
3417 | R-134a | 36.3 | 46.27 | 31.57 | 64.2765
3418 | R-134a | 36.4 | 46.36 | 31.66 | 64.4598
3419 | R-134a | 36.5 | 46.45 | 31.75 | 64.643
3420 | R-134a | 36.6 | 46.54 | 31.84 | 64.8262
3421 | R-134a | 36.7 | 46.63 | 31.93 | 65.0095
3422 | R-134a | 36.8 | 46.73 | 32.03 | 65.2131
3423 | R-134a | 36.9 | 46.82 | 32.12 | 65.3963
3424 | R-134a | 37 | 46.91 | 32.21 | 65.5796
3425 | R-134a | 37.1 | 47 | 32.3 | 65.7628
3426 | R-134a | 37.2 | 47.09 | 32.39 | 65.946
3427 | R-134a | 37.3 | 47.19 | 32.49 | 66.1496
3428 | R-134a | 37.4 | 47.28 | 32.58 | 66.3329
3429 | R-134a | 37.5 | 47.37 | 32.67 | 66.5161
3430 | R-134a | 37.6 | 47.47 | 32.77 | 66.7197
3431 | R-134a | 37.7 | 47.56 | 32.86 | 66.903
3432 | R-134a | 37.8 | 47.65 | 32.95 | 67.0862
3433 | R-134a | 37.9 | 47.75 | 33.05 | 67.2898
3434 | R-134a | 38 | 47.84 | 33.14 | 67.473
3435 | R-134a | 38.1 | 47.93 | 33.23 | 67.6563
3436 | R-134a | 38.2 | 48.03 | 33.33 | 67.8599
3437 | R-134a | 38.3 | 48.12 | 33.42 | 68.0431
3438 | R-134a | 38.4 | 48.22 | 33.52 | 68.2467
3439 | R-134a | 38.5 | 48.31 | 33.61 | 68.43
3440 | R-134a | 38.6 | 48.4 | 33.7 | 68.6132
3441 | R-134a | 38.7 | 48.5 | 33.8 | 68.8168
3442 | R-134a | 38.8 | 48.59 | 33.89 | 69
3443 | R-134a | 38.9 | 48.69 | 33.99 | 69.2036
3444 | R-134a | 39 | 48.78 | 34.08 | 69.3869
3445 | R-134a | 39.1 | 48.88 | 34.18 | 69.5905
3446 | R-134a | 39.2 | 48.97 | 34.27 | 69.7737
3447 | R-134a | 39.3 | 49.07 | 34.37 | 69.9773
3448 | R-134a | 39.4 | 49.16 | 34.46 | 70.1606
3449 | R-134a | 39.5 | 49.26 | 34.56 | 70.3642
3450 | R-134a | 39.6 | 49.36 | 34.66 | 70.5678
3451 | R-134a | 39.7 | 49.45 | 34.75 | 70.751
3452 | R-134a | 39.8 | 49.55 | 34.85 | 70.9546
3453 | R-134a | 39.9 | 49.64 | 34.94 | 71.1378
3454 | R-134a | 40 | 49.74 | 35.04 | 71.3414
3455 | R-134a | 40.1 | 49.84 | 35.14 | 71.545
3456 | R-134a | 40.2 | 49.93 | 35.23 | 71.7283
3457 | R-134a | 40.3 | 50.03 | 35.33 | 71.9319
3458 | R-134a | 40.4 | 50.13 | 35.43 | 72.1355
3459 | R-134a | 40.5 | 50.23 | 35.53 | 72.3391
3460 | R-134a | 40.6 | 50.32 | 35.62 | 72.5223
3461 | R-134a | 40.7 | 50.42 | 35.72 | 72.7259
3462 | R-134a | 40.8 | 50.52 | 35.82 | 72.9295
3463 | R-134a | 40.9 | 50.62 | 35.92 | 73.1331
3464 | R-134a | 41 | 50.71 | 36.01 | 73.3164
3465 | R-134a | 41.1 | 50.81 | 36.11 | 73.52
3466 | R-134a | 41.2 | 50.91 | 36.21 | 73.7236
3467 | R-134a | 41.3 | 51.01 | 36.31 | 73.9272
3468 | R-134a | 41.4 | 51.11 | 36.41 | 74.1308
3469 | R-134a | 41.5 | 51.21 | 36.51 | 74.3344
3470 | R-134a | 41.6 | 51.3 | 36.6 | 74.5176
3471 | R-134a | 41.7 | 51.4 | 36.7 | 74.7212
3472 | R-134a | 41.8 | 51.5 | 36.8 | 74.9248
3473 | R-134a | 41.9 | 51.6 | 36.9 | 75.1284
3474 | R-134a | 42 | 51.7 | 37 | 75.332
3475 | R-134a | 42.1 | 51.8 | 37.1 | 75.5356
3476 | R-134a | 42.2 | 51.9 | 37.2 | 75.7392
3477 | R-134a | 42.3 | 52 | 37.3 | 75.9428
3478 | R-134a | 42.4 | 52.1 | 37.4 | 76.1464
3479 | R-134a | 42.5 | 52.2 | 37.5 | 76.35
3480 | R-134a | 42.6 | 52.3 | 37.6 | 76.5536
3481 | R-134a | 42.7 | 52.4 | 37.7 | 76.7572
3482 | R-134a | 42.8 | 52.5 | 37.8 | 76.9608
3483 | R-134a | 42.9 | 52.6 | 37.9 | 77.1644
3484 | R-134a | 43 | 52.7 | 38 | 77.368
3485 | R-134a | 43.1 | 52.8 | 38.1 | 77.5716
3486 | R-134a | 43.2 | 52.9 | 38.2 | 77.7752
3487 | R-134a | 43.3 | 53.01 | 38.31 | 77.9992
3488 | R-134a | 43.4 | 53.11 | 38.41 | 78.2028
3489 | R-134a | 43.5 | 53.21 | 38.51 | 78.4064
3490 | R-134a | 43.6 | 53.31 | 38.61 | 78.61
3491 | R-134a | 43.7 | 53.41 | 38.71 | 78.8136
3492 | R-134a | 43.8 | 53.51 | 38.81 | 79.0172
3493 | R-134a | 43.9 | 53.62 | 38.92 | 79.2411
3494 | R-134a | 44 | 53.72 | 39.02 | 79.4447
3495 | R-134a | 44.1 | 53.82 | 39.12 | 79.6483
3496 | R-134a | 44.2 | 53.92 | 39.22 | 79.8519
3497 | R-134a | 44.3 | 54.03 | 39.33 | 80.0759
3498 | R-134a | 44.4 | 54.13 | 39.43 | 80.2795
3499 | R-134a | 44.5 | 54.23 | 39.53 | 80.4831
3500 | R-134a | 44.6 | 54.34 | 39.64 | 80.707
3501 | R-134a | 44.7 | 54.44 | 39.74 | 80.9106
3502 | R-134a | 44.8 | 54.54 | 39.84 | 81.1142
3503 | R-134a | 44.9 | 54.65 | 39.95 | 81.3382
3504 | R-134a | 45 | 54.75 | 40.05 | 81.5418
3505 | R-134a | 45.1 | 54.85 | 40.15 | 81.7454
3506 | R-134a | 45.2 | 54.96 | 40.26 | 81.9694
3507 | R-134a | 45.3 | 55.06 | 40.36 | 82.173
3508 | R-134a | 45.4 | 55.17 | 40.47 | 82.3969
3509 | R-134a | 45.5 | 55.27 | 40.57 | 82.6005
3510 | R-134a | 45.6 | 55.38 | 40.68 | 82.8245
3511 | R-134a | 45.7 | 55.48 | 40.78 | 83.0281
3512 | R-134a | 45.8 | 55.59 | 40.89 | 83.252
3513 | R-134a | 45.9 | 55.69 | 40.99 | 83.4556
3514 | R-134a | 46 | 55.8 | 41.1 | 83.6796
3515 | R-134a | 46.1 | 55.9 | 41.2 | 83.8832
3516 | R-134a | 46.2 | 56.01 | 41.31 | 84.1072
3517 | R-134a | 46.3 | 56.11 | 41.41 | 84.3108
3518 | R-134a | 46.4 | 56.22 | 41.52 | 84.5347
3519 | R-134a | 46.5 | 56.32 | 41.62 | 84.7383
3520 | R-134a | 46.6 | 56.43 | 41.73 | 84.9623
3521 | R-134a | 46.7 | 56.54 | 41.84 | 85.1862
3522 | R-134a | 46.8 | 56.64 | 41.94 | 85.3898
3523 | R-134a | 46.9 | 56.75 | 42.05 | 85.6138
3524 | R-134a | 47 | 56.86 | 42.16 | 85.8378
3525 | R-134a | 47.1 | 56.96 | 42.26 | 86.0414
3526 | R-134a | 47.2 | 57.07 | 42.37 | 86.2653
3527 | R-134a | 47.3 | 57.18 | 42.48 | 86.4893
3528 | R-134a | 47.4 | 57.29 | 42.59 | 86.7132
3529 | R-134a | 47.5 | 57.39 | 42.69 | 86.9168
3530 | R-134a | 47.6 | 57.5 | 42.8 | 87.1408
3531 | R-134a | 47.7 | 57.61 | 42.91 | 87.3648
3532 | R-134a | 47.8 | 57.72 | 43.02 | 87.5887
3533 | R-134a | 47.9 | 57.83 | 43.13 | 87.8127
3534 | R-134a | 48 | 57.93 | 43.23 | 88.0163
3535 | R-134a | 48.1 | 58.04 | 43.34 | 88.2402
3536 | R-134a | 48.2 | 58.15 | 43.45 | 88.4642
3537 | R-134a | 48.3 | 58.26 | 43.56 | 88.6882
3538 | R-134a | 48.4 | 58.37 | 43.67 | 88.9121
3539 | R-134a | 48.5 | 58.48 | 43.78 | 89.1361
3540 | R-134a | 48.6 | 58.59 | 43.89 | 89.36
3541 | R-134a | 48.7 | 58.7 | 44 | 89.584
3542 | R-134a | 48.8 | 58.81 | 44.11 | 89.808
3543 | R-134a | 48.9 | 58.92 | 44.22 | 90.0319
3544 | R-134a | 49 | 59.03 | 44.33 | 90.2559
3545 | R-134a | 49.1 | 59.14 | 44.44 | 90.4798
3546 | R-134a | 49.2 | 59.25 | 44.55 | 90.7038
3547 | R-134a | 49.3 | 59.36 | 44.66 | 90.9278
3548 | R-134a | 49.4 | 59.47 | 44.77 | 91.1517
3549 | R-134a | 49.5 | 59.58 | 44.88 | 91.3757
3550 | R-134a | 49.6 | 59.69 | 44.99 | 91.5996
3551 | R-134a | 49.7 | 59.8 | 45.1 | 91.8236
3552 | R-134a | 49.8 | 59.91 | 45.21 | 92.0476
3553 | R-134a | 49.9 | 60.02 | 45.32 | 92.2715
3554 | R-134a | 50 | 60.13 | 45.43 | 92.4955
3555 | R-134a | 50.1 | 60.25 | 45.55 | 92.7398
3556 | R-134a | 50.2 | 60.36 | 45.66 | 92.9638
3557 | R-134a | 50.3 | 60.47 | 45.77 | 93.1877
3558 | R-134a | 50.4 | 60.58 | 45.88 | 93.4117
3559 | R-134a | 50.5 | 60.69 | 45.99 | 93.6356
3560 | R-134a | 50.6 | 60.81 | 46.11 | 93.88
3561 | R-134a | 50.7 | 60.92 | 46.22 | 94.1039
3562 | R-134a | 50.8 | 61.03 | 46.33 | 94.3279
3563 | R-134a | 50.9 | 61.14 | 46.44 | 94.5518
3564 | R-134a | 51 | 61.26 | 46.56 | 94.7962
3565 | R-134a | 51.1 | 61.37 | 46.67 | 95.0201
3566 | R-134a | 51.2 | 61.48 | 46.78 | 95.2441
3567 | R-134a | 51.3 | 61.6 | 46.9 | 95.4884
3568 | R-134a | 51.4 | 61.71 | 47.01 | 95.7124
3569 | R-134a | 51.5 | 61.83 | 47.13 | 95.9567
3570 | R-134a | 51.6 | 61.94 | 47.24 | 96.1806
3571 | R-134a | 51.7 | 62.05 | 47.35 | 96.4046
3572 | R-134a | 51.8 | 62.17 | 47.47 | 96.6489
3573 | R-134a | 51.9 | 62.28 | 47.58 | 96.8729
3574 | R-134a | 52 | 62.4 | 47.7 | 97.1172
3575 | R-134a | 52.1 | 62.51 | 47.81 | 97.3412
3576 | R-134a | 52.2 | 62.63 | 47.93 | 97.5855
3577 | R-134a | 52.3 | 62.74 | 48.04 | 97.8094
3578 | R-134a | 52.4 | 62.86 | 48.16 | 98.0538
3579 | R-134a | 52.5 | 62.97 | 48.27 | 98.2777
3580 | R-134a | 52.6 | 63.09 | 48.39 | 98.522
3581 | R-134a | 52.7 | 63.2 | 48.5 | 98.746
3582 | R-134a | 52.8 | 63.32 | 48.62 | 98.9903
3583 | R-134a | 52.9 | 63.44 | 48.74 | 99.2346
3584 | R-134a | 53 | 63.55 | 48.85 | 99.4586
3585 | R-134a | 53.1 | 63.67 | 48.97 | 99.7029
3586 | R-134a | 53.2 | 63.79 | 49.09 | 99.9472
3587 | R-134a | 53.3 | 63.9 | 49.2 | 100.1712
3588 | R-134a | 53.4 | 64.02 | 49.32 | 100.4155
3589 | R-134a | 53.5 | 64.14 | 49.44 | 100.6598
3590 | R-134a | 53.6 | 64.25 | 49.55 | 100.8838
3591 | R-134a | 53.7 | 64.37 | 49.67 | 101.1281
3592 | R-134a | 53.8 | 64.49 | 49.79 | 101.3724
3593 | R-134a | 53.9 | 64.61 | 49.91 | 101.6168
3594 | R-134a | 54 | 64.72 | 50.02 | 101.8407
3595 | R-134a | 54.1 | 64.84 | 50.14 | 102.085
3596 | R-134a | 54.2 | 64.96 | 50.26 | 102.3294
3597 | R-134a | 54.3 | 65.08 | 50.38 | 102.5737
3598 | R-134a | 54.4 | 65.2 | 50.5 | 102.818
3599 | R-134a | 54.5 | 65.32 | 50.62 | 103.0623
3600 | R-134a | 54.6 | 65.44 | 50.74 | 103.3066
3601 | R-134a | 54.7 | 65.55 | 50.85 | 103.5306
3602 | R-134a | 54.8 | 65.67 | 50.97 | 103.7749
3603 | R-134a | 54.9 | 65.79 | 51.09 | 104.0192
3604 | R-134a | 55 | 65.91 | 51.21 | 104.2636
3605 | R-134a | 55.1 | 66.03 | 51.33 | 104.5079
3606 | R-134a | 55.2 | 66.15 | 51.45 | 104.7522
3607 | R-134a | 55.3 | 66.27 | 51.57 | 104.9965
3608 | R-134a | 55.4 | 66.39 | 51.69 | 105.2408
3609 | R-134a | 55.5 | 66.51 | 51.81 | 105.4852
3610 | R-134a | 55.6 | 66.63 | 51.93 | 105.7295
3611 | R-134a | 55.7 | 66.75 | 52.05 | 105.9738
3612 | R-134a | 55.8 | 66.88 | 52.18 | 106.2385
3613 | R-134a | 55.9 | 67 | 52.3 | 106.4828
3614 | R-134a | 56 | 67.12 | 52.42 | 106.7271
3615 | R-134a | 56.1 | 67.24 | 52.54 | 106.9714
3616 | R-134a | 56.2 | 67.36 | 52.66 | 107.2158
3617 | R-134a | 56.3 | 67.48 | 52.78 | 107.4601
3618 | R-134a | 56.4 | 67.6 | 52.9 | 107.7044
3619 | R-134a | 56.5 | 67.73 | 53.03 | 107.9691
3620 | R-134a | 56.6 | 67.85 | 53.15 | 108.2134
3621 | R-134a | 56.7 | 67.97 | 53.27 | 108.4577
3622 | R-134a | 56.8 | 68.09 | 53.39 | 108.702
3623 | R-134a | 56.9 | 68.22 | 53.52 | 108.9667
3624 | R-134a | 57 | 68.34 | 53.64 | 109.211
3625 | R-134a | 57.1 | 68.46 | 53.76 | 109.4554
3626 | R-134a | 57.2 | 68.59 | 53.89 | 109.72
3627 | R-134a | 57.3 | 68.71 | 54.01 | 109.9644
3628 | R-134a | 57.4 | 68.83 | 54.13 | 110.2087
3629 | R-134a | 57.5 | 68.96 | 54.26 | 110.4734
3630 | R-134a | 57.6 | 69.08 | 54.38 | 110.7177
3631 | R-134a | 57.7 | 69.2 | 54.5 | 110.962
3632 | R-134a | 57.8 | 69.33 | 54.63 | 111.2267
3633 | R-134a | 57.9 | 69.45 | 54.75 | 111.471
3634 | R-134a | 58 | 69.58 | 54.88 | 111.7357
3635 | R-134a | 58.1 | 69.7 | 55 | 111.98
3636 | R-134a | 58.2 | 69.83 | 55.13 | 112.2447
3637 | R-134a | 58.3 | 69.95 | 55.25 | 112.489
3638 | R-134a | 58.4 | 70.08 | 55.38 | 112.7537
3639 | R-134a | 58.5 | 70.2 | 55.5 | 112.998
3640 | R-134a | 58.6 | 70.33 | 55.63 | 113.2627
3641 | R-134a | 58.7 | 70.45 | 55.75 | 113.507
3642 | R-134a | 58.8 | 70.58 | 55.88 | 113.7717
3643 | R-134a | 58.9 | 70.71 | 56.01 | 114.0364
3644 | R-134a | 59 | 70.83 | 56.13 | 114.2807
3645 | R-134a | 59.1 | 70.96 | 56.26 | 114.5454
3646 | R-134a | 59.2 | 71.09 | 56.39 | 114.81
3647 | R-134a | 59.3 | 71.21 | 56.51 | 115.0544
3648 | R-134a | 59.4 | 71.34 | 56.64 | 115.319
3649 | R-134a | 59.5 | 71.47 | 56.77 | 115.5837
3650 | R-134a | 59.6 | 71.59 | 56.89 | 115.828
3651 | R-134a | 59.7 | 71.72 | 57.02 | 116.0927
3652 | R-134a | 59.8 | 71.85 | 57.15 | 116.3574
3653 | R-134a | 59.9 | 71.98 | 57.28 | 116.6221
3654 | R-134a | 60 | 72.11 | 57.41 | 116.8868
3655 | R-134a | 60.1 | 72.23 | 57.53 | 117.1311
3656 | R-134a | 60.2 | 72.36 | 57.66 | 117.3958
3657 | R-134a | 60.3 | 72.49 | 57.79 | 117.6604
3658 | R-134a | 60.4 | 72.62 | 57.92 | 117.9251
3659 | R-134a | 60.5 | 72.75 | 58.05 | 118.1898
3660 | R-134a | 60.6 | 72.88 | 58.18 | 118.4545
3661 | R-134a | 60.7 | 73.01 | 58.31 | 118.7192
3662 | R-134a | 60.8 | 73.14 | 58.44 | 118.9838
3663 | R-134a | 60.9 | 73.26 | 58.56 | 119.2282
3664 | R-134a | 61 | 73.39 | 58.69 | 119.4928
3665 | R-134a | 61.1 | 73.52 | 58.82 | 119.7575
3666 | R-134a | 61.2 | 73.65 | 58.95 | 120.0222
3667 | R-134a | 61.3 | 73.79 | 59.09 | 120.3072
3668 | R-134a | 61.4 | 73.92 | 59.22 | 120.5719
3669 | R-134a | 61.5 | 74.05 | 59.35 | 120.8366
3670 | R-134a | 61.6 | 74.18 | 59.48 | 121.1013
3671 | R-134a | 61.7 | 74.31 | 59.61 | 121.366
3672 | R-134a | 61.8 | 74.44 | 59.74 | 121.6306
3673 | R-134a | 61.9 | 74.57 | 59.87 | 121.8953
3674 | R-134a | 62 | 74.7 | 60 | 122.16
3675 | R-134a | 62.1 | 74.83 | 60.13 | 122.4247
3676 | R-134a | 62.2 | 74.97 | 60.27 | 122.7097
3677 | R-134a | 62.3 | 75.1 | 60.4 | 122.9744
3678 | R-134a | 62.4 | 75.23 | 60.53 | 123.2391
3679 | R-134a | 62.5 | 75.36 | 60.66 | 123.5038
3680 | R-134a | 62.6 | 75.49 | 60.79 | 123.7684
3681 | R-134a | 62.7 | 75.63 | 60.93 | 124.0535
3682 | R-134a | 62.8 | 75.76 | 61.06 | 124.3182
3683 | R-134a | 62.9 | 75.89 | 61.19 | 124.5828
3684 | R-134a | 63 | 76.03 | 61.33 | 124.8679
3685 | R-134a | 63.1 | 76.16 | 61.46 | 125.1326
3686 | R-134a | 63.2 | 76.29 | 61.59 | 125.3972
3687 | R-134a | 63.3 | 76.43 | 61.73 | 125.6823
3688 | R-134a | 63.4 | 76.56 | 61.86 | 125.947
3689 | R-134a | 63.5 | 76.7 | 62 | 126.232
3690 | R-134a | 63.6 | 76.83 | 62.13 | 126.4967
3691 | R-134a | 63.7 | 76.96 | 62.26 | 126.7614
3692 | R-134a | 63.8 | 77.1 | 62.4 | 127.0464
3693 | R-134a | 63.9 | 77.23 | 62.53 | 127.3111
3694 | R-134a | 64 | 77.37 | 62.67 | 127.5961
3695 | R-134a | 64.1 | 77.5 | 62.8 | 127.8608
3696 | R-134a | 64.2 | 77.64 | 62.94 | 128.1458
3697 | R-134a | 64.3 | 77.78 | 63.08 | 128.4309
3698 | R-134a | 64.4 | 77.91 | 63.21 | 128.6956
3699 | R-134a | 64.5 | 78.05 | 63.35 | 128.9806
3700 | R-134a | 64.6 | 78.18 | 63.48 | 129.2453
3701 | R-134a | 64.7 | 78.32 | 63.62 | 129.5303
3702 | R-134a | 64.8 | 78.46 | 63.76 | 129.8154
3703 | R-134a | 64.9 | 78.59 | 63.89 | 130.08
3704 | R-134a | 65 | 78.73 | 64.03 | 130.3651
3705 | R-134a | 65.1 | 78.87 | 64.17 | 130.6501
3706 | R-134a | 65.2 | 79 | 64.3 | 130.9148
3707 | R-134a | 65.3 | 79.14 | 64.44 | 131.1998
3708 | R-134a | 65.4 | 79.28 | 64.58 | 131.4849
3709 | R-134a | 65.5 | 79.42 | 64.72 | 131.7699
3710 | R-134a | 65.6 | 79.55 | 64.85 | 132.0346
3711 | R-134a | 65.7 | 79.69 | 64.99 | 132.3196
3712 | R-134a | 65.8 | 79.83 | 65.13 | 132.6047
3713 | R-134a | 65.9 | 79.97 | 65.27 | 132.8897
3714 | R-134a | 66 | 80.11 | 65.41 | 133.1748
3715 | R-134a | 66.1 | 80.25 | 65.55 | 133.4598
3716 | R-134a | 66.2 | 80.39 | 65.69 | 133.7448
3717 | R-134a | 66.3 | 80.52 | 65.82 | 134.0095
3718 | R-134a | 66.4 | 80.66 | 65.96 | 134.2946
3719 | R-134a | 66.5 | 80.8 | 66.1 | 134.5796
3720 | R-134a | 66.6 | 80.94 | 66.24 | 134.8646
3721 | R-134a | 66.7 | 81.08 | 66.38 | 135.1497
3722 | R-134a | 66.8 | 81.22 | 66.52 | 135.4347
3723 | R-134a | 66.9 | 81.36 | 66.66 | 135.7198
3724 | R-134a | 67 | 81.5 | 66.8 | 136.0048
3725 | R-134a | 67.1 | 81.64 | 66.94 | 136.2898
3726 | R-134a | 67.2 | 81.79 | 67.09 | 136.5952
3727 | R-134a | 67.3 | 81.93 | 67.23 | 136.8803
3728 | R-134a | 67.4 | 82.07 | 67.37 | 137.1653
3729 | R-134a | 67.5 | 82.21 | 67.51 | 137.4504
3730 | R-134a | 67.6 | 82.35 | 67.65 | 137.7354
3731 | R-134a | 67.7 | 82.49 | 67.79 | 138.0204
3732 | R-134a | 67.8 | 82.63 | 67.93 | 138.3055
3733 | R-134a | 67.9 | 82.78 | 68.08 | 138.6109
3734 | R-134a | 68 | 82.92 | 68.22 | 138.8959
3735 | R-134a | 68.1 | 83.06 | 68.36 | 139.181
3736 | R-134a | 68.2 | 83.2 | 68.5 | 139.466
3737 | R-134a | 68.3 | 83.35 | 68.65 | 139.7714
3738 | R-134a | 68.4 | 83.49 | 68.79 | 140.0564
3739 | R-134a | 68.5 | 83.63 | 68.93 | 140.3415
3740 | R-134a | 68.6 | 83.78 | 69.08 | 140.6469
3741 | R-134a | 68.7 | 83.92 | 69.22 | 140.9319
3742 | R-134a | 68.8 | 84.06 | 69.36 | 141.217
3743 | R-134a | 68.9 | 84.21 | 69.51 | 141.5224
3744 | R-134a | 69 | 84.35 | 69.65 | 141.8074
3745 | R-134a | 69.1 | 84.5 | 69.8 | 142.1128
3746 | R-134a | 69.2 | 84.64 | 69.94 | 142.3978
3747 | R-134a | 69.3 | 84.79 | 70.09 | 142.7032
3748 | R-134a | 69.4 | 84.93 | 70.23 | 142.9883
3749 | R-134a | 69.5 | 85.08 | 70.38 | 143.2937
3750 | R-134a | 69.6 | 85.22 | 70.52 | 143.5787
3751 | R-134a | 69.7 | 85.37 | 70.67 | 143.8841
3752 | R-134a | 69.8 | 85.51 | 70.81 | 144.1692
3753 | R-134a | 69.9 | 85.66 | 70.96 | 144.4746
3754 | R-134a | 70 | 85.8 | 71.1 | 144.7596
3755 | R-134a | 70.1 | 85.95 | 71.25 | 145.065
3756 | R-134a | 70.2 | 86.1 | 71.4 | 145.3704
3757 | R-134a | 70.3 | 86.24 | 71.54 | 145.6554
3758 | R-134a | 70.4 | 86.39 | 71.69 | 145.9608
3759 | R-134a | 70.5 | 86.54 | 71.84 | 146.2662
3760 | R-134a | 70.6 | 86.68 | 71.98 | 146.5513
3761 | R-134a | 70.7 | 86.83 | 72.13 | 146.8567
3762 | R-134a | 70.8 | 86.98 | 72.28 | 147.1621
3763 | R-134a | 70.9 | 87.13 | 72.43 | 147.4675
3764 | R-134a | 71 | 87.28 | 72.58 | 147.7729
3765 | R-134a | 71.1 | 87.42 | 72.72 | 148.0579
3766 | R-134a | 71.2 | 87.57 | 72.87 | 148.3633
3767 | R-134a | 71.3 | 87.72 | 73.02 | 148.6687
3768 | R-134a | 71.4 | 87.87 | 73.17 | 148.9741
3769 | R-134a | 71.5 | 88.02 | 73.32 | 149.2795
3770 | R-134a | 71.6 | 88.17 | 73.47 | 149.5849
3771 | R-134a | 71.7 | 88.32 | 73.62 | 149.8903
3772 | R-134a | 71.8 | 88.47 | 73.77 | 150.1957
3773 | R-134a | 71.9 | 88.62 | 73.92 | 150.5011
3774 | R-134a | 72 | 88.77 | 74.07 | 150.8065
3775 | R-134a | 72.1 | 88.92 | 74.22 | 151.1119
3776 | R-134a | 72.2 | 89.07 | 74.37 | 151.4173
3777 | R-134a | 72.3 | 89.22 | 74.52 | 151.7227
3778 | R-134a | 72.4 | 89.37 | 74.67 | 152.0281
3779 | R-134a | 72.5 | 89.52 | 74.82 | 152.3335
3780 | R-134a | 72.6 | 89.67 | 74.97 | 152.6389
3781 | R-134a | 72.7 | 89.82 | 75.12 | 152.9443
3782 | R-134a | 72.8 | 89.97 | 75.27 | 153.2497
3783 | R-134a | 72.9 | 90.12 | 75.42 | 153.5551
3784 | R-134a | 73 | 90.27 | 75.57 | 153.8605
3785 | R-134a | 73.1 | 90.43 | 75.73 | 154.1863
3786 | R-134a | 73.2 | 90.58 | 75.88 | 154.4917
3787 | R-134a | 73.3 | 90.73 | 76.03 | 154.7971
3788 | R-134a | 73.4 | 90.88 | 76.18 | 155.1025
3789 | R-134a | 73.5 | 91.04 | 76.34 | 155.4282
3790 | R-134a | 73.6 | 91.19 | 76.49 | 155.7336
3791 | R-134a | 73.7 | 91.34 | 76.64 | 156.039
3792 | R-134a | 73.8 | 91.5 | 76.8 | 156.3648
3793 | R-134a | 73.9 | 91.65 | 76.95 | 156.6702
3794 | R-134a | 74 | 91.8 | 77.1 | 156.9756
3795 | R-134a | 74.1 | 91.96 | 77.26 | 157.3014
3796 | R-134a | 74.2 | 92.11 | 77.41 | 157.6068
3797 | R-134a | 74.3 | 92.27 | 77.57 | 157.9325
3798 | R-134a | 74.4 | 92.42 | 77.72 | 158.2379
3799 | R-134a | 74.5 | 92.57 | 77.87 | 158.5433
3800 | R-134a | 74.6 | 92.73 | 78.03 | 158.8691
3801 | R-134a | 74.7 | 92.88 | 78.18 | 159.1745
3802 | R-134a | 74.8 | 93.04 | 78.34 | 159.5002
3803 | R-134a | 74.9 | 93.2 | 78.5 | 159.826
3804 | R-134a | 75 | 93.35 | 78.65 | 160.1314
3805 | R-134a | 75.1 | 93.51 | 78.81 | 160.4572
3806 | R-134a | 75.2 | 93.66 | 78.96 | 160.7626
3807 | R-134a | 75.3 | 93.82 | 79.12 | 161.0883
3808 | R-134a | 75.4 | 93.98 | 79.28 | 161.4141
3809 | R-134a | 75.5 | 94.13 | 79.43 | 161.7195
3810 | R-134a | 75.6 | 94.29 | 79.59 | 162.0452
3811 | R-134a | 75.7 | 94.45 | 79.75 | 162.371
3812 | R-134a | 75.8 | 94.6 | 79.9 | 162.6764
3813 | R-134a | 75.9 | 94.76 | 80.06 | 163.0022
3814 | R-134a | 76 | 94.92 | 80.22 | 163.3279
3815 | R-134a | 76.1 | 95.08 | 80.38 | 163.6537
3816 | R-134a | 76.2 | 95.23 | 80.53 | 163.9591
3817 | R-134a | 76.3 | 95.39 | 80.69 | 164.2848
3818 | R-134a | 76.4 | 95.55 | 80.85 | 164.6106
3819 | R-134a | 76.5 | 95.71 | 81.01 | 164.9364
3820 | R-134a | 76.6 | 95.87 | 81.17 | 165.2621
3821 | R-134a | 76.7 | 96.03 | 81.33 | 165.5879
3822 | R-134a | 76.8 | 96.19 | 81.49 | 165.9136
3823 | R-134a | 76.9 | 96.35 | 81.65 | 166.2394
3824 | R-134a | 77 | 96.51 | 81.81 | 166.5652
3825 | R-134a | 77.1 | 96.67 | 81.97 | 166.8909
3826 | R-134a | 77.2 | 96.83 | 82.13 | 167.2167
3827 | R-134a | 77.3 | 96.99 | 82.29 | 167.5424
3828 | R-134a | 77.4 | 97.15 | 82.45 | 167.8682
3829 | R-134a | 77.5 | 97.31 | 82.61 | 168.194
3830 | R-134a | 77.6 | 97.47 | 82.77 | 168.5197
3831 | R-134a | 77.7 | 97.63 | 82.93 | 168.8455
3832 | R-134a | 77.8 | 97.79 | 83.09 | 169.1712
3833 | R-134a | 77.9 | 97.95 | 83.25 | 169.497
3834 | R-134a | 78 | 98.11 | 83.41 | 169.8228
3835 | R-134a | 78.1 | 98.27 | 83.57 | 170.1485
3836 | R-134a | 78.2 | 98.44 | 83.74 | 170.4946
3837 | R-134a | 78.3 | 98.6 | 83.9 | 170.8204
3838 | R-134a | 78.4 | 98.76 | 84.06 | 171.1462
3839 | R-134a | 78.5 | 98.92 | 84.22 | 171.4719
3840 | R-134a | 78.6 | 99.09 | 84.39 | 171.818
3841 | R-134a | 78.7 | 99.25 | 84.55 | 172.1438
3842 | R-134a | 78.8 | 99.41 | 84.71 | 172.4696
3843 | R-134a | 78.9 | 99.58 | 84.88 | 172.8157
3844 | R-134a | 79 | 99.74 | 85.04 | 173.1414
3845 | R-134a | 79.1 | 99.9 | 85.2 | 173.4672
3846 | R-134a | 79.2 | 100.1 | 85.4 | 173.8744
3847 | R-134a | 79.3 | 100.2 | 85.5 | 174.078
3848 | R-134a | 79.4 | 100.4 | 85.7 | 174.4852
3849 | R-134a | 79.5 | 100.6 | 85.9 | 174.8924
3850 | R-134a | 79.6 | 100.7 | 86 | 175.096
3851 | R-134a | 79.7 | 100.9 | 86.2 | 175.5032
3852 | R-134a | 79.8 | 101.1 | 86.4 | 175.9104
3853 | R-134a | 79.9 | 101.2 | 86.5 | 176.114
3854 | R-134a | 80 | 101.4 | 86.7 | 176.5212
3855 | R-134a | 80.1 | 101.6 | 86.9 | 176.9284
3856 | R-134a | 80.2 | 101.7 | 87 | 177.132
3857 | R-134a | 80.3 | 101.9 | 87.2 | 177.5392
3858 | R-134a | 80.4 | 102.1 | 87.4 | 177.9464
3859 | R-134a | 80.5 | 102.2 | 87.5 | 178.15
3860 | R-134a | 80.6 | 102.4 | 87.7 | 178.5572
3861 | R-134a | 80.7 | 102.6 | 87.9 | 178.9644
3862 | R-134a | 80.8 | 102.7 | 88 | 179.168
3863 | R-134a | 80.9 | 102.9 | 88.2 | 179.5752
3864 | R-134a | 81 | 103.1 | 88.4 | 179.9824
3865 | R-134a | 81.1 | 103.2 | 88.5 | 180.186
3866 | R-134a | 81.2 | 103.4 | 88.7 | 180.5932
3867 | R-134a | 81.3 | 103.6 | 88.9 | 181.0004
3868 | R-134a | 81.4 | 103.7 | 89 | 181.204
3869 | R-134a | 81.5 | 103.9 | 89.2 | 181.6112
3870 | R-134a | 81.6 | 104.1 | 89.4 | 182.0184
3871 | R-134a | 81.7 | 104.2 | 89.5 | 182.222
3872 | R-134a | 81.8 | 104.4 | 89.7 | 182.6292
3873 | R-134a | 81.9 | 104.6 | 89.9 | 183.0364
3874 | R-134a | 82 | 104.7 | 90 | 183.24
3875 | R-134a | 82.1 | 104.9 | 90.2 | 183.6472
3876 | R-134a | 82.2 | 105.1 | 90.4 | 184.0544
3877 | R-134a | 82.3 | 105.3 | 90.6 | 184.4616
3878 | R-134a | 82.4 | 105.4 | 90.7 | 184.6652
3879 | R-134a | 82.5 | 105.6 | 90.9 | 185.0724
3880 | R-134a | 82.6 | 105.8 | 91.1 | 185.4796
3881 | R-134a | 82.7 | 105.9 | 91.2 | 185.6832
3882 | R-134a | 82.8 | 106.1 | 91.4 | 186.0904
3883 | R-134a | 82.9 | 106.3 | 91.6 | 186.4976
3884 | R-134a | 83 | 106.5 | 91.8 | 186.9048
3885 | R-134a | 83.1 | 106.6 | 91.9 | 187.1084
3886 | R-134a | 83.2 | 106.8 | 92.1 | 187.5156
3887 | R-134a | 83.3 | 107 | 92.3 | 187.9228
3888 | R-134a | 83.4 | 107.1 | 92.4 | 188.1264
3889 | R-134a | 83.5 | 107.3 | 92.6 | 188.5336
3890 | R-134a | 83.6 | 107.5 | 92.8 | 188.9408
3891 | R-134a | 83.7 | 107.7 | 93 | 189.348
3892 | R-134a | 83.8 | 107.8 | 93.1 | 189.5516
3893 | R-134a | 83.9 | 108 | 93.3 | 189.9588
3894 | R-134a | 84 | 108.2 | 93.5 | 190.366
3895 | R-134a | 84.1 | 108.4 | 93.7 | 190.7732
3896 | R-134a | 84.2 | 108.5 | 93.8 | 190.9768
3897 | R-134a | 84.3 | 108.7 | 94 | 191.384
3898 | R-134a | 84.4 | 108.9 | 94.2 | 191.7912
3899 | R-134a | 84.5 | 109.1 | 94.4 | 192.1984
3900 | R-134a | 84.6 | 109.2 | 94.5 | 192.402
3901 | R-134a | 84.7 | 109.4 | 94.7 | 192.8092
3902 | R-134a | 84.8 | 109.6 | 94.9 | 193.2164
3903 | R-134a | 84.9 | 109.8 | 95.1 | 193.6236
3904 | R-134a | 85 | 109.9 | 95.2 | 193.8272
3905 | R-134a | 85.1 | 110.1 | 95.4 | 194.2344
3906 | R-134a | 85.2 | 110.3 | 95.6 | 194.6416
3907 | R-134a | 85.3 | 110.5 | 95.8 | 195.0488
3908 | R-134a | 85.4 | 110.6 | 95.9 | 195.2524
3909 | R-134a | 85.5 | 110.8 | 96.1 | 195.6596
3910 | R-134a | 85.6 | 111 | 96.3 | 196.0668
3911 | R-134a | 85.7 | 111.2 | 96.5 | 196.474
3912 | R-134a | 85.8 | 111.4 | 96.7 | 196.8812
3913 | R-134a | 85.9 | 111.5 | 96.8 | 197.0848
3914 | R-134a | 86 | 111.7 | 97 | 197.492
3915 | R-134a | 86.1 | 111.9 | 97.2 | 197.8992
3916 | R-134a | 86.2 | 112.1 | 97.4 | 198.3064
3917 | R-134a | 86.3 | 112.2 | 97.5 | 198.51
3918 | R-134a | 86.4 | 112.4 | 97.7 | 198.9172
3919 | R-134a | 86.5 | 112.6 | 97.9 | 199.3244
3920 | R-134a | 86.6 | 112.8 | 98.1 | 199.7316
3921 | R-134a | 86.7 | 113 | 98.3 | 200.1388
3922 | R-134a | 86.8 | 113.1 | 98.4 | 200.3424
3923 | R-134a | 86.9 | 113.3 | 98.6 | 200.7496
3924 | R-134a | 87 | 113.5 | 98.8 | 201.1568
3925 | R-134a | 87.1 | 113.7 | 99 | 201.564
3926 | R-134a | 87.2 | 113.9 | 99.2 | 201.9712
3927 | R-134a | 87.3 | 114 | 99.3 | 202.1748
3928 | R-134a | 87.4 | 114.2 | 99.5 | 202.582
3929 | R-134a | 87.5 | 114.4 | 99.7 | 202.9892
3930 | R-134a | 87.6 | 114.6 | 99.9 | 203.3964
3931 | R-134a | 87.7 | 114.8 | 100.1 | 203.8036
3932 | R-134a | 87.8 | 115 | 100.3 | 204.2108
3933 | R-134a | 87.9 | 115.1 | 100.4 | 204.4144
3934 | R-134a | 88 | 115.3 | 100.6 | 204.8216
3935 | R-134a | 88.1 | 115.5 | 100.8 | 205.2288
3936 | R-134a | 88.2 | 115.7 | 101 | 205.636
3937 | R-134a | 88.3 | 115.9 | 101.2 | 206.0432
3938 | R-134a | 88.4 | 116 | 101.3 | 206.2468
3939 | R-134a | 88.5 | 116.2 | 101.5 | 206.654
3940 | R-134a | 88.6 | 116.4 | 101.7 | 207.0612
3941 | R-134a | 88.7 | 116.6 | 101.9 | 207.4684
3942 | R-134a | 88.8 | 116.8 | 102.1 | 207.8756
3943 | R-134a | 88.9 | 117 | 102.3 | 208.2828
3944 | R-134a | 89 | 117.2 | 102.5 | 208.69
3945 | R-134a | 89.1 | 117.3 | 102.6 | 208.8936
3946 | R-134a | 89.2 | 117.5 | 102.8 | 209.3008
3947 | R-134a | 89.3 | 117.7 | 103 | 209.708
3948 | R-134a | 89.4 | 117.9 | 103.2 | 210.1152
3949 | R-134a | 89.5 | 118.1 | 103.4 | 210.5224
3950 | R-134a | 89.6 | 118.3 | 103.6 | 210.9296
3951 | R-134a | 89.7 | 118.5 | 103.8 | 211.3368
3952 | R-134a | 89.8 | 118.6 | 103.9 | 211.5404
3953 | R-134a | 89.9 | 118.8 | 104.1 | 211.9476
3954 | R-134a | 90 | 119 | 104.3 | 212.3548
3955 | R-134a | 90.1 | 119.2 | 104.5 | 212.762
3956 | R-134a | 90.2 | 119.4 | 104.7 | 213.1692
3957 | R-134a | 90.3 | 119.6 | 104.9 | 213.5764
3958 | R-134a | 90.4 | 119.8 | 105.1 | 213.9836
3959 | R-134a | 90.5 | 120 | 105.3 | 214.3908
3960 | R-134a | 90.6 | 120.1 | 105.4 | 214.5944
3961 | R-134a | 90.7 | 120.3 | 105.6 | 215.0016
3962 | R-134a | 90.8 | 120.5 | 105.8 | 215.4088
3963 | R-134a | 90.9 | 120.7 | 106 | 215.816
3964 | R-134a | 91 | 120.9 | 106.2 | 216.2232
3965 | R-134a | 91.1 | 121.1 | 106.4 | 216.6304
3966 | R-134a | 91.2 | 121.3 | 106.6 | 217.0376
3967 | R-134a | 91.3 | 121.5 | 106.8 | 217.4448
3968 | R-134a | 91.4 | 121.7 | 107 | 217.852
3969 | R-134a | 91.5 | 121.8 | 107.1 | 218.0556
3970 | R-134a | 91.6 | 122 | 107.3 | 218.4628
3971 | R-134a | 91.7 | 122.2 | 107.5 | 218.87
3972 | R-134a | 91.8 | 122.4 | 107.7 | 219.2772
3973 | R-134a | 91.9 | 122.6 | 107.9 | 219.6844
3974 | R-134a | 92 | 122.8 | 108.1 | 220.0916
3975 | R-134a | 92.1 | 123 | 108.3 | 220.4988
3976 | R-134a | 92.2 | 123.2 | 108.5 | 220.906
3977 | R-134a | 92.3 | 123.4 | 108.7 | 221.3132
3978 | R-134a | 92.4 | 123.6 | 108.9 | 221.7204
3979 | R-134a | 92.5 | 123.8 | 109.1 | 222.1276
3980 | R-134a | 92.6 | 124 | 109.3 | 222.5348
3981 | R-134a | 92.7 | 124.1 | 109.4 | 222.7384
3982 | R-134a | 92.8 | 124.3 | 109.6 | 223.1456
3983 | R-134a | 92.9 | 124.5 | 109.8 | 223.5528
3984 | R-134a | 93 | 124.7 | 110 | 223.96
3985 | R-134a | 93.1 | 124.9 | 110.2 | 224.3672
3986 | R-134a | 93.2 | 125.1 | 110.4 | 224.7744
3987 | R-134a | 93.3 | 125.3 | 110.6 | 225.1816
3988 | R-134a | 93.4 | 125.5 | 110.8 | 225.5888
3989 | R-134a | 93.5 | 125.7 | 111 | 225.996
3990 | R-134a | 93.6 | 125.9 | 111.2 | 226.4032
3991 | R-134a | 93.7 | 126.1 | 111.4 | 226.8104
3992 | R-134a | 93.8 | 126.3 | 111.6 | 227.2176
3993 | R-134a | 93.9 | 126.5 | 111.8 | 227.6248
3994 | R-134a | 94 | 126.7 | 112 | 228.032
3995 | R-134a | 94.1 | 126.9 | 112.2 | 228.4392
3996 | R-134a | 94.2 | 127.1 | 112.4 | 228.8464
3997 | R-134a | 94.3 | 127.3 | 112.6 | 229.2536
3998 | R-134a | 94.4 | 127.5 | 112.8 | 229.6608
3999 | R-134a | 94.5 | 127.7 | 113 | 230.068
4000 | R-134a | 94.6 | 127.9 | 113.2 | 230.4752
4001 | R-134a | 94.7 | 128.1 | 113.4 | 230.8824
4002 | R-134a | 94.8 | 128.2 | 113.5 | 231.086
4003 | R-134a | 94.9 | 128.4 | 113.7 | 231.4932
4004 | R-134a | 95 | 128.6 | 113.9 | 231.9004
4005 | R-134a | 95.1 | 128.8 | 114.1 | 232.3076
4006 | R-134a | 95.2 | 129 | 114.3 | 232.7148
4007 | R-134a | 95.3 | 129.2 | 114.5 | 233.122
4008 | R-134a | 95.4 | 129.4 | 114.7 | 233.5292
4009 | R-134a | 95.5 | 129.6 | 114.9 | 233.9364
4010 | R-134a | 95.6 | 129.8 | 115.1 | 234.3436
4011 | R-134a | 95.7 | 130 | 115.3 | 234.7508
4012 | R-134a | 95.8 | 130.2 | 115.5 | 235.158
4013 | R-134a | 95.9 | 130.4 | 115.7 | 235.5652
4014 | R-134a | 96 | 130.6 | 115.9 | 235.9724
4015 | R-134a | 96.1 | 130.8 | 116.1 | 236.3796
4016 | R-134a | 96.2 | 131 | 116.3 | 236.7868
4017 | R-134a | 96.3 | 131.2 | 116.5 | 237.194
4018 | R-134a | 96.4 | 131.4 | 116.7 | 237.6012
4019 | R-134a | 96.5 | 131.6 | 116.9 | 238.0084
4020 | R-134a | 96.6 | 131.8 | 117.1 | 238.4156
4021 | R-134a | 96.7 | 132.1 | 117.4 | 239.0264
4022 | R-134a | 96.8 | 132.3 | 117.6 | 239.4336
4023 | R-134a | 96.9 | 132.5 | 117.8 | 239.8408
4024 | R-134a | 97 | 132.7 | 118 | 240.248
4025 | R-134a | 97.1 | 132.9 | 118.2 | 240.6552
4026 | R-134a | 97.2 | 133.1 | 118.4 | 241.0624
4027 | R-134a | 97.3 | 133.3 | 118.6 | 241.4696
4028 | R-134a | 97.4 | 133.5 | 118.8 | 241.8768
4029 | R-134a | 97.5 | 133.7 | 119 | 242.284
4030 | R-134a | 97.6 | 133.9 | 119.2 | 242.6912
4031 | R-134a | 97.7 | 134.1 | 119.4 | 243.0984
4032 | R-134a | 97.8 | 134.3 | 119.6 | 243.5056
4033 | R-134a | 97.9 | 134.5 | 119.8 | 243.9128
4034 | R-134a | 98 | 134.7 | 120 | 244.32
4035 | R-134a | 98.1 | 134.9 | 120.2 | 244.7272
4036 | R-134a | 98.2 | 135.1 | 120.4 | 245.1344
4037 | R-134a | 98.3 | 135.3 | 120.6 | 245.5416
4038 | R-134a | 98.4 | 135.5 | 120.8 | 245.9488
4039 | R-134a | 98.5 | 135.7 | 121 | 246.356
4040 | R-134a | 98.6 | 135.9 | 121.2 | 246.7632
4041 | R-134a | 98.7 | 136.1 | 121.4 | 247.1704
4042 | R-134a | 98.8 | 136.3 | 121.6 | 247.5776
4043 | R-134a | 98.9 | 136.6 | 121.9 | 248.1884
4044 | R-134a | 99 | 136.8 | 122.1 | 248.5956
4045 | R-134a | 99.1 | 137 | 122.3 | 249.0028
4046 | R-134a | 99.2 | 137.2 | 122.5 | 249.41
4047 | R-134a | 99.3 | 137.4 | 122.7 | 249.8172
4048 | R-134a | 99.4 | 137.6 | 122.9 | 250.2244
4049 | R-134a | 99.5 | 137.8 | 123.1 | 250.6316
4050 | R-134a | 99.6 | 138 | 123.3 | 251.0388
4051 | R-134a | 99.7 | 138.2 | 123.5 | 251.446
4052 | R-134a | 99.8 | 138.4 | 123.7 | 251.8532
4053 | R-134a | 99.9 | 138.6 | 123.9 | 252.2604
4054 | R-134a | 100 | 138.9 | 124.2 | 252.8712
4055 | R-134a | 100.1 | 139.1 | 124.4 | 253.2784
4056 | R-134a | 100.2 | 139.3 | 124.6 | 253.6856
4057 | R-134a | 100.3 | 139.5 | 124.8 | 254.0928
4058 | R-134a | 100.4 | 139.7 | 125 | 254.5
4059 | R-134a | 100.5 | 139.9 | 125.2 | 254.9072
4060 | R-134a | 100.6 | 140.1 | 125.4 | 255.3144
4061 | R-134a | 100.7 | 140.3 | 125.6 | 255.7216
4062 | R-134a | 100.8 | 140.5 | 125.8 | 256.1288
4063 | R-134a | 100.9 | 140.8 | 126.1 | 256.7396
4064 | R-134a | 101 | 141 | 126.3 | 257.1468
4065 | R-134a | 101.1 | 141.2 | 126.5 | 257.554
4066 | R-134a | 101.2 | 141.4 | 126.7 | 257.9612
4067 | R-134a | 101.3 | 141.6 | 126.9 | 258.3684
4068 | R-134a | 101.4 | 141.8 | 127.1 | 258.7756
4069 | R-134a | 101.5 | 142 | 127.3 | 259.1828
4070 | R-134a | 101.6 | 142.2 | 127.5 | 259.59
4071 | R-134a | 101.7 | 142.5 | 127.8 | 260.2008
4072 | R-134a | 101.8 | 142.7 | 128 | 260.608
4073 | R-134a | 101.9 | 142.9 | 128.2 | 261.0152
4074 | R-134a | 102 | 143.1 | 128.4 | 261.4224
4075 | R-134a | 102.1 | 143.3 | 128.6 | 261.8296
4076 | R-134a | 102.2 | 143.5 | 128.8 | 262.2368
4077 | R-134a | 102.3 | 143.7 | 129 | 262.644
4078 | R-134a | 102.4 | 144 | 129.3 | 263.2548
4079 | R-134a | 102.5 | 144.2 | 129.5 | 263.662
4080 | R-134a | 102.6 | 144.4 | 129.7 | 264.0692
4081 | R-134a | 102.7 | 144.6 | 129.9 | 264.4764
4082 | R-134a | 102.8 | 144.8 | 130.1 | 264.8836
4083 | R-134a | 102.9 | 145 | 130.3 | 265.2908
4084 | R-134a | 103 | 145.3 | 130.6 | 265.9016
4085 | R-134a | 103.1 | 145.5 | 130.8 | 266.3088
4086 | R-134a | 103.2 | 145.7 | 131 | 266.716
4087 | R-134a | 103.3 | 145.9 | 131.2 | 267.1232
4088 | R-134a | 103.4 | 146.1 | 131.4 | 267.5304
4089 | R-134a | 103.5 | 146.3 | 131.6 | 267.9376
4090 | R-134a | 103.6 | 146.6 | 131.9 | 268.5484
4091 | R-134a | 103.7 | 146.8 | 132.1 | 268.9556
4092 | R-134a | 103.8 | 147 | 132.3 | 269.3628
4093 | R-134a | 103.9 | 147.2 | 132.5 | 269.77
4094 | R-134a | 104 | 147.4 | 132.7 | 270.1772
4095 | R-134a | 104.1 | 147.7 | 133 | 270.788
4096 | R-134a | 104.2 | 147.9 | 133.2 | 271.1952
4097 | R-134a | 104.3 | 148.1 | 133.4 | 271.6024
4098 | R-134a | 104.4 | 148.3 | 133.6 | 272.0096
4099 | R-134a | 104.5 | 148.5 | 133.8 | 272.4168
4100 | R-134a | 104.6 | 148.8 | 134.1 | 273.0276
4101 | R-134a | 104.7 | 149 | 134.3 | 273.4348
4102 | R-134a | 104.8 | 149.2 | 134.5 | 273.842
4103 | R-134a | 104.9 | 149.4 | 134.7 | 274.2492
4104 | R-134a | 105 | 149.7 | 135 | 274.86
4105 | R-134a | 105.1 | 149.9 | 135.2 | 275.2672
4106 | R-134a | 105.2 | 150.1 | 135.4 | 275.6744
4107 | R-134a | 105.3 | 150.3 | 135.6 | 276.0816
4108 | R-134a | 105.4 | 150.5 | 135.8 | 276.4888
4109 | R-134a | 105.5 | 150.8 | 136.1 | 277.0996
4110 | R-134a | 105.6 | 151 | 136.3 | 277.5068
4111 | R-134a | 105.7 | 151.2 | 136.5 | 277.914
4112 | R-134a | 105.8 | 151.4 | 136.7 | 278.3212
4113 | R-134a | 105.9 | 151.7 | 137 | 278.932
4114 | R-134a | 106 | 151.9 | 137.2 | 279.3392
4115 | R-134a | 106.1 | 152.1 | 137.4 | 279.7464
4116 | R-134a | 106.2 | 152.3 | 137.6 | 280.1536
4117 | R-134a | 106.3 | 152.6 | 137.9 | 280.7644
4118 | R-134a | 106.4 | 152.8 | 138.1 | 281.1716
4119 | R-134a | 106.5 | 153 | 138.3 | 281.5788
4120 | R-134a | 106.6 | 153.2 | 138.5 | 281.986
4121 | R-134a | 106.7 | 153.5 | 138.8 | 282.5968
4122 | R-134a | 106.8 | 153.7 | 139 | 283.004
4123 | R-134a | 106.9 | 153.9 | 139.2 | 283.4112
4124 | R-134a | 107 | 154.1 | 139.4 | 283.8184
4125 | R-134a | 107.1 | 154.4 | 139.7 | 284.4292
4126 | R-134a | 107.2 | 154.6 | 139.9 | 284.8364
4127 | R-134a | 107.3 | 154.8 | 140.1 | 285.2436
4128 | R-134a | 107.4 | 155.1 | 140.4 | 285.8544
4129 | R-134a | 107.5 | 155.3 | 140.6 | 286.2616
4130 | R-134a | 107.6 | 155.5 | 140.8 | 286.6688
4131 | R-134a | 107.7 | 155.7 | 141 | 287.076
4132 | R-134a | 107.8 | 156 | 141.3 | 287.6868
4133 | R-134a | 107.9 | 156.2 | 141.5 | 288.094
4134 | R-134a | 108 | 156.4 | 141.7 | 288.5012
4135 | R-134a | 108.1 | 156.7 | 142 | 289.112
4136 | R-134a | 108.2 | 156.9 | 142.2 | 289.5192
4137 | R-134a | 108.3 | 157.1 | 142.4 | 289.9264
4138 | R-134a | 108.4 | 157.4 | 142.7 | 290.5372
4139 | R-134a | 108.5 | 157.6 | 142.9 | 290.9444
4140 | R-134a | 108.6 | 157.8 | 143.1 | 291.3516
4141 | R-134a | 108.7 | 158 | 143.3 | 291.7588
4142 | R-134a | 108.8 | 158.3 | 143.6 | 292.3696
4143 | R-134a | 108.9 | 158.5 | 143.8 | 292.7768
4144 | R-134a | 109 | 158.7 | 144 | 293.184
4145 | R-134a | 109.1 | 159 | 144.3 | 293.7948
4146 | R-134a | 109.2 | 159.2 | 144.5 | 294.202
4147 | R-134a | 109.3 | 159.4 | 144.7 | 294.6092
4148 | R-134a | 109.4 | 159.7 | 145 | 295.22
4149 | R-134a | 109.5 | 159.9 | 145.2 | 295.6272
4150 | R-134a | 109.6 | 160.1 | 145.4 | 296.0344
4151 | R-134a | 109.7 | 160.4 | 145.7 | 296.6452
4152 | R-134a | 109.8 | 160.6 | 145.9 | 297.0524
4153 | R-134a | 109.9 | 160.8 | 146.1 | 297.4596
4154 | R-134a | 110 | 161.1 | 146.4 | 298.0704
4155 | R-134a | 110.1 | 161.3 | 146.6 | 298.4776
4156 | R-134a | 110.2 | 161.5 | 146.8 | 298.8848
4157 | R-134a | 110.3 | 161.8 | 147.1 | 299.4956
4158 | R-134a | 110.4 | 162 | 147.3 | 299.9028
4159 | R-134a | 110.5 | 162.3 | 147.6 | 300.5136
4160 | R-134a | 110.6 | 162.5 | 147.8 | 300.9208
4161 | R-134a | 110.7 | 162.7 | 148 | 301.328
4162 | R-134a | 110.8 | 163 | 148.3 | 301.9388
4163 | R-134a | 110.9 | 163.2 | 148.5 | 302.346
4164 | R-134a | 111 | 163.4 | 148.7 | 302.7532
4165 | R-134a | 111.1 | 163.7 | 149 | 303.364
4166 | R-134a | 111.2 | 163.9 | 149.2 | 303.7712
4167 | R-134a | 111.3 | 164.1 | 149.4 | 304.1784
4168 | R-134a | 111.4 | 164.4 | 149.7 | 304.7892
4169 | R-134a | 111.5 | 164.6 | 149.9 | 305.1964
4170 | R-134a | 111.6 | 164.9 | 150.2 | 305.8072
4171 | R-134a | 111.7 | 165.1 | 150.4 | 306.2144
4172 | R-134a | 111.8 | 165.3 | 150.6 | 306.6216
4173 | R-134a | 111.9 | 165.6 | 150.9 | 307.2324
4174 | R-134a | 112 | 165.8 | 151.1 | 307.6396
4175 | R-134a | 112.1 | 166.1 | 151.4 | 308.2504
4176 | R-134a | 112.2 | 166.3 | 151.6 | 308.6576
4177 | R-134a | 112.3 | 166.5 | 151.8 | 309.0648
4178 | R-134a | 112.4 | 166.8 | 152.1 | 309.6756
4179 | R-134a | 112.5 | 167 | 152.3 | 310.0828
4180 | R-134a | 112.6 | 167.3 | 152.6 | 310.6936
4181 | R-134a | 112.7 | 167.5 | 152.8 | 311.1008
4182 | R-134a | 112.8 | 167.7 | 153 | 311.508
4183 | R-134a | 112.9 | 168 | 153.3 | 312.1188
4184 | R-134a | 113 | 168.2 | 153.5 | 312.526
4185 | R-134a | 113.1 | 168.5 | 153.8 | 313.1368
4186 | R-134a | 113.2 | 168.7 | 154 | 313.544
4187 | R-134a | 113.3 | 169 | 154.3 | 314.1548
4188 | R-134a | 113.4 | 169.2 | 154.5 | 314.562
4189 | R-134a | 113.5 | 169.4 | 154.7 | 314.9692
4190 | R-134a | 113.6 | 169.7 | 155 | 315.58
4191 | R-134a | 113.7 | 169.9 | 155.2 | 315.9872
4192 | R-134a | 113.8 | 170.2 | 155.5 | 316.598
4193 | R-134a | 113.9 | 170.4 | 155.7 | 317.0052
4194 | R-134a | 114 | 170.7 | 156 | 317.616
4195 | R-134a | 114.1 | 170.9 | 156.2 | 318.0232
4196 | R-134a | 114.2 | 171.2 | 156.5 | 318.634
4197 | R-134a | 114.3 | 171.4 | 156.7 | 319.0412
4198 | R-134a | 114.4 | 171.7 | 157 | 319.652
4199 | R-134a | 114.5 | 171.9 | 157.2 | 320.0592
4200 | R-134a | 114.6 | 172.1 | 157.4 | 320.4664
4201 | R-134a | 114.7 | 172.4 | 157.7 | 321.0772
4202 | R-134a | 114.8 | 172.6 | 157.9 | 321.4844
4203 | R-134a | 114.9 | 172.9 | 158.2 | 322.0952
4204 | R-134a | 115 | 173.1 | 158.4 | 322.5024
4205 | R-134a | 115.1 | 173.4 | 158.7 | 323.1132
4206 | R-134a | 115.2 | 173.6 | 158.9 | 323.5204
4207 | R-134a | 115.3 | 173.9 | 159.2 | 324.1312
4208 | R-134a | 115.4 | 174.1 | 159.4 | 324.5384
4209 | R-134a | 115.5 | 174.4 | 159.7 | 325.1492
4210 | R-134a | 115.6 | 174.6 | 159.9 | 325.5564
4211 | R-134a | 115.7 | 174.9 | 160.2 | 326.1672
4212 | R-134a | 115.8 | 175.1 | 160.4 | 326.5744
4213 | R-134a | 115.9 | 175.4 | 160.7 | 327.1852
4214 | R-134a | 116 | 175.6 | 160.9 | 327.5924
4215 | R-134a | 116.1 | 175.9 | 161.2 | 328.2032
4216 | R-134a | 116.2 | 176.1 | 161.4 | 328.6104
4217 | R-134a | 116.3 | 176.4 | 161.7 | 329.2212
4218 | R-134a | 116.4 | 176.6 | 161.9 | 329.6284
4219 | R-134a | 116.5 | 176.9 | 162.2 | 330.2392
4220 | R-134a | 116.6 | 177.1 | 162.4 | 330.6464
4221 | R-134a | 116.7 | 177.4 | 162.7 | 331.2572
4222 | R-134a | 116.8 | 177.6 | 162.9 | 331.6644
4223 | R-134a | 116.9 | 177.9 | 163.2 | 332.2752
4224 | R-134a | 117 | 178.1 | 163.4 | 332.6824
4225 | R-134a | 117.1 | 178.4 | 163.7 | 333.2932
4226 | R-134a | 117.2 | 178.7 | 164 | 333.904
4227 | R-134a | 117.3 | 178.9 | 164.2 | 334.3112
4228 | R-134a | 117.4 | 179.2 | 164.5 | 334.922
4229 | R-134a | 117.5 | 179.4 | 164.7 | 335.3292
4230 | R-134a | 117.6 | 179.7 | 165 | 335.94
4231 | R-134a | 117.7 | 179.9 | 165.2 | 336.3472
4232 | R-134a | 117.8 | 180.2 | 165.5 | 336.958
4233 | R-134a | 117.9 | 180.4 | 165.7 | 337.3652
4234 | R-134a | 118 | 180.7 | 166 | 337.976
4235 | R-134a | 118.1 | 180.9 | 166.2 | 338.3832
4236 | R-134a | 118.2 | 181.2 | 166.5 | 338.994
4237 | R-134a | 118.3 | 181.5 | 166.8 | 339.6048
4238 | R-134a | 118.4 | 181.7 | 167 | 340.012
4239 | R-134a | 118.5 | 182 | 167.3 | 340.6228
4240 | R-134a | 118.6 | 182.2 | 167.5 | 341.03
4241 | R-134a | 118.7 | 182.5 | 167.8 | 341.6408
4242 | R-134a | 118.8 | 182.7 | 168 | 342.048
4243 | R-134a | 118.9 | 183 | 168.3 | 342.6588
4244 | R-134a | 119 | 183.3 | 168.6 | 343.2696
4245 | R-134a | 119.1 | 183.5 | 168.8 | 343.6768
4246 | R-134a | 119.2 | 183.8 | 169.1 | 344.2876
4247 | R-134a | 119.3 | 184 | 169.3 | 344.6948
4248 | R-134a | 119.4 | 184.3 | 169.6 | 345.3056
4249 | R-134a | 119.5 | 184.6 | 169.9 | 345.9164
4250 | R-134a | 119.6 | 184.8 | 170.1 | 346.3236
4251 | R-134a | 119.7 | 185.1 | 170.4 | 346.9344
4252 | R-134a | 119.8 | 185.3 | 170.6 | 347.3416
4253 | R-134a | 119.9 | 185.6 | 170.9 | 347.9524
4254 | R-134a | 120 | 185.9 | 171.2 | 348.5632
4255 | R-123 | 10 | 2.63 | -12.08 | -24.5847
4256 | R-123 | 10.1 | 2.63 | -12.07 | -24.5684
4257 | R-123 | 10.2 | 2.64 | -12.06 | -24.5542
4258 | R-123 | 10.3 | 2.65 | -12.05 | -24.5399
4259 | R-123 | 10.4 | 2.66 | -12.04 | -24.5236
4260 | R-123 | 10.5 | 2.66 | -12.04 | -24.5094
4261 | R-123 | 10.6 | 2.67 | -12.03 | -24.4931
4262 | R-123 | 10.7 | 2.68 | -12.02 | -24.4768
4263 | R-123 | 10.8 | 2.69 | -12.02 | -24.4625
4264 | R-123 | 10.9 | 2.69 | -12.01 | -24.4462
4265 | R-123 | 11 | 2.7 | -12 | -24.432
4266 | R-123 | 11.1 | 2.71 | -11.99 | -24.4157
4267 | R-123 | 11.2 | 2.72 | -11.98 | -24.3994
4268 | R-123 | 11.3 | 2.72 | -11.98 | -24.3852
4269 | R-123 | 11.4 | 2.73 | -11.97 | -24.3689
4270 | R-123 | 11.5 | 2.74 | -11.96 | -24.3526
4271 | R-123 | 11.6 | 2.75 | -11.95 | -24.3383
4272 | R-123 | 11.7 | 2.75 | -11.95 | -24.3221
4273 | R-123 | 11.8 | 2.76 | -11.94 | -24.3058
4274 | R-123 | 11.9 | 2.77 | -11.93 | -24.2915
4275 | R-123 | 12 | 2.78 | -11.92 | -24.2752
4276 | R-123 | 12.1 | 2.79 | -11.92 | -24.2589
4277 | R-123 | 12.2 | 2.79 | -11.91 | -24.2427
4278 | R-123 | 12.3 | 2.8 | -11.9 | -24.2264
4279 | R-123 | 12.4 | 2.81 | -11.89 | -24.2101
4280 | R-123 | 12.5 | 2.82 | -11.88 | -24.1958
4281 | R-123 | 12.6 | 2.82 | -11.88 | -24.1795
4282 | R-123 | 12.7 | 2.83 | -11.87 | -24.1633
4283 | R-123 | 12.8 | 2.84 | -11.86 | -24.147
4284 | R-123 | 12.9 | 2.85 | -11.85 | -24.1307
4285 | R-123 | 13 | 2.86 | -11.84 | -24.1144
4286 | R-123 | 13.1 | 2.86 | -11.84 | -24.0981
4287 | R-123 | 13.2 | 2.87 | -11.83 | -24.0818
4288 | R-123 | 13.3 | 2.88 | -11.82 | -24.0655
4289 | R-123 | 13.4 | 2.89 | -11.81 | -24.0492
4290 | R-123 | 13.5 | 2.9 | -11.8 | -24.0329
4291 | R-123 | 13.6 | 2.9 | -11.8 | -24.0167
4292 | R-123 | 13.7 | 2.91 | -11.79 | -24.0004
4293 | R-123 | 13.8 | 2.92 | -11.78 | -23.9841
4294 | R-123 | 13.9 | 2.93 | -11.77 | -23.9678
4295 | R-123 | 14 | 2.94 | -11.76 | -23.9495
4296 | R-123 | 14.1 | 2.94 | -11.76 | -23.9332
4297 | R-123 | 14.2 | 2.95 | -11.75 | -23.9169
4298 | R-123 | 14.3 | 2.96 | -11.74 | -23.9006
4299 | R-123 | 14.4 | 2.97 | -11.73 | -23.8843
4300 | R-123 | 14.5 | 2.98 | -11.72 | -23.866
4301 | R-123 | 14.6 | 2.99 | -11.71 | -23.8497
4302 | R-123 | 14.7 | 2.99 | -11.71 | -23.8334
4303 | R-123 | 14.8 | 3 | -11.7 | -23.8171
4304 | R-123 | 14.9 | 3.01 | -11.69 | -23.7988
4305 | R-123 | 15 | 3.02 | -11.68 | -23.7825
4306 | R-123 | 15.1 | 3.03 | -11.67 | -23.7662
4307 | R-123 | 15.2 | 3.04 | -11.66 | -23.7479
4308 | R-123 | 15.3 | 3.04 | -11.66 | -23.7316
4309 | R-123 | 15.4 | 3.05 | -11.65 | -23.7153
4310 | R-123 | 15.5 | 3.06 | -11.64 | -23.697
4311 | R-123 | 15.6 | 3.07 | -11.63 | -23.6807
4312 | R-123 | 15.7 | 3.08 | -11.62 | -23.6624
4313 | R-123 | 15.8 | 3.09 | -11.61 | -23.6461
4314 | R-123 | 15.9 | 3.1 | -11.61 | -23.6278
4315 | R-123 | 16 | 3.1 | -11.6 | -23.6115
4316 | R-123 | 16.1 | 3.11 | -11.59 | -23.5932
4317 | R-123 | 16.2 | 3.12 | -11.58 | -23.5769
4318 | R-123 | 16.3 | 3.13 | -11.57 | -23.5586
4319 | R-123 | 16.4 | 3.14 | -11.56 | -23.5402
4320 | R-123 | 16.5 | 3.15 | -11.55 | -23.5239
4321 | R-123 | 16.6 | 3.16 | -11.54 | -23.5056
4322 | R-123 | 16.7 | 3.16 | -11.54 | -23.4893
4323 | R-123 | 16.8 | 3.17 | -11.53 | -23.471
4324 | R-123 | 16.9 | 3.18 | -11.52 | -23.4527
4325 | R-123 | 17 | 3.19 | -11.51 | -23.4344
4326 | R-123 | 17.1 | 3.2 | -11.5 | -23.4181
4327 | R-123 | 17.2 | 3.21 | -11.49 | -23.3998
4328 | R-123 | 17.3 | 3.22 | -11.48 | -23.3814
4329 | R-123 | 17.4 | 3.23 | -11.47 | -23.3631
4330 | R-123 | 17.5 | 3.23 | -11.47 | -23.3468
4331 | R-123 | 17.6 | 3.24 | -11.46 | -23.3285
4332 | R-123 | 17.7 | 3.25 | -11.45 | -23.3102
4333 | R-123 | 17.8 | 3.26 | -11.44 | -23.2918
4334 | R-123 | 17.9 | 3.27 | -11.43 | -23.2735
4335 | R-123 | 18 | 3.28 | -11.42 | -23.2552
4336 | R-123 | 18.1 | 3.29 | -11.41 | -23.2369
4337 | R-123 | 18.2 | 3.3 | -11.4 | -23.2185
4338 | R-123 | 18.3 | 3.3 | -11.4 | -23.2023
4339 | R-123 | 18.4 | 3.31 | -11.39 | -23.1839
4340 | R-123 | 18.5 | 3.32 | -11.38 | -23.1656
4341 | R-123 | 18.6 | 3.33 | -11.37 | -23.1453
4342 | R-123 | 18.7 | 3.34 | -11.36 | -23.1269
4343 | R-123 | 18.8 | 3.35 | -11.35 | -23.1086
4344 | R-123 | 18.9 | 3.36 | -11.34 | -23.0903
4345 | R-123 | 19 | 3.37 | -11.33 | -23.072
4346 | R-123 | 19.1 | 3.38 | -11.32 | -23.0536
4347 | R-123 | 19.2 | 3.39 | -11.31 | -23.0353
4348 | R-123 | 19.3 | 3.4 | -11.3 | -23.017
4349 | R-123 | 19.4 | 3.4 | -11.3 | -22.9987
4350 | R-123 | 19.5 | 3.41 | -11.29 | -22.9783
4351 | R-123 | 19.6 | 3.42 | -11.28 | -22.96
4352 | R-123 | 19.7 | 3.43 | -11.27 | -22.9416
4353 | R-123 | 19.8 | 3.44 | -11.26 | -22.9233
4354 | R-123 | 19.9 | 3.45 | -11.25 | -22.903
4355 | R-123 | 20 | 3.46 | -11.24 | -22.8846
4356 | R-123 | 20.1 | 3.47 | -11.23 | -22.8663
4357 | R-123 | 20.2 | 3.48 | -11.22 | -22.846
4358 | R-123 | 20.3 | 3.49 | -11.21 | -22.8276
4359 | R-123 | 20.4 | 3.5 | -11.2 | -22.8093
4360 | R-123 | 20.5 | 3.51 | -11.19 | -22.7889
4361 | R-123 | 20.6 | 3.52 | -11.18 | -22.7706
4362 | R-123 | 20.7 | 3.53 | -11.17 | -22.7503
4363 | R-123 | 20.8 | 3.54 | -11.17 | -22.7319
4364 | R-123 | 20.9 | 3.54 | -11.15 | -22.7116
4365 | R-123 | 21 | 3.55 | -11.15 | -22.6933
4366 | R-123 | 21.1 | 3.56 | -11.14 | -22.6729
4367 | R-123 | 21.2 | 3.57 | -11.13 | -22.6546
4368 | R-123 | 21.3 | 3.58 | -11.12 | -22.6342
4369 | R-123 | 21.4 | 3.59 | -11.11 | -22.6159
4370 | R-123 | 21.5 | 3.6 | -11.1 | -22.5955
4371 | R-123 | 21.6 | 3.61 | -11.09 | -22.5752
4372 | R-123 | 21.7 | 3.62 | -11.08 | -22.5568
4373 | R-123 | 21.8 | 3.63 | -11.07 | -22.5365
4374 | R-123 | 21.9 | 3.64 | -11.06 | -22.5161
4375 | R-123 | 22 | 3.65 | -11.05 | -22.4978
4376 | R-123 | 22.1 | 3.66 | -11.04 | -22.4774
4377 | R-123 | 22.2 | 3.67 | -11.03 | -22.4571
4378 | R-123 | 22.3 | 3.68 | -11.02 | -22.4367
4379 | R-123 | 22.4 | 3.69 | -11.01 | -22.4184
4380 | R-123 | 22.5 | 3.7 | -11 | -22.398
4381 | R-123 | 22.6 | 3.71 | -10.99 | -22.3777
4382 | R-123 | 22.7 | 3.72 | -10.98 | -22.3573
4383 | R-123 | 22.8 | 3.73 | -10.97 | -22.337
4384 | R-123 | 22.9 | 3.74 | -10.96 | -22.3166
4385 | R-123 | 23 | 3.75 | -10.95 | -22.2962
4386 | R-123 | 23.1 | 3.76 | -10.94 | -22.2759
4387 | R-123 | 23.2 | 3.77 | -10.93 | -22.2555
4388 | R-123 | 23.3 | 3.78 | -10.92 | -22.2352
4389 | R-123 | 23.4 | 3.79 | -10.91 | -22.2148
4390 | R-123 | 23.5 | 3.8 | -10.9 | -22.1944
4391 | R-123 | 23.6 | 3.81 | -10.89 | -22.1741
4392 | R-123 | 23.7 | 3.82 | -10.88 | -22.1537
4393 | R-123 | 23.8 | 3.83 | -10.87 | -22.1334
4394 | R-123 | 23.9 | 3.84 | -10.86 | -22.113
4395 | R-123 | 24 | 3.85 | -10.85 | -22.0926
4396 | R-123 | 24.1 | 3.86 | -10.84 | -22.0723
4397 | R-123 | 24.2 | 3.87 | -10.83 | -22.0499
4398 | R-123 | 24.3 | 3.88 | -10.82 | -22.0295
4399 | R-123 | 24.4 | 3.89 | -10.81 | -22.0092
4400 | R-123 | 24.5 | 3.9 | -10.8 | -21.9888
4401 | R-123 | 24.6 | 3.91 | -10.79 | -21.9664
4402 | R-123 | 24.7 | 3.92 | -10.78 | -21.946
4403 | R-123 | 24.8 | 3.93 | -10.77 | -21.9257
4404 | R-123 | 24.9 | 3.94 | -10.76 | -21.9033
4405 | R-123 | 25 | 3.95 | -10.75 | -21.8829
4406 | R-123 | 25.1 | 3.96 | -10.74 | -21.8626
4407 | R-123 | 25.2 | 3.97 | -10.73 | -21.8402
4408 | R-123 | 25.3 | 3.98 | -10.72 | -21.8198
4409 | R-123 | 25.4 | 3.99 | -10.71 | -21.7974
4410 | R-123 | 25.5 | 4 | -10.7 | -21.7771
4411 | R-123 | 25.6 | 4.01 | -10.69 | -21.7547
4412 | R-123 | 25.7 | 4.03 | -10.68 | -21.7343
4413 | R-123 | 25.8 | 4.04 | -10.66 | -21.7119
4414 | R-123 | 25.9 | 4.05 | -10.65 | -21.6915
4415 | R-123 | 26 | 4.06 | -10.64 | -21.6691
4416 | R-123 | 26.1 | 4.07 | -10.63 | -21.6488
4417 | R-123 | 26.2 | 4.08 | -10.62 | -21.6264
4418 | R-123 | 26.3 | 4.09 | -10.61 | -21.604
4419 | R-123 | 26.4 | 4.1 | -10.6 | -21.5836
4420 | R-123 | 26.5 | 4.11 | -10.59 | -21.5612
4421 | R-123 | 26.6 | 4.12 | -10.58 | -21.5388
4422 | R-123 | 26.7 | 4.13 | -10.57 | -21.5164
4423 | R-123 | 26.8 | 4.14 | -10.56 | -21.4961
4424 | R-123 | 26.9 | 4.15 | -10.55 | -21.4737
4425 | R-123 | 27 | 4.16 | -10.54 | -21.4513
4426 | R-123 | 27.1 | 4.17 | -10.53 | -21.4289
4427 | R-123 | 27.2 | 4.19 | -10.51 | -21.4065
4428 | R-123 | 27.3 | 4.2 | -10.5 | -21.3841
4429 | R-123 | 27.4 | 4.21 | -10.49 | -21.3617
4430 | R-123 | 27.5 | 4.22 | -10.48 | -21.3413
4431 | R-123 | 27.6 | 4.23 | -10.47 | -21.319
4432 | R-123 | 27.7 | 4.24 | -10.46 | -21.2966
4433 | R-123 | 27.8 | 4.25 | -10.45 | -21.2742
4434 | R-123 | 27.9 | 4.26 | -10.44 | -21.2518
4435 | R-123 | 28 | 4.27 | -10.43 | -21.2294
4436 | R-123 | 28.1 | 4.29 | -10.42 | -21.2049
4437 | R-123 | 28.2 | 4.3 | -10.4 | -21.1825
4438 | R-123 | 28.3 | 4.31 | -10.39 | -21.1602
4439 | R-123 | 28.4 | 4.32 | -10.38 | -21.1378
4440 | R-123 | 28.5 | 4.33 | -10.37 | -21.1154
4441 | R-123 | 28.6 | 4.34 | -10.36 | -21.093
4442 | R-123 | 28.7 | 4.35 | -10.35 | -21.0706
4443 | R-123 | 28.8 | 4.36 | -10.34 | -21.0461
4444 | R-123 | 28.9 | 4.37 | -10.33 | -21.0237
4445 | R-123 | 29 | 4.38 | -10.31 | -21.0013
4446 | R-123 | 29.1 | 4.4 | -10.3 | -20.9769
4447 | R-123 | 29.2 | 4.41 | -10.29 | -20.9545
4448 | R-123 | 29.3 | 4.42 | -10.28 | -20.9321
4449 | R-123 | 29.4 | 4.43 | -10.27 | -20.9077
4450 | R-123 | 29.5 | 4.44 | -10.26 | -20.8853
4451 | R-123 | 29.6 | 4.45 | -10.25 | -20.8629
4452 | R-123 | 29.7 | 4.46 | -10.23 | -20.8385
4453 | R-123 | 29.8 | 4.48 | -10.22 | -20.8161
4454 | R-123 | 29.9 | 4.49 | -10.21 | -20.7916
4455 | R-123 | 30 | 4.5 | -10.2 | -20.7692
4456 | R-123 | 30.1 | 4.51 | -10.19 | -20.7448
4457 | R-123 | 30.2 | 4.52 | -10.18 | -20.7224
4458 | R-123 | 30.3 | 4.53 | -10.17 | -20.698
4459 | R-123 | 30.4 | 4.55 | -10.15 | -20.6735
4460 | R-123 | 30.5 | 4.56 | -10.14 | -20.6512
4461 | R-123 | 30.6 | 4.57 | -10.13 | -20.6267
4462 | R-123 | 30.7 | 4.58 | -10.12 | -20.6023
4463 | R-123 | 30.8 | 4.59 | -10.11 | -20.5799
4464 | R-123 | 30.9 | 4.6 | -10.1 | -20.5555
4465 | R-123 | 31 | 4.62 | -10.08 | -20.531
4466 | R-123 | 31.1 | 4.63 | -10.07 | -20.5066
4467 | R-123 | 31.2 | 4.64 | -10.06 | -20.4842
4468 | R-123 | 31.3 | 4.65 | -10.05 | -20.4598
4469 | R-123 | 31.4 | 4.66 | -10.04 | -20.4353
4470 | R-123 | 31.5 | 4.67 | -10.03 | -20.4109
4471 | R-123 | 31.6 | 4.69 | -10.01 | -20.3865
4472 | R-123 | 31.7 | 4.7 | -10 | -20.362
4473 | R-123 | 31.8 | 4.71 | -9.99 | -20.3376
4474 | R-123 | 31.9 | 4.72 | -9.98 | -20.3132
4475 | R-123 | 32 | 4.74 | -9.96 | -20.2887
4476 | R-123 | 32.1 | 4.75 | -9.95 | -20.2643
4477 | R-123 | 32.2 | 4.76 | -9.94 | -20.2399
4478 | R-123 | 32.3 | 4.77 | -9.93 | -20.2154
4479 | R-123 | 32.4 | 4.78 | -9.92 | -20.191
4480 | R-123 | 32.5 | 4.8 | -9.9 | -20.1666
4481 | R-123 | 32.6 | 4.81 | -9.89 | -20.1422
4482 | R-123 | 32.7 | 4.82 | -9.88 | -20.1177
4483 | R-123 | 32.8 | 4.83 | -9.87 | -20.0912
4484 | R-123 | 32.9 | 4.84 | -9.86 | -20.0668
4485 | R-123 | 33 | 4.86 | -9.84 | -20.0424
4486 | R-123 | 33.1 | 4.87 | -9.83 | -20.0179
4487 | R-123 | 33.2 | 4.88 | -9.82 | -19.9915
4488 | R-123 | 33.3 | 4.89 | -9.81 | -19.9671
4489 | R-123 | 33.4 | 4.91 | -9.8 | -19.9426
4490 | R-123 | 33.5 | 4.92 | -9.78 | -19.9161
4491 | R-123 | 33.6 | 4.93 | -9.77 | -19.8917
4492 | R-123 | 33.7 | 4.94 | -9.76 | -19.8652
4493 | R-123 | 33.8 | 4.96 | -9.75 | -19.8408
4494 | R-123 | 33.9 | 4.97 | -9.73 | -19.8144
4495 | R-123 | 34 | 4.98 | -9.72 | -19.7899
4496 | R-123 | 34.1 | 4.99 | -9.71 | -19.7634
4497 | R-123 | 34.2 | 5 | -9.7 | -19.739
4498 | R-123 | 34.3 | 5.02 | -9.68 | -19.7126
4499 | R-123 | 34.4 | 5.03 | -9.67 | -19.6881
4500 | R-123 | 34.5 | 5.04 | -9.66 | -19.6617
4501 | R-123 | 34.6 | 5.06 | -9.64 | -19.6352
4502 | R-123 | 34.7 | 5.07 | -9.63 | -19.6107
4503 | R-123 | 34.8 | 5.08 | -9.62 | -19.5843
4504 | R-123 | 34.9 | 5.09 | -9.61 | -19.5578
4505 | R-123 | 35 | 5.11 | -9.59 | -19.5313
4506 | R-123 | 35.1 | 5.12 | -9.58 | -19.5069
4507 | R-123 | 35.2 | 5.13 | -9.57 | -19.4805
4508 | R-123 | 35.3 | 5.15 | -9.55 | -19.454
4509 | R-123 | 35.4 | 5.16 | -9.54 | -19.4275
4510 | R-123 | 35.5 | 5.17 | -9.53 | -19.401
4511 | R-123 | 35.6 | 5.18 | -9.52 | -19.3746
4512 | R-123 | 35.7 | 5.2 | -9.5 | -19.3481
4513 | R-123 | 35.8 | 5.21 | -9.49 | -19.3216
4514 | R-123 | 35.9 | 5.22 | -9.48 | -19.2972
4515 | R-123 | 36 | 5.24 | -9.46 | -19.2687
4516 | R-123 | 36.1 | 5.25 | -9.45 | -19.2422
4517 | R-123 | 36.2 | 5.26 | -9.44 | -19.2158
4518 | R-123 | 36.3 | 5.28 | -9.43 | -19.1893
4519 | R-123 | 36.4 | 5.29 | -9.41 | -19.1628
4520 | R-123 | 36.5 | 5.3 | -9.4 | -19.1364
4521 | R-123 | 36.6 | 5.31 | -9.39 | -19.1099
4522 | R-123 | 36.7 | 5.33 | -9.37 | -19.0834
4523 | R-123 | 36.8 | 5.34 | -9.36 | -19.0549
4524 | R-123 | 36.9 | 5.35 | -9.35 | -19.0285
4525 | R-123 | 37 | 5.37 | -9.33 | -19.002
4526 | R-123 | 37.1 | 5.38 | -9.32 | -18.9755
4527 | R-123 | 37.2 | 5.39 | -9.31 | -18.947
4528 | R-123 | 37.3 | 5.41 | -9.29 | -18.9205
4529 | R-123 | 37.4 | 5.42 | -9.28 | -18.892
4530 | R-123 | 37.5 | 5.43 | -9.27 | -18.8656
4531 | R-123 | 37.6 | 5.45 | -9.25 | -18.8391
4532 | R-123 | 37.7 | 5.46 | -9.24 | -18.8106
4533 | R-123 | 37.8 | 5.47 | -9.23 | -18.7841
4534 | R-123 | 37.9 | 5.49 | -9.21 | -18.7556
4535 | R-123 | 38 | 5.5 | -9.2 | -18.7292
4536 | R-123 | 38.1 | 5.51 | -9.19 | -18.7007
4537 | R-123 | 38.2 | 5.53 | -9.17 | -18.6722
4538 | R-123 | 38.3 | 5.54 | -9.16 | -18.6457
4539 | R-123 | 38.4 | 5.56 | -9.14 | -18.6172
4540 | R-123 | 38.5 | 5.57 | -9.13 | -18.5887
4541 | R-123 | 38.6 | 5.58 | -9.12 | -18.5622
4542 | R-123 | 38.7 | 5.6 | -9.1 | -18.5337
4543 | R-123 | 38.8 | 5.61 | -9.09 | -18.5052
4544 | R-123 | 38.9 | 5.63 | -9.08 | -18.4767
4545 | R-123 | 39 | 5.64 | -9.06 | -18.4502
4546 | R-123 | 39.1 | 5.65 | -9.05 | -18.4217
4547 | R-123 | 39.2 | 5.67 | -9.03 | -18.3932
4548 | R-123 | 39.3 | 5.68 | -9.02 | -18.3647
4549 | R-123 | 39.4 | 5.69 | -9.01 | -18.3362
4550 | R-123 | 39.5 | 5.71 | -8.99 | -18.3077
4551 | R-123 | 39.6 | 5.72 | -8.98 | -18.2792
4552 | R-123 | 39.7 | 5.74 | -8.96 | -18.2507
4553 | R-123 | 39.8 | 5.75 | -8.95 | -18.2222
4554 | R-123 | 39.9 | 5.76 | -8.94 | -18.1937
4555 | R-123 | 40 | 5.78 | -8.92 | -18.1652
4556 | R-123 | 40.1 | 5.79 | -8.91 | -18.1367
4557 | R-123 | 40.2 | 5.81 | -8.89 | -18.1082
4558 | R-123 | 40.3 | 5.82 | -8.88 | -18.0776
4559 | R-123 | 40.4 | 5.84 | -8.87 | -18.0491
4560 | R-123 | 40.5 | 5.85 | -8.85 | -18.0206
4561 | R-123 | 40.6 | 5.86 | -8.84 | -17.9921
4562 | R-123 | 40.7 | 5.88 | -8.82 | -17.9616
4563 | R-123 | 40.8 | 5.89 | -8.81 | -17.9331
4564 | R-123 | 40.9 | 5.91 | -8.79 | -17.9046
4565 | R-123 | 41 | 5.92 | -8.78 | -17.874
4566 | R-123 | 41.1 | 5.94 | -8.77 | -17.8455
4567 | R-123 | 41.2 | 5.95 | -8.75 | -17.817
4568 | R-123 | 41.3 | 5.96 | -8.74 | -17.7865
4569 | R-123 | 41.4 | 5.98 | -8.72 | -17.758
4570 | R-123 | 41.5 | 5.99 | -8.71 | -17.7275
4571 | R-123 | 41.6 | 6.01 | -8.69 | -17.6989
4572 | R-123 | 41.7 | 6.02 | -8.68 | -17.6684
4573 | R-123 | 41.8 | 6.04 | -8.66 | -17.6379
4574 | R-123 | 41.9 | 6.05 | -8.65 | -17.6094
4575 | R-123 | 42 | 6.07 | -8.63 | -17.5788
4576 | R-123 | 42.1 | 6.08 | -8.62 | -17.5483
4577 | R-123 | 42.2 | 6.09 | -8.61 | -17.5198
4578 | R-123 | 42.3 | 6.11 | -8.59 | -17.4892
4579 | R-123 | 42.4 | 6.13 | -8.58 | -17.4587
4580 | R-123 | 42.5 | 6.14 | -8.56 | -17.4282
4581 | R-123 | 42.6 | 6.15 | -8.55 | -17.3997
4582 | R-123 | 42.7 | 6.17 | -8.53 | -17.3691
4583 | R-123 | 42.8 | 6.18 | -8.52 | -17.3386
4584 | R-123 | 42.9 | 6.2 | -8.5 | -17.308
4585 | R-123 | 43 | 6.21 | -8.49 | -17.2775
4586 | R-123 | 43.1 | 6.23 | -8.47 | -17.247
4587 | R-123 | 43.2 | 6.24 | -8.46 | -17.2164
4588 | R-123 | 43.3 | 6.26 | -8.44 | -17.1859
4589 | R-123 | 43.4 | 6.27 | -8.43 | -17.1553
4590 | R-123 | 43.5 | 6.29 | -8.41 | -17.1248
4591 | R-123 | 43.6 | 6.3 | -8.4 | -17.0943
4592 | R-123 | 43.7 | 6.32 | -8.38 | -17.0637
4593 | R-123 | 43.8 | 6.34 | -8.37 | -17.0311
4594 | R-123 | 43.9 | 6.35 | -8.35 | -17.0006
4595 | R-123 | 44 | 6.37 | -8.34 | -16.9701
4596 | R-123 | 44.1 | 6.38 | -8.32 | -16.9395
4597 | R-123 | 44.2 | 6.4 | -8.3 | -16.9069
4598 | R-123 | 44.3 | 6.41 | -8.29 | -16.8764
4599 | R-123 | 44.4 | 6.43 | -8.27 | -16.8459
4600 | R-123 | 44.5 | 6.44 | -8.26 | -16.8133
4601 | R-123 | 44.6 | 6.46 | -8.24 | -16.7828
4602 | R-123 | 44.7 | 6.47 | -8.23 | -16.7522
4603 | R-123 | 44.8 | 6.49 | -8.21 | -16.7196
4604 | R-123 | 44.9 | 6.5 | -8.2 | -16.6891
4605 | R-123 | 45 | 6.52 | -8.18 | -16.6565
4606 | R-123 | 45.1 | 6.54 | -8.17 | -16.6239
4607 | R-123 | 45.2 | 6.55 | -8.15 | -16.5934
4608 | R-123 | 45.3 | 6.57 | -8.13 | -16.5608
4609 | R-123 | 45.4 | 6.58 | -8.12 | -16.5303
4610 | R-123 | 45.5 | 6.6 | -8.1 | -16.4977
4611 | R-123 | 45.6 | 6.61 | -8.09 | -16.4651
4612 | R-123 | 45.7 | 6.63 | -8.07 | -16.4326
4613 | R-123 | 45.8 | 6.64 | -8.06 | -16.402
4614 | R-123 | 45.9 | 6.66 | -8.04 | -16.3694
4615 | R-123 | 46 | 6.68 | -8.02 | -16.3369
4616 | R-123 | 46.1 | 6.69 | -8.01 | -16.3043
4617 | R-123 | 46.2 | 6.71 | -7.99 | -16.2717
4618 | R-123 | 46.3 | 6.72 | -7.98 | -16.2391
4619 | R-123 | 46.4 | 6.74 | -7.96 | -16.2066
4620 | R-123 | 46.5 | 6.75 | -7.95 | -16.176
4621 | R-123 | 46.6 | 6.77 | -7.93 | -16.1414
4622 | R-123 | 46.7 | 6.79 | -7.91 | -16.1088
4623 | R-123 | 46.8 | 6.8 | -7.9 | -16.0763
4624 | R-123 | 46.9 | 6.82 | -7.88 | -16.0437
4625 | R-123 | 47 | 6.84 | -7.86 | -16.0111
4626 | R-123 | 47.1 | 6.85 | -7.85 | -15.9785
4627 | R-123 | 47.2 | 6.87 | -7.83 | -15.9459
4628 | R-123 | 47.3 | 6.88 | -7.82 | -15.9134
4629 | R-123 | 47.4 | 6.9 | -7.8 | -15.8788
4630 | R-123 | 47.5 | 6.92 | -7.78 | -15.8462
4631 | R-123 | 47.6 | 6.93 | -7.77 | -15.8136
4632 | R-123 | 47.7 | 6.95 | -7.75 | -15.779
4633 | R-123 | 47.8 | 6.97 | -7.73 | -15.7464
4634 | R-123 | 47.9 | 6.98 | -7.72 | -15.7139
4635 | R-123 | 48 | 7 | -7.7 | -15.6792
4636 | R-123 | 48.1 | 7.02 | -7.69 | -15.6467
4637 | R-123 | 48.2 | 7.03 | -7.67 | -15.612
4638 | R-123 | 48.3 | 7.05 | -7.65 | -15.5795
4639 | R-123 | 48.4 | 7.07 | -7.63 | -15.5449
4640 | R-123 | 48.5 | 7.08 | -7.62 | -15.5123
4641 | R-123 | 48.6 | 7.1 | -7.6 | -15.4777
4642 | R-123 | 48.7 | 7.12 | -7.59 | -15.4431
4643 | R-123 | 48.8 | 7.13 | -7.57 | -15.4105
4644 | R-123 | 48.9 | 7.15 | -7.55 | -15.3759
4645 | R-123 | 49 | 7.17 | -7.54 | -15.3413
4646 | R-123 | 49.1 | 7.18 | -7.52 | -15.3066
4647 | R-123 | 49.2 | 7.2 | -7.5 | -15.272
4648 | R-123 | 49.3 | 7.21 | -7.49 | -15.2395
4649 | R-123 | 49.4 | 7.23 | -7.47 | -15.2049
4650 | R-123 | 49.5 | 7.25 | -7.45 | -15.1702
4651 | R-123 | 49.6 | 7.27 | -7.43 | -15.1356
4652 | R-123 | 49.7 | 7.28 | -7.42 | -15.101
4653 | R-123 | 49.8 | 7.3 | -7.4 | -15.0664
4654 | R-123 | 49.9 | 7.32 | -7.38 | -15.0318
4655 | R-123 | 50 | 7.33 | -7.37 | -14.9972
4656 | R-123 | 50.1 | 7.35 | -7.35 | -14.9626
4657 | R-123 | 50.2 | 7.37 | -7.33 | -14.9279
4658 | R-123 | 50.3 | 7.39 | -7.31 | -14.8913
4659 | R-123 | 50.4 | 7.4 | -7.3 | -14.8567
4660 | R-123 | 50.5 | 7.42 | -7.28 | -14.8221
4661 | R-123 | 50.6 | 7.44 | -7.26 | -14.7875
4662 | R-123 | 50.7 | 7.45 | -7.25 | -14.7529
4663 | R-123 | 50.8 | 7.47 | -7.23 | -14.7162
4664 | R-123 | 50.9 | 7.49 | -7.21 | -14.6816
4665 | R-123 | 51 | 7.51 | -7.19 | -14.6449
4666 | R-123 | 51.1 | 7.52 | -7.18 | -14.6103
4667 | R-123 | 51.2 | 7.54 | -7.16 | -14.5757
4668 | R-123 | 51.3 | 7.56 | -7.14 | -14.5391
4669 | R-123 | 51.4 | 7.58 | -7.12 | -14.5045
4670 | R-123 | 51.5 | 7.59 | -7.11 | -14.4678
4671 | R-123 | 51.6 | 7.61 | -7.09 | -14.4312
4672 | R-123 | 51.7 | 7.63 | -7.07 | -14.3966
4673 | R-123 | 51.8 | 7.65 | -7.05 | -14.3599
4674 | R-123 | 51.9 | 7.66 | -7.04 | -14.3253
4675 | R-123 | 52 | 7.68 | -7.02 | -14.2887
4676 | R-123 | 52.1 | 7.7 | -7 | -14.252
4677 | R-123 | 52.2 | 7.72 | -6.98 | -14.2154
4678 | R-123 | 52.3 | 7.74 | -6.96 | -14.1787
4679 | R-123 | 52.4 | 7.75 | -6.95 | -14.1441
4680 | R-123 | 52.5 | 7.77 | -6.93 | -14.1074
4681 | R-123 | 52.6 | 7.79 | -6.91 | -14.0708
4682 | R-123 | 52.7 | 7.81 | -6.89 | -14.0342
4683 | R-123 | 52.8 | 7.83 | -6.88 | -13.9975
4684 | R-123 | 52.9 | 7.84 | -6.86 | -13.9609
4685 | R-123 | 53 | 7.86 | -6.84 | -13.9242
4686 | R-123 | 53.1 | 7.88 | -6.82 | -13.8876
4687 | R-123 | 53.2 | 7.9 | -6.8 | -13.8509
4688 | R-123 | 53.3 | 7.92 | -6.79 | -13.8143
4689 | R-123 | 53.4 | 7.93 | -6.77 | -13.7756
4690 | R-123 | 53.5 | 7.95 | -6.75 | -13.7389
4691 | R-123 | 53.6 | 7.97 | -6.73 | -13.7023
4692 | R-123 | 53.7 | 7.99 | -6.71 | -13.6656
4693 | R-123 | 53.8 | 8.01 | -6.69 | -13.627
4694 | R-123 | 53.9 | 8.03 | -6.67 | -13.5903
4695 | R-123 | 54 | 8.04 | -6.66 | -13.5536
4696 | R-123 | 54.1 | 8.06 | -6.64 | -13.515
4697 | R-123 | 54.2 | 8.08 | -6.62 | -13.4783
4698 | R-123 | 54.3 | 8.1 | -6.6 | -13.4396
4699 | R-123 | 54.4 | 8.12 | -6.58 | -13.403
4700 | R-123 | 54.5 | 8.14 | -6.56 | -13.3643
4701 | R-123 | 54.6 | 8.15 | -6.55 | -13.3277
4702 | R-123 | 54.7 | 8.17 | -6.53 | -13.289
4703 | R-123 | 54.8 | 8.19 | -6.51 | -13.2523
4704 | R-123 | 54.9 | 8.21 | -6.49 | -13.2136
4705 | R-123 | 55 | 8.23 | -6.47 | -13.175
4706 | R-123 | 55.1 | 8.25 | -6.45 | -13.1363
4707 | R-123 | 55.2 | 8.27 | -6.43 | -13.0996
4708 | R-123 | 55.3 | 8.29 | -6.42 | -13.0609
4709 | R-123 | 55.4 | 8.3 | -6.4 | -13.0223
4710 | R-123 | 55.5 | 8.32 | -6.38 | -12.9836
4711 | R-123 | 55.6 | 8.34 | -6.36 | -12.9449
4712 | R-123 | 55.7 | 8.36 | -6.34 | -12.9062
4713 | R-123 | 55.8 | 8.38 | -6.32 | -12.8675
4714 | R-123 | 55.9 | 8.4 | -6.3 | -12.8288
4715 | R-123 | 56 | 8.42 | -6.28 | -12.7902
4716 | R-123 | 56.1 | 8.44 | -6.26 | -12.7515
4717 | R-123 | 56.2 | 8.46 | -6.24 | -12.7128
4718 | R-123 | 56.3 | 8.47 | -6.23 | -12.6741
4719 | R-123 | 56.4 | 8.49 | -6.21 | -12.6354
4720 | R-123 | 56.5 | 8.51 | -6.19 | -12.5947
4721 | R-123 | 56.6 | 8.53 | -6.17 | -12.556
4722 | R-123 | 56.7 | 8.55 | -6.15 | -12.5173
4723 | R-123 | 56.8 | 8.57 | -6.13 | -12.4786
4724 | R-123 | 56.9 | 8.59 | -6.11 | -12.4379
4725 | R-123 | 57 | 8.61 | -6.09 | -12.3992
4726 | R-123 | 57.1 | 8.63 | -6.07 | -12.3585
4727 | R-123 | 57.2 | 8.65 | -6.05 | -12.3198
4728 | R-123 | 57.3 | 8.67 | -6.03 | -12.2791
4729 | R-123 | 57.4 | 8.69 | -6.01 | -12.2404
4730 | R-123 | 57.5 | 8.71 | -5.99 | -12.1997
4731 | R-123 | 57.6 | 8.73 | -5.97 | -12.161
4732 | R-123 | 57.7 | 8.75 | -5.95 | -12.1203
4733 | R-123 | 57.8 | 8.77 | -5.93 | -12.0796
4734 | R-123 | 57.9 | 8.79 | -5.91 | -12.0409
4735 | R-123 | 58 | 8.81 | -5.89 | -12.0002
4736 | R-123 | 58.1 | 8.83 | -5.87 | -11.9595
4737 | R-123 | 58.2 | 8.85 | -5.85 | -11.9187
4738 | R-123 | 58.3 | 8.87 | -5.84 | -11.8801
4739 | R-123 | 58.4 | 8.88 | -5.82 | -11.8393
4740 | R-123 | 58.5 | 8.9 | -5.8 | -11.7986
4741 | R-123 | 58.6 | 8.93 | -5.78 | -11.7579
4742 | R-123 | 58.7 | 8.95 | -5.75 | -11.7172
4743 | R-123 | 58.8 | 8.96 | -5.74 | -11.6765
4744 | R-123 | 58.9 | 8.98 | -5.71 | -11.6357
4745 | R-123 | 59 | 9.01 | -5.7 | -11.595
4746 | R-123 | 59.1 | 9.03 | -5.67 | -11.5523
4747 | R-123 | 59.2 | 9.05 | -5.65 | -11.5115
4748 | R-123 | 59.3 | 9.07 | -5.63 | -11.4708
4749 | R-123 | 59.4 | 9.09 | -5.61 | -11.4301
4750 | R-123 | 59.5 | 9.11 | -5.59 | -11.3894
4751 | R-123 | 59.6 | 9.13 | -5.57 | -11.3466
4752 | R-123 | 59.7 | 9.15 | -5.55 | -11.3059
4753 | R-123 | 59.8 | 9.17 | -5.53 | -11.2631
4754 | R-123 | 59.9 | 9.19 | -5.51 | -11.2224
4755 | R-123 | 60 | 9.21 | -5.49 | -11.1817
4756 | R-123 | 60.1 | 9.23 | -5.47 | -11.139
4757 | R-123 | 60.2 | 9.25 | -5.45 | -11.0982
4758 | R-123 | 60.3 | 9.27 | -5.43 | -11.0555
4759 | R-123 | 60.4 | 9.29 | -5.41 | -11.0127
4760 | R-123 | 60.5 | 9.31 | -5.39 | -10.972
4761 | R-123 | 60.6 | 9.33 | -5.37 | -10.9292
4762 | R-123 | 60.7 | 9.35 | -5.35 | -10.8865
4763 | R-123 | 60.8 | 9.37 | -5.33 | -10.8458
4764 | R-123 | 60.9 | 9.39 | -5.31 | -10.803
4765 | R-123 | 61 | 9.42 | -5.29 | -10.7603
4766 | R-123 | 61.1 | 9.44 | -5.26 | -10.7175
4767 | R-123 | 61.2 | 9.46 | -5.24 | -10.6747
4768 | R-123 | 61.3 | 9.48 | -5.22 | -10.632
4769 | R-123 | 61.4 | 9.5 | -5.2 | -10.5892
4770 | R-123 | 61.5 | 9.52 | -5.18 | -10.5465
4771 | R-123 | 61.6 | 9.54 | -5.16 | -10.5037
4772 | R-123 | 61.7 | 9.56 | -5.14 | -10.461
4773 | R-123 | 61.8 | 9.58 | -5.12 | -10.4182
4774 | R-123 | 61.9 | 9.6 | -5.1 | -10.3755
4775 | R-123 | 62 | 9.63 | -5.08 | -10.3327
4776 | R-123 | 62.1 | 9.65 | -5.05 | -10.2899
4777 | R-123 | 62.2 | 9.67 | -5.03 | -10.2452
4778 | R-123 | 62.3 | 9.69 | -5.01 | -10.2024
4779 | R-123 | 62.4 | 9.71 | -4.99 | -10.1596
4780 | R-123 | 62.5 | 9.73 | -4.97 | -10.1149
4781 | R-123 | 62.6 | 9.75 | -4.95 | -10.0721
4782 | R-123 | 62.7 | 9.78 | -4.92 | -10.0273
4783 | R-123 | 62.8 | 9.8 | -4.9 | -9.9845
4784 | R-123 | 62.9 | 9.82 | -4.88 | -9.9398
4785 | R-123 | 63 | 9.84 | -4.86 | -9.897
4786 | R-123 | 63.1 | 9.86 | -4.84 | -9.8522
4787 | R-123 | 63.2 | 9.88 | -4.82 | -9.8095
4788 | R-123 | 63.3 | 9.9 | -4.8 | -9.7647
4789 | R-123 | 63.4 | 9.93 | -4.77 | -9.7199
4790 | R-123 | 63.5 | 9.95 | -4.75 | -9.6751
4791 | R-123 | 63.6 | 9.97 | -4.73 | -9.6323
4792 | R-123 | 63.7 | 9.99 | -4.71 | -9.5875
4793 | R-123 | 63.8 | 10.01 | -4.69 | -9.5488
4794 | R-123 | 63.9 | 10.03 | -4.67 | -9.5081
4795 | R-123 | 64 | 10.06 | -4.64 | -9.447
4796 | R-123 | 64.1 | 10.08 | -4.62 | -9.4063
4797 | R-123 | 64.2 | 10.1 | -4.6 | -9.3656
4798 | R-123 | 64.3 | 10.12 | -4.58 | -9.3249
4799 | R-123 | 64.4 | 10.15 | -4.55 | -9.2638
4800 | R-123 | 64.5 | 10.17 | -4.53 | -9.2231
4801 | R-123 | 64.6 | 10.19 | -4.51 | -9.1824
4802 | R-123 | 64.7 | 10.21 | -4.49 | -9.1416
4803 | R-123 | 64.8 | 10.23 | -4.47 | -9.1009
4804 | R-123 | 64.9 | 10.26 | -4.44 | -9.0398
4805 | R-123 | 65 | 10.28 | -4.42 | -8.9991
4806 | R-123 | 65.1 | 10.3 | -4.4 | -8.9584
4807 | R-123 | 65.2 | 10.32 | -4.38 | -8.9177
4808 | R-123 | 65.3 | 10.35 | -4.35 | -8.8566
4809 | R-123 | 65.4 | 10.37 | -4.33 | -8.8159
4810 | R-123 | 65.5 | 10.39 | -4.31 | -8.7752
4811 | R-123 | 65.6 | 10.41 | -4.29 | -8.7344
4812 | R-123 | 65.7 | 10.44 | -4.26 | -8.6734
4813 | R-123 | 65.8 | 10.46 | -4.24 | -8.6326
4814 | R-123 | 65.9 | 10.48 | -4.22 | -8.5919
4815 | R-123 | 66 | 10.5 | -4.2 | -8.5512
4816 | R-123 | 66.1 | 10.53 | -4.17 | -8.4901
4817 | R-123 | 66.2 | 10.55 | -4.15 | -8.4494
4818 | R-123 | 66.3 | 10.57 | -4.13 | -8.4087
4819 | R-123 | 66.4 | 10.6 | -4.1 | -8.3476
4820 | R-123 | 66.5 | 10.62 | -4.08 | -8.3069
4821 | R-123 | 66.6 | 10.64 | -4.06 | -8.2662
4822 | R-123 | 66.7 | 10.66 | -4.04 | -8.2254
4823 | R-123 | 66.8 | 10.69 | -4.01 | -8.1644
4824 | R-123 | 66.9 | 10.71 | -3.99 | -8.1236
4825 | R-123 | 67 | 10.73 | -3.97 | -8.0829
4826 | R-123 | 67.1 | 10.76 | -3.94 | -8.0218
4827 | R-123 | 67.2 | 10.78 | -3.92 | -7.9811
4828 | R-123 | 67.3 | 10.8 | -3.9 | -7.9404
4829 | R-123 | 67.4 | 10.83 | -3.87 | -7.8793
4830 | R-123 | 67.5 | 10.85 | -3.85 | -7.8386
4831 | R-123 | 67.6 | 10.87 | -3.83 | -7.7979
4832 | R-123 | 67.7 | 10.9 | -3.8 | -7.7368
4833 | R-123 | 67.8 | 10.92 | -3.78 | -7.6961
4834 | R-123 | 67.9 | 10.94 | -3.76 | -7.6554
4835 | R-123 | 68 | 10.97 | -3.73 | -7.5943
4836 | R-123 | 68.1 | 10.99 | -3.71 | -7.5536
4837 | R-123 | 68.2 | 11.01 | -3.69 | -7.5128
4838 | R-123 | 68.3 | 11.04 | -3.66 | -7.4518
4839 | R-123 | 68.4 | 11.06 | -3.64 | -7.411
4840 | R-123 | 68.5 | 11.08 | -3.62 | -7.3703
4841 | R-123 | 68.6 | 11.11 | -3.59 | -7.3092
4842 | R-123 | 68.7 | 11.13 | -3.57 | -7.2685
4843 | R-123 | 68.8 | 11.16 | -3.54 | -7.2074
4844 | R-123 | 68.9 | 11.18 | -3.52 | -7.1667
4845 | R-123 | 69 | 11.2 | -3.5 | -7.126
4846 | R-123 | 69.1 | 11.23 | -3.47 | -7.0649
4847 | R-123 | 69.2 | 11.25 | -3.45 | -7.0242
4848 | R-123 | 69.3 | 11.28 | -3.42 | -6.9631
4849 | R-123 | 69.4 | 11.3 | -3.4 | -6.9224
4850 | R-123 | 69.5 | 11.32 | -3.38 | -6.8817
4851 | R-123 | 69.6 | 11.35 | -3.35 | -6.8206
4852 | R-123 | 69.7 | 11.37 | -3.33 | -6.7799
4853 | R-123 | 69.8 | 11.4 | -3.3 | -6.7188
4854 | R-123 | 69.9 | 11.42 | -3.28 | -6.6781
4855 | R-123 | 70 | 11.44 | -3.26 | -6.6374
4856 | R-123 | 70.1 | 11.47 | -3.23 | -6.5763
4857 | R-123 | 70.2 | 11.49 | -3.21 | -6.5356
4858 | R-123 | 70.3 | 11.52 | -3.18 | -6.4745
4859 | R-123 | 70.4 | 11.54 | -3.16 | -6.4338
4860 | R-123 | 70.5 | 11.57 | -3.13 | -6.3727
4861 | R-123 | 70.6 | 11.59 | -3.11 | -6.332
4862 | R-123 | 70.7 | 11.62 | -3.08 | -6.2709
4863 | R-123 | 70.8 | 11.64 | -3.06 | -6.2302
4864 | R-123 | 70.9 | 11.67 | -3.03 | -6.1691
4865 | R-123 | 71 | 11.69 | -3.01 | -6.1284
4866 | R-123 | 71.1 | 11.71 | -2.99 | -6.0876
4867 | R-123 | 71.2 | 11.74 | -2.96 | -6.0266
4868 | R-123 | 71.3 | 11.76 | -2.94 | -5.9858
4869 | R-123 | 71.4 | 11.79 | -2.91 | -5.9248
4870 | R-123 | 71.5 | 11.81 | -2.89 | -5.884
4871 | R-123 | 71.6 | 11.84 | -2.86 | -5.823
4872 | R-123 | 71.7 | 11.86 | -2.84 | -5.7822
4873 | R-123 | 71.8 | 11.89 | -2.81 | -5.7212
4874 | R-123 | 71.9 | 11.91 | -2.79 | -5.6804
4875 | R-123 | 72 | 11.94 | -2.76 | -5.6194
4876 | R-123 | 72.1 | 11.96 | -2.74 | -5.5786
4877 | R-123 | 72.2 | 11.99 | -2.71 | -5.5176
4878 | R-123 | 72.3 | 12.02 | -2.68 | -5.4565
4879 | R-123 | 72.4 | 12.04 | -2.66 | -5.4158
4880 | R-123 | 72.5 | 12.07 | -2.63 | -5.3547
4881 | R-123 | 72.6 | 12.09 | -2.61 | -5.314
4882 | R-123 | 72.7 | 12.12 | -2.58 | -5.2529
4883 | R-123 | 72.8 | 12.14 | -2.56 | -5.2122
4884 | R-123 | 72.9 | 12.17 | -2.53 | -5.1511
4885 | R-123 | 73 | 12.19 | -2.51 | -5.1104
4886 | R-123 | 73.1 | 12.22 | -2.48 | -5.0493
4887 | R-123 | 73.2 | 12.24 | -2.46 | -5.0086
4888 | R-123 | 73.3 | 12.27 | -2.43 | -4.9475
4889 | R-123 | 73.4 | 12.3 | -2.4 | -4.8864
4890 | R-123 | 73.5 | 12.32 | -2.38 | -4.8457
4891 | R-123 | 73.6 | 12.35 | -2.35 | -4.7846
4892 | R-123 | 73.7 | 12.37 | -2.33 | -4.7439
4893 | R-123 | 73.8 | 12.4 | -2.3 | -4.6828
4894 | R-123 | 73.9 | 12.42 | -2.28 | -4.6421
4895 | R-123 | 74 | 12.45 | -2.25 | -4.581
4896 | R-123 | 74.1 | 12.48 | -2.22 | -4.5199
4897 | R-123 | 74.2 | 12.5 | -2.2 | -4.4792
4898 | R-123 | 74.3 | 12.53 | -2.17 | -4.4181
4899 | R-123 | 74.4 | 12.56 | -2.14 | -4.357
4900 | R-123 | 74.5 | 12.58 | -2.12 | -4.3163
4901 | R-123 | 74.6 | 12.61 | -2.09 | -4.2552
4902 | R-123 | 74.7 | 12.63 | -2.07 | -4.2145
4903 | R-123 | 74.8 | 12.66 | -2.04 | -4.1534
4904 | R-123 | 74.9 | 12.69 | -2.01 | -4.0924
4905 | R-123 | 75 | 12.71 | -1.99 | -4.0516
4906 | R-123 | 75.1 | 12.74 | -1.96 | -3.9906
4907 | R-123 | 75.2 | 12.77 | -1.93 | -3.9295
4908 | R-123 | 75.3 | 12.79 | -1.91 | -3.8888
4909 | R-123 | 75.4 | 12.82 | -1.88 | -3.8277
4910 | R-123 | 75.5 | 12.85 | -1.85 | -3.7666
4911 | R-123 | 75.6 | 12.87 | -1.83 | -3.7259
4912 | R-123 | 75.7 | 12.9 | -1.8 | -3.6648
4913 | R-123 | 75.8 | 12.93 | -1.77 | -3.6037
4914 | R-123 | 75.9 | 12.95 | -1.75 | -3.563
4915 | R-123 | 76 | 12.98 | -1.72 | -3.5019
4916 | R-123 | 76.1 | 13.01 | -1.69 | -3.4408
4917 | R-123 | 76.2 | 13.03 | -1.67 | -3.4001
4918 | R-123 | 76.3 | 13.06 | -1.64 | -3.339
4919 | R-123 | 76.4 | 13.09 | -1.61 | -3.278
4920 | R-123 | 76.5 | 13.11 | -1.59 | -3.2372
4921 | R-123 | 76.6 | 13.14 | -1.56 | -3.1762
4922 | R-123 | 76.7 | 13.17 | -1.53 | -3.1151
4923 | R-123 | 76.8 | 13.2 | -1.5 | -3.054
4924 | R-123 | 76.9 | 13.22 | -1.48 | -3.0133
4925 | R-123 | 77 | 13.25 | -1.45 | -2.9522
4926 | R-123 | 77.1 | 13.28 | -1.42 | -2.8911
4927 | R-123 | 77.2 | 13.3 | -1.4 | -2.8504
4928 | R-123 | 77.3 | 13.33 | -1.37 | -2.7893
4929 | R-123 | 77.4 | 13.36 | -1.34 | -2.7282
4930 | R-123 | 77.5 | 13.39 | -1.31 | -2.6672
4931 | R-123 | 77.6 | 13.41 | -1.29 | -2.6264
4932 | R-123 | 77.7 | 13.44 | -1.26 | -2.5654
4933 | R-123 | 77.8 | 13.47 | -1.23 | -2.5043
4934 | R-123 | 77.9 | 13.5 | -1.2 | -2.4432
4935 | R-123 | 78 | 13.53 | -1.17 | -2.3821
4936 | R-123 | 78.1 | 13.55 | -1.15 | -2.3414
4937 | R-123 | 78.2 | 13.58 | -1.12 | -2.2803
4938 | R-123 | 78.3 | 13.61 | -1.09 | -2.2192
4939 | R-123 | 78.4 | 13.64 | -1.06 | -2.1582
4940 | R-123 | 78.5 | 13.66 | -1.04 | -2.1174
4941 | R-123 | 78.6 | 13.69 | -1.01 | -2.0564
4942 | R-123 | 78.7 | 13.72 | -0.98 | -1.9953
4943 | R-123 | 78.8 | 13.75 | -0.95 | -1.9342
4944 | R-123 | 78.9 | 13.78 | -0.92 | -1.8731
4945 | R-123 | 79 | 13.81 | -0.89 | -1.812
4946 | R-123 | 79.1 | 13.83 | -0.87 | -1.7713
4947 | R-123 | 79.2 | 13.86 | -0.84 | -1.7102
4948 | R-123 | 79.3 | 13.89 | -0.81 | -1.6492
4949 | R-123 | 79.4 | 13.92 | -0.78 | -1.5881
4950 | R-123 | 79.5 | 13.95 | -0.75 | -1.527
4951 | R-123 | 79.6 | 13.98 | -0.72 | -1.4659
4952 | R-123 | 79.7 | 14 | -0.7 | -1.4252
4953 | R-123 | 79.8 | 14.03 | -0.67 | -1.3641
4954 | R-123 | 79.9 | 14.06 | -0.64 | -1.303
4955 | R-123 | 80 | 14.09 | -0.61 | -1.242
4956 | R-123 | 80.1 | 14.12 | -0.58 | -1.1809
4957 | R-123 | 80.2 | 14.15 | -0.55 | -1.1198
4958 | R-123 | 80.3 | 14.18 | -0.52 | -1.0587
4959 | R-123 | 80.4 | 14.2 | -0.5 | -1.018
4960 | R-123 | 80.5 | 14.23 | -0.47 | -0.95692
4961 | R-123 | 80.6 | 14.26 | -0.44 | -0.89584
4962 | R-123 | 80.7 | 14.29 | -0.41 | -0.83476
4963 | R-123 | 80.8 | 14.32 | -0.38 | -0.77368
4964 | R-123 | 80.9 | 14.35 | -0.35 | -0.7126
4965 | R-123 | 81 | 14.38 | -0.32 | -0.65152
4966 | R-123 | 81.1 | 14.41 | -0.29 | -0.59044
4967 | R-123 | 81.2 | 14.44 | -0.26 | -0.52936
4968 | R-123 | 81.3 | 14.47 | -0.23 | -0.46828
4969 | R-123 | 81.4 | 14.5 | -0.2 | -0.4072
4970 | R-123 | 81.5 | 14.52 | -0.18 | -0.36648
4971 | R-123 | 81.6 | 14.55 | -0.15 | -0.3054
4972 | R-123 | 81.7 | 14.58 | -0.12 | -0.24432
4973 | R-123 | 81.8 | 14.61 | -0.09 | -0.18324
4974 | R-123 | 81.9 | 14.64 | -0.06 | -0.12216
4975 | R-123 | 82 | 14.67 | -0.03 | -0.06108
4976 | R-123 | 82.1 | 14.7 | 0 | 0
4977 | R-123 | 82.2 | 14.73 | 0.03 | 0.06108
4978 | R-123 | 82.3 | 14.76 | 0.06 | 0.12216
4979 | R-123 | 82.4 | 14.79 | 0.09 | 0.18324
4980 | R-123 | 82.5 | 14.82 | 0.12 | 0.24432
4981 | R-123 | 82.6 | 14.85 | 0.15 | 0.3054
4982 | R-123 | 82.7 | 14.88 | 0.18 | 0.36648
4983 | R-123 | 82.8 | 14.91 | 0.21 | 0.42756
4984 | R-123 | 82.9 | 14.94 | 0.24 | 0.48864
4985 | R-123 | 83 | 14.97 | 0.27 | 0.54972
4986 | R-123 | 83.1 | 15 | 0.3 | 0.6108
4987 | R-123 | 83.2 | 15.03 | 0.33 | 0.67188
4988 | R-123 | 83.3 | 15.06 | 0.36 | 0.73296
4989 | R-123 | 83.4 | 15.09 | 0.39 | 0.79404
4990 | R-123 | 83.5 | 15.12 | 0.42 | 0.85512
4991 | R-123 | 83.6 | 15.15 | 0.45 | 0.9162
4992 | R-123 | 83.7 | 15.18 | 0.48 | 0.97728
4993 | R-123 | 83.8 | 15.21 | 0.51 | 1.0384
4994 | R-123 | 83.9 | 15.24 | 0.54 | 1.0994
4995 | R-123 | 84 | 15.27 | 0.57 | 1.1605
4996 | R-123 | 84.1 | 15.3 | 0.6 | 1.2216
4997 | R-123 | 84.2 | 15.33 | 0.63 | 1.2827
4998 | R-123 | 84.3 | 15.36 | 0.66 | 1.3438
4999 | R-123 | 84.4 | 15.4 | 0.7 | 1.4252
5000 | R-123 | 84.5 | 15.43 | 0.73 | 1.4863
5001 | R-123 | 84.6 | 15.46 | 0.76 | 1.5474
5002 | R-123 | 84.7 | 15.49 | 0.79 | 1.6084
5003 | R-123 | 84.8 | 15.52 | 0.82 | 1.6695
5004 | R-123 | 84.9 | 15.55 | 0.85 | 1.7306
5005 | R-123 | 85 | 15.58 | 0.88 | 1.7917
5006 | R-123 | 85.1 | 15.61 | 0.91 | 1.8528
5007 | R-123 | 85.2 | 15.64 | 0.94 | 1.9138
5008 | R-123 | 85.3 | 15.67 | 0.97 | 1.9749
5009 | R-123 | 85.4 | 15.7 | 1 | 2.036
5010 | R-123 | 85.5 | 15.74 | 1.04 | 2.1174
5011 | R-123 | 85.6 | 15.77 | 1.07 | 2.1785
5012 | R-123 | 85.7 | 15.8 | 1.1 | 2.2396
5013 | R-123 | 85.8 | 15.83 | 1.13 | 2.3007
5014 | R-123 | 85.9 | 15.86 | 1.16 | 2.3618
5015 | R-123 | 86 | 15.89 | 1.19 | 2.4228
5016 | R-123 | 86.1 | 15.92 | 1.22 | 2.4839
5017 | R-123 | 86.2 | 15.96 | 1.26 | 2.5654
5018 | R-123 | 86.3 | 15.99 | 1.29 | 2.6264
5019 | R-123 | 86.4 | 16.02 | 1.32 | 2.6875
5020 | R-123 | 86.5 | 16.05 | 1.35 | 2.7486
5021 | R-123 | 86.6 | 16.08 | 1.38 | 2.8097
5022 | R-123 | 86.7 | 16.11 | 1.41 | 2.8708
5023 | R-123 | 86.8 | 16.15 | 1.45 | 2.9522
5024 | R-123 | 86.9 | 16.18 | 1.48 | 3.0133
5025 | R-123 | 87 | 16.21 | 1.51 | 3.0744
5026 | R-123 | 87.1 | 16.24 | 1.54 | 3.1354
5027 | R-123 | 87.2 | 16.27 | 1.57 | 3.1965
5028 | R-123 | 87.3 | 16.31 | 1.61 | 3.278
5029 | R-123 | 87.4 | 16.34 | 1.64 | 3.339
5030 | R-123 | 87.5 | 16.37 | 1.67 | 3.4001
5031 | R-123 | 87.6 | 16.4 | 1.7 | 3.4612
5032 | R-123 | 87.7 | 16.44 | 1.74 | 3.5426
5033 | R-123 | 87.8 | 16.47 | 1.77 | 3.6037
5034 | R-123 | 87.9 | 16.5 | 1.8 | 3.6648
5035 | R-123 | 88 | 16.53 | 1.83 | 3.7259
5036 | R-123 | 88.1 | 16.57 | 1.87 | 3.8073
5037 | R-123 | 88.2 | 16.6 | 1.9 | 3.8684
5038 | R-123 | 88.3 | 16.63 | 1.93 | 3.9295
5039 | R-123 | 88.4 | 16.66 | 1.96 | 3.9906
5040 | R-123 | 88.5 | 16.7 | 2 | 4.072
5041 | R-123 | 88.6 | 16.73 | 2.03 | 4.1331
5042 | R-123 | 88.7 | 16.76 | 2.06 | 4.1942
5043 | R-123 | 88.8 | 16.79 | 2.09 | 4.2552
5044 | R-123 | 88.9 | 16.83 | 2.13 | 4.3367
5045 | R-123 | 89 | 16.86 | 2.16 | 4.3978
5046 | R-123 | 89.1 | 16.89 | 2.19 | 4.4588
5047 | R-123 | 89.2 | 16.93 | 2.23 | 4.5403
5048 | R-123 | 89.3 | 16.96 | 2.26 | 4.6014
5049 | R-123 | 89.4 | 16.99 | 2.29 | 4.6624
5050 | R-123 | 89.5 | 17.03 | 2.33 | 4.7439
5051 | R-123 | 89.6 | 17.06 | 2.36 | 4.805
5052 | R-123 | 89.7 | 17.09 | 2.39 | 4.866
5053 | R-123 | 89.8 | 17.13 | 2.43 | 4.9475
5054 | R-123 | 89.9 | 17.16 | 2.46 | 5.0086
5055 | R-123 | 90 | 17.19 | 2.49 | 5.0696
5056 | R-123 | 90.1 | 17.23 | 2.53 | 5.1511
5057 | R-123 | 90.2 | 17.26 | 2.56 | 5.2122
5058 | R-123 | 90.3 | 17.29 | 2.59 | 5.2732
5059 | R-123 | 90.4 | 17.33 | 2.63 | 5.3547
5060 | R-123 | 90.5 | 17.36 | 2.66 | 5.4158
5061 | R-123 | 90.6 | 17.39 | 2.69 | 5.4768
5062 | R-123 | 90.7 | 17.43 | 2.73 | 5.5583
5063 | R-123 | 90.8 | 17.46 | 2.76 | 5.6194
5064 | R-123 | 90.9 | 17.5 | 2.8 | 5.7008
5065 | R-123 | 91 | 17.53 | 2.83 | 5.7619
5066 | R-123 | 91.1 | 17.56 | 2.86 | 5.823
5067 | R-123 | 91.2 | 17.6 | 2.9 | 5.9044
5068 | R-123 | 91.3 | 17.63 | 2.93 | 5.9655
5069 | R-123 | 91.4 | 17.67 | 2.97 | 6.0469
5070 | R-123 | 91.5 | 17.7 | 3 | 6.108
5071 | R-123 | 91.6 | 17.73 | 3.03 | 6.1691
5072 | R-123 | 91.7 | 17.77 | 3.07 | 6.2505
5073 | R-123 | 91.8 | 17.8 | 3.1 | 6.3116
5074 | R-123 | 91.9 | 17.84 | 3.14 | 6.393
5075 | R-123 | 92 | 17.87 | 3.17 | 6.4541
5076 | R-123 | 92.1 | 17.91 | 3.21 | 6.5356
5077 | R-123 | 92.2 | 17.94 | 3.24 | 6.5966
5078 | R-123 | 92.3 | 17.98 | 3.28 | 6.6781
5079 | R-123 | 92.4 | 18.01 | 3.31 | 6.7392
5080 | R-123 | 92.5 | 18.05 | 3.35 | 6.8206
5081 | R-123 | 92.6 | 18.08 | 3.38 | 6.8817
5082 | R-123 | 92.7 | 18.12 | 3.42 | 6.9631
5083 | R-123 | 92.8 | 18.15 | 3.45 | 7.0242
5084 | R-123 | 92.9 | 18.18 | 3.48 | 7.0853
5085 | R-123 | 93 | 18.22 | 3.52 | 7.1667
5086 | R-123 | 93.1 | 18.26 | 3.56 | 7.2482
5087 | R-123 | 93.2 | 18.29 | 3.59 | 7.3092
5088 | R-123 | 93.3 | 18.33 | 3.63 | 7.3907
5089 | R-123 | 93.4 | 18.36 | 3.66 | 7.4518
5090 | R-123 | 93.5 | 18.4 | 3.7 | 7.5332
5091 | R-123 | 93.6 | 18.43 | 3.73 | 7.5943
5092 | R-123 | 93.7 | 18.47 | 3.77 | 7.6757
5093 | R-123 | 93.8 | 18.5 | 3.8 | 7.7368
5094 | R-123 | 93.9 | 18.54 | 3.84 | 7.8182
5095 | R-123 | 94 | 18.57 | 3.87 | 7.8793
5096 | R-123 | 94.1 | 18.61 | 3.91 | 7.9608
5097 | R-123 | 94.2 | 18.64 | 3.94 | 8.0218
5098 | R-123 | 94.3 | 18.68 | 3.98 | 8.1033
5099 | R-123 | 94.4 | 18.72 | 4.02 | 8.1847
5100 | R-123 | 94.5 | 18.75 | 4.05 | 8.2458
5101 | R-123 | 94.6 | 18.79 | 4.09 | 8.3272
5102 | R-123 | 94.7 | 18.82 | 4.12 | 8.3883
5103 | R-123 | 94.8 | 18.86 | 4.16 | 8.4698
5104 | R-123 | 94.9 | 18.9 | 4.2 | 8.5512
5105 | R-123 | 95 | 18.93 | 4.23 | 8.6123
5106 | R-123 | 95.1 | 18.97 | 4.27 | 8.6937
5107 | R-123 | 95.2 | 19 | 4.3 | 8.7548
5108 | R-123 | 95.3 | 19.04 | 4.34 | 8.8362
5109 | R-123 | 95.4 | 19.08 | 4.38 | 8.9177
5110 | R-123 | 95.5 | 19.11 | 4.41 | 8.9788
5111 | R-123 | 95.6 | 19.15 | 4.45 | 9.0602
5112 | R-123 | 95.7 | 19.19 | 4.49 | 9.1416
5113 | R-123 | 95.8 | 19.22 | 4.52 | 9.2027
5114 | R-123 | 95.9 | 19.26 | 4.56 | 9.2842
5115 | R-123 | 96 | 19.3 | 4.6 | 9.3656
5116 | R-123 | 96.1 | 19.33 | 4.63 | 9.4267
5117 | R-123 | 96.2 | 19.37 | 4.67 | 9.5081
5118 | R-123 | 96.3 | 19.41 | 4.71 | 9.5896
5119 | R-123 | 96.4 | 19.44 | 4.74 | 9.6506
5120 | R-123 | 96.5 | 19.48 | 4.78 | 9.7321
5121 | R-123 | 96.6 | 19.52 | 4.82 | 9.8135
5122 | R-123 | 96.7 | 19.55 | 4.85 | 9.8746
5123 | R-123 | 96.8 | 19.59 | 4.89 | 9.956
5124 | R-123 | 96.9 | 19.63 | 4.93 | 10.0375
5125 | R-123 | 97 | 19.66 | 4.96 | 10.0986
5126 | R-123 | 97.1 | 19.7 | 5 | 10.18
5127 | R-123 | 97.2 | 19.74 | 5.04 | 10.2614
5128 | R-123 | 97.3 | 19.78 | 5.08 | 10.3429
5129 | R-123 | 97.4 | 19.81 | 5.11 | 10.404
5130 | R-123 | 97.5 | 19.85 | 5.15 | 10.4854
5131 | R-123 | 97.6 | 19.89 | 5.19 | 10.5668
5132 | R-123 | 97.7 | 19.93 | 5.23 | 10.6483
5133 | R-123 | 97.8 | 19.96 | 5.26 | 10.7094
5134 | R-123 | 97.9 | 20 | 5.3 | 10.7908
5135 | R-123 | 98 | 20.04 | 5.34 | 10.8722
5136 | R-123 | 98.1 | 20.08 | 5.38 | 10.9537
5137 | R-123 | 98.2 | 20.11 | 5.41 | 11.0148
5138 | R-123 | 98.3 | 20.15 | 5.45 | 11.0962
5139 | R-123 | 98.4 | 20.19 | 5.49 | 11.1776
5140 | R-123 | 98.5 | 20.23 | 5.53 | 11.2591
5141 | R-123 | 98.6 | 20.27 | 5.57 | 11.3405
5142 | R-123 | 98.7 | 20.3 | 5.6 | 11.4016
5143 | R-123 | 98.8 | 20.34 | 5.64 | 11.483
5144 | R-123 | 98.9 | 20.38 | 5.68 | 11.5645
5145 | R-123 | 99 | 20.42 | 5.72 | 11.6459
5146 | R-123 | 99.1 | 20.46 | 5.76 | 11.7274
5147 | R-123 | 99.2 | 20.5 | 5.8 | 11.8088
5148 | R-123 | 99.3 | 20.53 | 5.83 | 11.8699
5149 | R-123 | 99.4 | 20.57 | 5.87 | 11.9513
5150 | R-123 | 99.5 | 20.61 | 5.91 | 12.0328
5151 | R-123 | 99.6 | 20.65 | 5.95 | 12.1142
5152 | R-123 | 99.7 | 20.69 | 5.99 | 12.1956
5153 | R-123 | 99.8 | 20.73 | 6.03 | 12.2771
5154 | R-123 | 99.9 | 20.77 | 6.07 | 12.3585
5155 | R-123 | 100 | 20.8 | 6.1 | 12.4196
5156 | R-123 | 100.1 | 20.84 | 6.14 | 12.501
5157 | R-123 | 100.2 | 20.88 | 6.18 | 12.5825
5158 | R-123 | 100.3 | 20.92 | 6.22 | 12.6639
5159 | R-123 | 100.4 | 20.96 | 6.26 | 12.7454
5160 | R-123 | 100.5 | 21 | 6.3 | 12.8268
5161 | R-123 | 100.6 | 21.04 | 6.34 | 12.9082
5162 | R-123 | 100.7 | 21.08 | 6.38 | 12.9897
5163 | R-123 | 100.8 | 21.12 | 6.42 | 13.0711
5164 | R-123 | 100.9 | 21.16 | 6.46 | 13.1526
5165 | R-123 | 101 | 21.2 | 6.5 | 13.234
5166 | R-123 | 101.1 | 21.24 | 6.54 | 13.3154
5167 | R-123 | 101.2 | 21.27 | 6.57 | 13.3765
5168 | R-123 | 101.3 | 21.31 | 6.61 | 13.458
5169 | R-123 | 101.4 | 21.35 | 6.65 | 13.5394
5170 | R-123 | 101.5 | 21.39 | 6.69 | 13.6208
5171 | R-123 | 101.6 | 21.43 | 6.73 | 13.7023
5172 | R-123 | 101.7 | 21.47 | 6.77 | 13.7837
5173 | R-123 | 101.8 | 21.51 | 6.81 | 13.8652
5174 | R-123 | 101.9 | 21.55 | 6.85 | 13.9466
5175 | R-123 | 102 | 21.59 | 6.89 | 14.028
5176 | R-123 | 102.1 | 21.63 | 6.93 | 14.1095
5177 | R-123 | 102.2 | 21.67 | 6.97 | 14.1909
5178 | R-123 | 102.3 | 21.71 | 7.01 | 14.2724
5179 | R-123 | 102.4 | 21.75 | 7.05 | 14.3538
5180 | R-123 | 102.5 | 21.79 | 7.09 | 14.4352
5181 | R-123 | 102.6 | 21.83 | 7.13 | 14.5167
5182 | R-123 | 102.7 | 21.87 | 7.17 | 14.5981
5183 | R-123 | 102.8 | 21.91 | 7.21 | 14.6796
5184 | R-123 | 102.9 | 21.96 | 7.26 | 14.7814
5185 | R-123 | 103 | 22 | 7.3 | 14.8628
5186 | R-123 | 103.1 | 22.04 | 7.34 | 14.9442
5187 | R-123 | 103.2 | 22.08 | 7.38 | 15.0257
5188 | R-123 | 103.3 | 22.12 | 7.42 | 15.1071
5189 | R-123 | 103.4 | 22.16 | 7.46 | 15.1886
5190 | R-123 | 103.5 | 22.2 | 7.5 | 15.27
5191 | R-123 | 103.6 | 22.24 | 7.54 | 15.3514
5192 | R-123 | 103.7 | 22.28 | 7.58 | 15.4329
5193 | R-123 | 103.8 | 22.32 | 7.62 | 15.5143
5194 | R-123 | 103.9 | 22.36 | 7.66 | 15.5958
5195 | R-123 | 104 | 22.4 | 7.7 | 15.6772
5196 | R-123 | 104.1 | 22.45 | 7.75 | 15.779
5197 | R-123 | 104.2 | 22.49 | 7.79 | 15.8604
5198 | R-123 | 104.3 | 22.53 | 7.83 | 15.9419
5199 | R-123 | 104.4 | 22.57 | 7.87 | 16.0233
5200 | R-123 | 104.5 | 22.61 | 7.91 | 16.1048
5201 | R-123 | 104.6 | 22.65 | 7.95 | 16.1862
5202 | R-123 | 104.7 | 22.69 | 7.99 | 16.2676
5203 | R-123 | 104.8 | 22.74 | 8.04 | 16.3694
5204 | R-123 | 104.9 | 22.78 | 8.08 | 16.4509
5205 | R-123 | 105 | 22.82 | 8.12 | 16.5323
5206 | R-123 | 105.1 | 22.86 | 8.16 | 16.6138
5207 | R-123 | 105.2 | 22.9 | 8.2 | 16.6952
5208 | R-123 | 105.3 | 22.94 | 8.24 | 16.7766
5209 | R-123 | 105.4 | 22.99 | 8.29 | 16.8784
5210 | R-123 | 105.5 | 23.03 | 8.33 | 16.9599
5211 | R-123 | 105.6 | 23.07 | 8.37 | 17.0413
5212 | R-123 | 105.7 | 23.11 | 8.41 | 17.1228
5213 | R-123 | 105.8 | 23.15 | 8.45 | 17.2042
5214 | R-123 | 105.9 | 23.2 | 8.5 | 17.306
5215 | R-123 | 106 | 23.24 | 8.54 | 17.3874
5216 | R-123 | 106.1 | 23.28 | 8.58 | 17.4689
5217 | R-123 | 106.2 | 23.32 | 8.62 | 17.5503
5218 | R-123 | 106.3 | 23.37 | 8.67 | 17.6521
5219 | R-123 | 106.4 | 23.41 | 8.71 | 17.7336
5220 | R-123 | 106.5 | 23.45 | 8.75 | 17.815
5221 | R-123 | 106.6 | 23.49 | 8.79 | 17.8964
5222 | R-123 | 106.7 | 23.54 | 8.84 | 17.9982
5223 | R-123 | 106.8 | 23.58 | 8.88 | 18.0797
5224 | R-123 | 106.9 | 23.62 | 8.92 | 18.1611
5225 | R-123 | 107 | 23.67 | 8.97 | 18.2629
5226 | R-123 | 107.1 | 23.71 | 9.01 | 18.3444
5227 | R-123 | 107.2 | 23.75 | 9.05 | 18.4258
5228 | R-123 | 107.3 | 23.79 | 9.09 | 18.5072
5229 | R-123 | 107.4 | 23.84 | 9.14 | 18.609
5230 | R-123 | 107.5 | 23.88 | 9.18 | 18.6905
5231 | R-123 | 107.6 | 23.92 | 9.22 | 18.7719
5232 | R-123 | 107.7 | 23.97 | 9.27 | 18.8737
5233 | R-123 | 107.8 | 24.01 | 9.31 | 18.9552
5234 | R-123 | 107.9 | 24.05 | 9.35 | 19.0366
5235 | R-123 | 108 | 24.1 | 9.4 | 19.1384
5236 | R-123 | 108.1 | 24.14 | 9.44 | 19.2198
5237 | R-123 | 108.2 | 24.18 | 9.48 | 19.3013
5238 | R-123 | 108.3 | 24.23 | 9.53 | 19.4031
5239 | R-123 | 108.4 | 24.27 | 9.57 | 19.4845
5240 | R-123 | 108.5 | 24.32 | 9.62 | 19.5863
5241 | R-123 | 108.6 | 24.36 | 9.66 | 19.6678
5242 | R-123 | 108.7 | 24.4 | 9.7 | 19.7492
5243 | R-123 | 108.8 | 24.45 | 9.75 | 19.851
5244 | R-123 | 108.9 | 24.49 | 9.79 | 19.9324
5245 | R-123 | 109 | 24.54 | 9.84 | 20.0342
5246 | R-123 | 109.1 | 24.58 | 9.88 | 20.1157
5247 | R-123 | 109.2 | 24.62 | 9.92 | 20.1971
5248 | R-123 | 109.3 | 24.67 | 9.97 | 20.2989
5249 | R-123 | 109.4 | 24.71 | 10.01 | 20.3804
5250 | R-123 | 109.5 | 24.76 | 10.06 | 20.4822
5251 | R-123 | 109.6 | 24.8 | 10.1 | 20.5636
5252 | R-123 | 109.7 | 24.85 | 10.15 | 20.6654
5253 | R-123 | 109.8 | 24.89 | 10.19 | 20.7468
5254 | R-123 | 109.9 | 24.94 | 10.24 | 20.8486
5255 | R-123 | 110 | 24.98 | 10.28 | 20.9301
5256 | R-123 | 110.1 | 25.03 | 10.33 | 21.0319
5257 | R-123 | 110.2 | 25.07 | 10.37 | 21.1133
5258 | R-123 | 110.3 | 25.12 | 10.42 | 21.2151
5259 | R-123 | 110.4 | 25.16 | 10.46 | 21.2966
5260 | R-123 | 110.5 | 25.21 | 10.51 | 21.3984
5261 | R-123 | 110.6 | 25.25 | 10.55 | 21.4798
5262 | R-123 | 110.7 | 25.3 | 10.6 | 21.5816
5263 | R-123 | 110.8 | 25.34 | 10.64 | 21.663
5264 | R-123 | 110.9 | 25.39 | 10.69 | 21.7648
5265 | R-123 | 111 | 25.43 | 10.73 | 21.8463
5266 | R-123 | 111.1 | 25.48 | 10.78 | 21.9481
5267 | R-123 | 111.2 | 25.52 | 10.82 | 22.0295
5268 | R-123 | 111.3 | 25.57 | 10.87 | 22.1313
5269 | R-123 | 111.4 | 25.61 | 10.91 | 22.2128
5270 | R-123 | 111.5 | 25.66 | 10.96 | 22.3146
5271 | R-123 | 111.6 | 25.7 | 11 | 22.396
5272 | R-123 | 111.7 | 25.75 | 11.05 | 22.4978
5273 | R-123 | 111.8 | 25.8 | 11.1 | 22.5996
5274 | R-123 | 111.9 | 25.84 | 11.14 | 22.681
5275 | R-123 | 112 | 25.89 | 11.19 | 22.7828
5276 | R-123 | 112.1 | 25.93 | 11.23 | 22.8643
5277 | R-123 | 112.2 | 25.98 | 11.28 | 22.9661
5278 | R-123 | 112.3 | 26.03 | 11.33 | 23.0679
5279 | R-123 | 112.4 | 26.07 | 11.37 | 23.1493
5280 | R-123 | 112.5 | 26.12 | 11.42 | 23.2511
5281 | R-123 | 112.6 | 26.17 | 11.47 | 23.3529
5282 | R-123 | 112.7 | 26.21 | 11.51 | 23.4344
5283 | R-123 | 112.8 | 26.26 | 11.56 | 23.5362
5284 | R-123 | 112.9 | 26.3 | 11.6 | 23.6176
5285 | R-123 | 113 | 26.35 | 11.65 | 23.7194
5286 | R-123 | 113.1 | 26.4 | 11.7 | 23.8212
5287 | R-123 | 113.2 | 26.44 | 11.74 | 23.9026
5288 | R-123 | 113.3 | 26.49 | 11.79 | 24.0044
5289 | R-123 | 113.4 | 26.54 | 11.84 | 24.1062
5290 | R-123 | 113.5 | 26.59 | 11.89 | 24.208
5291 | R-123 | 113.6 | 26.63 | 11.93 | 24.2895
5292 | R-123 | 113.7 | 26.68 | 11.98 | 24.3913
5293 | R-123 | 113.8 | 26.73 | 12.03 | 24.4931
5294 | R-123 | 113.9 | 26.77 | 12.07 | 24.5745
5295 | R-123 | 114 | 26.82 | 12.12 | 24.6763
5296 | R-123 | 114.1 | 26.87 | 12.17 | 24.7781
5297 | R-123 | 114.2 | 26.92 | 12.22 | 24.8799
5298 | R-123 | 114.3 | 26.96 | 12.26 | 24.9614
5299 | R-123 | 114.4 | 27.01 | 12.31 | 25.0632
5300 | R-123 | 114.5 | 27.06 | 12.36 | 25.165
5301 | R-123 | 114.6 | 27.11 | 12.41 | 25.2668
5302 | R-123 | 114.7 | 27.15 | 12.45 | 25.3482
5303 | R-123 | 114.8 | 27.2 | 12.5 | 25.45
5304 | R-123 | 114.9 | 27.25 | 12.55 | 25.5518
5305 | R-123 | 115 | 27.3 | 12.6 | 25.6536
5306 | R-123 | 115.1 | 27.35 | 12.65 | 25.7554
5307 | R-123 | 115.2 | 27.39 | 12.69 | 25.8368
5308 | R-123 | 115.3 | 27.44 | 12.74 | 25.9386
5309 | R-123 | 115.4 | 27.49 | 12.79 | 26.0404
5310 | R-123 | 115.5 | 27.54 | 12.84 | 26.1422
5311 | R-123 | 115.6 | 27.59 | 12.89 | 26.244
5312 | R-123 | 115.7 | 27.63 | 12.93 | 26.3255
5313 | R-123 | 115.8 | 27.68 | 12.98 | 26.4273
5314 | R-123 | 115.9 | 27.73 | 13.03 | 26.5291
5315 | R-123 | 116 | 27.78 | 13.08 | 26.6309
5316 | R-123 | 116.1 | 27.83 | 13.13 | 26.7327
5317 | R-123 | 116.2 | 27.88 | 13.18 | 26.8345
5318 | R-123 | 116.3 | 27.93 | 13.23 | 26.9363
5319 | R-123 | 116.4 | 27.97 | 13.27 | 27.0177
5320 | R-123 | 116.5 | 28.02 | 13.32 | 27.1195
5321 | R-123 | 116.6 | 28.07 | 13.37 | 27.2213
5322 | R-123 | 116.7 | 28.12 | 13.42 | 27.3231
5323 | R-123 | 116.8 | 28.17 | 13.47 | 27.4249
5324 | R-123 | 116.9 | 28.22 | 13.52 | 27.5267
5325 | R-123 | 117 | 28.27 | 13.57 | 27.6285
5326 | R-123 | 117.1 | 28.32 | 13.62 | 27.7303
5327 | R-123 | 117.2 | 28.37 | 13.67 | 27.8321
5328 | R-123 | 117.3 | 28.42 | 13.72 | 27.9339
5329 | R-123 | 117.4 | 28.47 | 13.77 | 28.0357
5330 | R-123 | 117.5 | 28.52 | 13.82 | 28.1375
5331 | R-123 | 117.6 | 28.57 | 13.87 | 28.2393
5332 | R-123 | 117.7 | 28.62 | 13.92 | 28.3411
5333 | R-123 | 117.8 | 28.67 | 13.97 | 28.4429
5334 | R-123 | 117.9 | 28.71 | 14.01 | 28.5244
5335 | R-123 | 118 | 28.76 | 14.06 | 28.6262
5336 | R-123 | 118.1 | 28.81 | 14.11 | 28.728
5337 | R-123 | 118.2 | 28.86 | 14.16 | 28.8298
5338 | R-123 | 118.3 | 28.91 | 14.21 | 28.9316
5339 | R-123 | 118.4 | 28.97 | 14.27 | 29.0537
5340 | R-123 | 118.5 | 29.02 | 14.32 | 29.1555
5341 | R-123 | 118.6 | 29.07 | 14.37 | 29.2573
5342 | R-123 | 118.7 | 29.12 | 14.42 | 29.3591
5343 | R-123 | 118.8 | 29.17 | 14.47 | 29.4609
5344 | R-123 | 118.9 | 29.22 | 14.52 | 29.5627
5345 | R-123 | 119 | 29.27 | 14.57 | 29.6645
5346 | R-123 | 119.1 | 29.32 | 14.62 | 29.7663
5347 | R-123 | 119.2 | 29.37 | 14.67 | 29.8681
5348 | R-123 | 119.3 | 29.42 | 14.72 | 29.9699
5349 | R-123 | 119.4 | 29.47 | 14.77 | 30.0717
5350 | R-123 | 119.5 | 29.52 | 14.82 | 30.1735
5351 | R-123 | 119.6 | 29.57 | 14.87 | 30.2753
5352 | R-123 | 119.7 | 29.62 | 14.92 | 30.3771
5353 | R-123 | 119.8 | 29.67 | 14.97 | 30.4789
5354 | R-123 | 119.9 | 29.73 | 15.03 | 30.6011
5355 | R-123 | 120 | 29.78 | 15.08 | 30.7029
5356 | R-22 | 10 | 47.54 | 32.84 | 66.8622
5357 | R-22 | 10.1 | 47.63 | 32.93 | 67.0455
5358 | R-22 | 10.2 | 47.73 | 33.03 | 67.2491
5359 | R-22 | 10.3 | 47.82 | 33.12 | 67.4323
5360 | R-22 | 10.4 | 47.92 | 33.22 | 67.6359
5361 | R-22 | 10.5 | 48.01 | 33.31 | 67.8192
5362 | R-22 | 10.6 | 48.11 | 33.41 | 68.0228
5363 | R-22 | 10.7 | 48.21 | 33.51 | 68.2264
5364 | R-22 | 10.8 | 48.3 | 33.6 | 68.4096
5365 | R-22 | 10.9 | 48.4 | 33.7 | 68.6132
5366 | R-22 | 11 | 48.49 | 33.79 | 68.7964
5367 | R-22 | 11.1 | 48.59 | 33.89 | 69
5368 | R-22 | 11.2 | 48.69 | 33.99 | 69.2036
5369 | R-22 | 11.3 | 48.78 | 34.08 | 69.3869
5370 | R-22 | 11.4 | 48.88 | 34.18 | 69.5905
5371 | R-22 | 11.5 | 48.98 | 34.28 | 69.7941
5372 | R-22 | 11.6 | 49.08 | 34.38 | 69.9977
5373 | R-22 | 11.7 | 49.17 | 34.47 | 70.1809
5374 | R-22 | 11.8 | 49.27 | 34.57 | 70.3845
5375 | R-22 | 11.9 | 49.37 | 34.67 | 70.5881
5376 | R-22 | 12 | 49.47 | 34.77 | 70.7917
5377 | R-22 | 12.1 | 49.57 | 34.87 | 70.9953
5378 | R-22 | 12.2 | 49.66 | 34.96 | 71.1786
5379 | R-22 | 12.3 | 49.76 | 35.06 | 71.3822
5380 | R-22 | 12.4 | 49.86 | 35.16 | 71.5858
5381 | R-22 | 12.5 | 49.96 | 35.26 | 71.7894
5382 | R-22 | 12.6 | 50.06 | 35.36 | 71.993
5383 | R-22 | 12.7 | 50.16 | 35.46 | 72.1966
5384 | R-22 | 12.8 | 50.26 | 35.56 | 72.4002
5385 | R-22 | 12.9 | 50.36 | 35.66 | 72.6038
5386 | R-22 | 13 | 50.45 | 35.75 | 72.787
5387 | R-22 | 13.1 | 50.55 | 35.85 | 72.9906
5388 | R-22 | 13.2 | 50.65 | 35.95 | 73.1942
5389 | R-22 | 13.3 | 50.75 | 36.05 | 73.3978
5390 | R-22 | 13.4 | 50.85 | 36.15 | 73.6014
5391 | R-22 | 13.5 | 50.95 | 36.25 | 73.805
5392 | R-22 | 13.6 | 51.05 | 36.35 | 74.0086
5393 | R-22 | 13.7 | 51.16 | 36.46 | 74.2326
5394 | R-22 | 13.8 | 51.26 | 36.56 | 74.4362
5395 | R-22 | 13.9 | 51.36 | 36.66 | 74.6398
5396 | R-22 | 14 | 51.46 | 36.76 | 74.8434
5397 | R-22 | 14.1 | 51.56 | 36.86 | 75.047
5398 | R-22 | 14.2 | 51.66 | 36.96 | 75.2506
5399 | R-22 | 14.3 | 51.76 | 37.06 | 75.4542
5400 | R-22 | 14.4 | 51.86 | 37.16 | 75.6578
5401 | R-22 | 14.5 | 51.96 | 37.26 | 75.8614
5402 | R-22 | 14.6 | 52.07 | 37.37 | 76.0853
5403 | R-22 | 14.7 | 52.17 | 37.47 | 76.2889
5404 | R-22 | 14.8 | 52.27 | 37.57 | 76.4925
5405 | R-22 | 14.9 | 52.37 | 37.67 | 76.6961
5406 | R-22 | 15 | 52.48 | 37.78 | 76.9201
5407 | R-22 | 15.1 | 52.58 | 37.88 | 77.1237
5408 | R-22 | 15.2 | 52.68 | 37.98 | 77.3273
5409 | R-22 | 15.3 | 52.78 | 38.08 | 77.5309
5410 | R-22 | 15.4 | 52.89 | 38.19 | 77.7548
5411 | R-22 | 15.5 | 52.99 | 38.29 | 77.9584
5412 | R-22 | 15.6 | 53.09 | 38.39 | 78.162
5413 | R-22 | 15.7 | 53.2 | 38.5 | 78.386
5414 | R-22 | 15.8 | 53.3 | 38.6 | 78.5896
5415 | R-22 | 15.9 | 53.4 | 38.7 | 78.7932
5416 | R-22 | 16 | 53.51 | 38.81 | 79.0172
5417 | R-22 | 16.1 | 53.61 | 38.91 | 79.2208
5418 | R-22 | 16.2 | 53.72 | 39.02 | 79.4447
5419 | R-22 | 16.3 | 53.82 | 39.12 | 79.6483
5420 | R-22 | 16.4 | 53.93 | 39.23 | 79.8723
5421 | R-22 | 16.5 | 54.03 | 39.33 | 80.0759
5422 | R-22 | 16.6 | 54.14 | 39.44 | 80.2998
5423 | R-22 | 16.7 | 54.24 | 39.54 | 80.5034
5424 | R-22 | 16.8 | 54.35 | 39.65 | 80.7274
5425 | R-22 | 16.9 | 54.45 | 39.75 | 80.931
5426 | R-22 | 17 | 54.56 | 39.86 | 81.155
5427 | R-22 | 17.1 | 54.66 | 39.96 | 81.3586
5428 | R-22 | 17.2 | 54.77 | 40.07 | 81.5825
5429 | R-22 | 17.3 | 54.87 | 40.17 | 81.7861
5430 | R-22 | 17.4 | 54.98 | 40.28 | 82.0101
5431 | R-22 | 17.5 | 55.09 | 40.39 | 82.234
5432 | R-22 | 17.6 | 55.19 | 40.49 | 82.4376
5433 | R-22 | 17.7 | 55.3 | 40.6 | 82.6616
5434 | R-22 | 17.8 | 55.41 | 40.71 | 82.8856
5435 | R-22 | 17.9 | 55.51 | 40.81 | 83.0892
5436 | R-22 | 18 | 55.62 | 40.92 | 83.3131
5437 | R-22 | 18.1 | 55.73 | 41.03 | 83.5371
5438 | R-22 | 18.2 | 55.83 | 41.13 | 83.7407
5439 | R-22 | 18.3 | 55.94 | 41.24 | 83.9646
5440 | R-22 | 18.4 | 56.05 | 41.35 | 84.1886
5441 | R-22 | 18.5 | 56.16 | 41.46 | 84.4126
5442 | R-22 | 18.6 | 56.27 | 41.57 | 84.6365
5443 | R-22 | 18.7 | 56.37 | 41.67 | 84.8401
5444 | R-22 | 18.8 | 56.48 | 41.78 | 85.0641
5445 | R-22 | 18.9 | 56.59 | 41.89 | 85.288
5446 | R-22 | 19 | 56.7 | 42 | 85.512
5447 | R-22 | 19.1 | 56.81 | 42.11 | 85.736
5448 | R-22 | 19.2 | 56.92 | 42.22 | 85.9599
5449 | R-22 | 19.3 | 57.03 | 42.33 | 86.1839
5450 | R-22 | 19.4 | 57.14 | 42.44 | 86.4078
5451 | R-22 | 19.5 | 57.25 | 42.55 | 86.6318
5452 | R-22 | 19.6 | 57.35 | 42.65 | 86.8354
5453 | R-22 | 19.7 | 57.46 | 42.76 | 87.0594
5454 | R-22 | 19.8 | 57.57 | 42.87 | 87.2833
5455 | R-22 | 19.9 | 57.68 | 42.98 | 87.5073
5456 | R-22 | 20 | 57.79 | 43.09 | 87.7312
5457 | R-22 | 20.1 | 57.91 | 43.21 | 87.9756
5458 | R-22 | 20.2 | 58.02 | 43.32 | 88.1995
5459 | R-22 | 20.3 | 58.13 | 43.43 | 88.4235
5460 | R-22 | 20.4 | 58.24 | 43.54 | 88.6474
5461 | R-22 | 20.5 | 58.35 | 43.65 | 88.8714
5462 | R-22 | 20.6 | 58.46 | 43.76 | 89.0954
5463 | R-22 | 20.7 | 58.57 | 43.87 | 89.3193
5464 | R-22 | 20.8 | 58.68 | 43.98 | 89.5433
5465 | R-22 | 20.9 | 58.79 | 44.09 | 89.7672
5466 | R-22 | 21 | 58.91 | 44.21 | 90.0116
5467 | R-22 | 21.1 | 59.02 | 44.32 | 90.2355
5468 | R-22 | 21.2 | 59.13 | 44.43 | 90.4595
5469 | R-22 | 21.3 | 59.24 | 44.54 | 90.6834
5470 | R-22 | 21.4 | 59.36 | 44.66 | 90.9278
5471 | R-22 | 21.5 | 59.47 | 44.77 | 91.1517
5472 | R-22 | 21.6 | 59.58 | 44.88 | 91.3757
5473 | R-22 | 21.7 | 59.69 | 44.99 | 91.5996
5474 | R-22 | 21.8 | 59.81 | 45.11 | 91.844
5475 | R-22 | 21.9 | 59.92 | 45.22 | 92.0679
5476 | R-22 | 22 | 60.03 | 45.33 | 92.2919
5477 | R-22 | 22.1 | 60.15 | 45.45 | 92.5362
5478 | R-22 | 22.2 | 60.26 | 45.56 | 92.7602
5479 | R-22 | 22.3 | 60.37 | 45.67 | 92.9841
5480 | R-22 | 22.4 | 60.49 | 45.79 | 93.2284
5481 | R-22 | 22.5 | 60.6 | 45.9 | 93.4524
5482 | R-22 | 22.6 | 60.72 | 46.02 | 93.6967
5483 | R-22 | 22.7 | 60.83 | 46.13 | 93.9207
5484 | R-22 | 22.8 | 60.95 | 46.25 | 94.165
5485 | R-22 | 22.9 | 61.06 | 46.36 | 94.389
5486 | R-22 | 23 | 61.18 | 46.48 | 94.6333
5487 | R-22 | 23.1 | 61.29 | 46.59 | 94.8572
5488 | R-22 | 23.2 | 61.41 | 46.71 | 95.1016
5489 | R-22 | 23.3 | 61.52 | 46.82 | 95.3255
5490 | R-22 | 23.4 | 61.64 | 46.94 | 95.5698
5491 | R-22 | 23.5 | 61.76 | 47.06 | 95.8142
5492 | R-22 | 23.6 | 61.87 | 47.17 | 96.0381
5493 | R-22 | 23.7 | 61.99 | 47.29 | 96.2824
5494 | R-22 | 23.8 | 62.1 | 47.4 | 96.5064
5495 | R-22 | 23.9 | 62.22 | 47.52 | 96.7507
5496 | R-22 | 24 | 62.34 | 47.64 | 96.995
5497 | R-22 | 24.1 | 62.45 | 47.75 | 97.219
5498 | R-22 | 24.2 | 62.57 | 47.87 | 97.4633
5499 | R-22 | 24.3 | 62.69 | 47.99 | 97.7076
5500 | R-22 | 24.4 | 62.81 | 48.11 | 97.952
5501 | R-22 | 24.5 | 62.92 | 48.22 | 98.1759
5502 | R-22 | 24.6 | 63.04 | 48.34 | 98.4202
5503 | R-22 | 24.7 | 63.16 | 48.46 | 98.6646
5504 | R-22 | 24.8 | 63.28 | 48.58 | 98.9089
5505 | R-22 | 24.9 | 63.4 | 48.7 | 99.1532
5506 | R-22 | 25 | 63.51 | 48.81 | 99.3772
5507 | R-22 | 25.1 | 63.63 | 48.93 | 99.6215
5508 | R-22 | 25.2 | 63.75 | 49.05 | 99.8658
5509 | R-22 | 25.3 | 63.87 | 49.17 | 100.1101
5510 | R-22 | 25.4 | 63.99 | 49.29 | 100.3544
5511 | R-22 | 25.5 | 64.11 | 49.41 | 100.5988
5512 | R-22 | 25.6 | 64.23 | 49.53 | 100.8431
5513 | R-22 | 25.7 | 64.35 | 49.65 | 101.0874
5514 | R-22 | 25.8 | 64.47 | 49.77 | 101.3317
5515 | R-22 | 25.9 | 64.59 | 49.89 | 101.576
5516 | R-22 | 26 | 64.71 | 50.01 | 101.8204
5517 | R-22 | 26.1 | 64.83 | 50.13 | 102.0647
5518 | R-22 | 26.2 | 64.95 | 50.25 | 102.309
5519 | R-22 | 26.3 | 65.07 | 50.37 | 102.5533
5520 | R-22 | 26.4 | 65.19 | 50.49 | 102.7976
5521 | R-22 | 26.5 | 65.31 | 50.61 | 103.042
5522 | R-22 | 26.6 | 65.43 | 50.73 | 103.2863
5523 | R-22 | 26.7 | 65.55 | 50.85 | 103.5306
5524 | R-22 | 26.8 | 65.67 | 50.97 | 103.7749
5525 | R-22 | 26.9 | 65.8 | 51.1 | 104.0396
5526 | R-22 | 27 | 65.92 | 51.22 | 104.2839
5527 | R-22 | 27.1 | 66.04 | 51.34 | 104.5282
5528 | R-22 | 27.2 | 66.16 | 51.46 | 104.7726
5529 | R-22 | 27.3 | 66.28 | 51.58 | 105.0169
5530 | R-22 | 27.4 | 66.41 | 51.71 | 105.2816
5531 | R-22 | 27.5 | 66.53 | 51.83 | 105.5259
5532 | R-22 | 27.6 | 66.65 | 51.95 | 105.7702
5533 | R-22 | 27.7 | 66.77 | 52.07 | 106.0145
5534 | R-22 | 27.8 | 66.9 | 52.2 | 106.2792
5535 | R-22 | 27.9 | 67.02 | 52.32 | 106.5235
5536 | R-22 | 28 | 67.14 | 52.44 | 106.7678
5537 | R-22 | 28.1 | 67.27 | 52.57 | 107.0325
5538 | R-22 | 28.2 | 67.39 | 52.69 | 107.2768
5539 | R-22 | 28.3 | 67.52 | 52.82 | 107.5415
5540 | R-22 | 28.4 | 67.64 | 52.94 | 107.7858
5541 | R-22 | 28.5 | 67.76 | 53.06 | 108.0302
5542 | R-22 | 28.6 | 67.89 | 53.19 | 108.2948
5543 | R-22 | 28.7 | 68.01 | 53.31 | 108.5392
5544 | R-22 | 28.8 | 68.14 | 53.44 | 108.8038
5545 | R-22 | 28.9 | 68.26 | 53.56 | 109.0482
5546 | R-22 | 29 | 68.39 | 53.69 | 109.3128
5547 | R-22 | 29.1 | 68.51 | 53.81 | 109.5572
5548 | R-22 | 29.2 | 68.64 | 53.94 | 109.8218
5549 | R-22 | 29.3 | 68.77 | 54.07 | 110.0865
5550 | R-22 | 29.4 | 68.89 | 54.19 | 110.3308
5551 | R-22 | 29.5 | 69.02 | 54.32 | 110.5955
5552 | R-22 | 29.6 | 69.14 | 54.44 | 110.8398
5553 | R-22 | 29.7 | 69.27 | 54.57 | 111.1045
5554 | R-22 | 29.8 | 69.4 | 54.7 | 111.3692
5555 | R-22 | 29.9 | 69.52 | 54.82 | 111.6135
5556 | R-22 | 30 | 69.65 | 54.95 | 111.8782
5557 | R-22 | 30.1 | 69.78 | 55.08 | 112.1429
5558 | R-22 | 30.2 | 69.91 | 55.21 | 112.4076
5559 | R-22 | 30.3 | 70.03 | 55.33 | 112.6519
5560 | R-22 | 30.4 | 70.16 | 55.46 | 112.9166
5561 | R-22 | 30.5 | 70.29 | 55.59 | 113.1812
5562 | R-22 | 30.6 | 70.42 | 55.72 | 113.4459
5563 | R-22 | 30.7 | 70.54 | 55.84 | 113.6902
5564 | R-22 | 30.8 | 70.67 | 55.97 | 113.9549
5565 | R-22 | 30.9 | 70.8 | 56.1 | 114.2196
5566 | R-22 | 31 | 70.93 | 56.23 | 114.4843
5567 | R-22 | 31.1 | 71.06 | 56.36 | 114.749
5568 | R-22 | 31.2 | 71.19 | 56.49 | 115.0136
5569 | R-22 | 31.3 | 71.32 | 56.62 | 115.2783
5570 | R-22 | 31.4 | 71.45 | 56.75 | 115.543
5571 | R-22 | 31.5 | 71.58 | 56.88 | 115.8077
5572 | R-22 | 31.6 | 71.71 | 57.01 | 116.0724
5573 | R-22 | 31.7 | 71.84 | 57.14 | 116.337
5574 | R-22 | 31.8 | 71.97 | 57.27 | 116.6017
5575 | R-22 | 31.9 | 72.1 | 57.4 | 116.8664
5576 | R-22 | 32 | 72.23 | 57.53 | 117.1311
5577 | R-22 | 32.1 | 72.36 | 57.66 | 117.3958
5578 | R-22 | 32.2 | 72.49 | 57.79 | 117.6604
5579 | R-22 | 32.3 | 72.62 | 57.92 | 117.9251
5580 | R-22 | 32.4 | 72.75 | 58.05 | 118.1898
5581 | R-22 | 32.5 | 72.88 | 58.18 | 118.4545
5582 | R-22 | 32.6 | 73.01 | 58.31 | 118.7192
5583 | R-22 | 32.7 | 73.15 | 58.45 | 119.0042
5584 | R-22 | 32.8 | 73.28 | 58.58 | 119.2689
5585 | R-22 | 32.9 | 73.41 | 58.71 | 119.5336
5586 | R-22 | 33 | 73.54 | 58.84 | 119.7982
5587 | R-22 | 33.1 | 73.67 | 58.97 | 120.0629
5588 | R-22 | 33.2 | 73.81 | 59.11 | 120.348
5589 | R-22 | 33.3 | 73.94 | 59.24 | 120.6126
5590 | R-22 | 33.4 | 74.07 | 59.37 | 120.8773
5591 | R-22 | 33.5 | 74.21 | 59.51 | 121.1624
5592 | R-22 | 33.6 | 74.34 | 59.64 | 121.427
5593 | R-22 | 33.7 | 74.47 | 59.77 | 121.6917
5594 | R-22 | 33.8 | 74.61 | 59.91 | 121.9768
5595 | R-22 | 33.9 | 74.74 | 60.04 | 122.2414
5596 | R-22 | 34 | 74.87 | 60.17 | 122.5061
5597 | R-22 | 34.1 | 75.01 | 60.31 | 122.7912
5598 | R-22 | 34.2 | 75.14 | 60.44 | 123.0558
5599 | R-22 | 34.3 | 75.28 | 60.58 | 123.3409
5600 | R-22 | 34.4 | 75.41 | 60.71 | 123.6056
5601 | R-22 | 34.5 | 75.55 | 60.85 | 123.8906
5602 | R-22 | 34.6 | 75.68 | 60.98 | 124.1553
5603 | R-22 | 34.7 | 75.82 | 61.12 | 124.4403
5604 | R-22 | 34.8 | 75.95 | 61.25 | 124.705
5605 | R-22 | 34.9 | 76.09 | 61.39 | 124.99
5606 | R-22 | 35 | 76.22 | 61.52 | 125.2547
5607 | R-22 | 35.1 | 76.36 | 61.66 | 125.5398
5608 | R-22 | 35.2 | 76.5 | 61.8 | 125.8248
5609 | R-22 | 35.3 | 76.63 | 61.93 | 126.0895
5610 | R-22 | 35.4 | 76.77 | 62.07 | 126.3745
5611 | R-22 | 35.5 | 76.91 | 62.21 | 126.6596
5612 | R-22 | 35.6 | 77.04 | 62.34 | 126.9242
5613 | R-22 | 35.7 | 77.18 | 62.48 | 127.2093
5614 | R-22 | 35.8 | 77.32 | 62.62 | 127.4943
5615 | R-22 | 35.9 | 77.46 | 62.76 | 127.7794
5616 | R-22 | 36 | 77.59 | 62.89 | 128.044
5617 | R-22 | 36.1 | 77.73 | 63.03 | 128.3291
5618 | R-22 | 36.2 | 77.87 | 63.17 | 128.6141
5619 | R-22 | 36.3 | 78.01 | 63.31 | 128.8992
5620 | R-22 | 36.4 | 78.15 | 63.45 | 129.1842
5621 | R-22 | 36.5 | 78.29 | 63.59 | 129.4692
5622 | R-22 | 36.6 | 78.42 | 63.72 | 129.7339
5623 | R-22 | 36.7 | 78.56 | 63.86 | 130.019
5624 | R-22 | 36.8 | 78.7 | 64 | 130.304
5625 | R-22 | 36.9 | 78.84 | 64.14 | 130.589
5626 | R-22 | 37 | 78.98 | 64.28 | 130.8741
5627 | R-22 | 37.1 | 79.12 | 64.42 | 131.1591
5628 | R-22 | 37.2 | 79.26 | 64.56 | 131.4442
5629 | R-22 | 37.3 | 79.4 | 64.7 | 131.7292
5630 | R-22 | 37.4 | 79.54 | 64.84 | 132.0142
5631 | R-22 | 37.5 | 79.68 | 64.98 | 132.2993
5632 | R-22 | 37.6 | 79.82 | 65.12 | 132.5843
5633 | R-22 | 37.7 | 79.96 | 65.26 | 132.8694
5634 | R-22 | 37.8 | 80.1 | 65.4 | 133.1544
5635 | R-22 | 37.9 | 80.25 | 65.55 | 133.4598
5636 | R-22 | 38 | 80.39 | 65.69 | 133.7448
5637 | R-22 | 38.1 | 80.53 | 65.83 | 134.0299
5638 | R-22 | 38.2 | 80.67 | 65.97 | 134.3149
5639 | R-22 | 38.3 | 80.81 | 66.11 | 134.6
5640 | R-22 | 38.4 | 80.95 | 66.25 | 134.885
5641 | R-22 | 38.5 | 81.1 | 66.4 | 135.1904
5642 | R-22 | 38.6 | 81.24 | 66.54 | 135.4754
5643 | R-22 | 38.7 | 81.38 | 66.68 | 135.7605
5644 | R-22 | 38.8 | 81.53 | 66.83 | 136.0659
5645 | R-22 | 38.9 | 81.67 | 66.97 | 136.3509
5646 | R-22 | 39 | 81.81 | 67.11 | 136.636
5647 | R-22 | 39.1 | 81.96 | 67.26 | 136.9414
5648 | R-22 | 39.2 | 82.1 | 67.4 | 137.2264
5649 | R-22 | 39.3 | 82.24 | 67.54 | 137.5114
5650 | R-22 | 39.4 | 82.39 | 67.69 | 137.8168
5651 | R-22 | 39.5 | 82.53 | 67.83 | 138.1019
5652 | R-22 | 39.6 | 82.68 | 67.98 | 138.4073
5653 | R-22 | 39.7 | 82.82 | 68.12 | 138.6923
5654 | R-22 | 39.8 | 82.97 | 68.27 | 138.9977
5655 | R-22 | 39.9 | 83.11 | 68.41 | 139.2828
5656 | R-22 | 40 | 83.26 | 68.56 | 139.5882
5657 | R-22 | 40.1 | 83.4 | 68.7 | 139.8732
5658 | R-22 | 40.2 | 83.55 | 68.85 | 140.1786
5659 | R-22 | 40.3 | 83.69 | 68.99 | 140.4636
5660 | R-22 | 40.4 | 83.84 | 69.14 | 140.769
5661 | R-22 | 40.5 | 83.98 | 69.28 | 141.0541
5662 | R-22 | 40.6 | 84.13 | 69.43 | 141.3595
5663 | R-22 | 40.7 | 84.28 | 69.58 | 141.6649
5664 | R-22 | 40.8 | 84.42 | 69.72 | 141.9499
5665 | R-22 | 40.9 | 84.57 | 69.87 | 142.2553
5666 | R-22 | 41 | 84.72 | 70.02 | 142.5607
5667 | R-22 | 41.1 | 84.87 | 70.17 | 142.8661
5668 | R-22 | 41.2 | 85.01 | 70.31 | 143.1512
5669 | R-22 | 41.3 | 85.16 | 70.46 | 143.4566
5670 | R-22 | 41.4 | 85.31 | 70.61 | 143.762
5671 | R-22 | 41.5 | 85.46 | 70.76 | 144.0674
5672 | R-22 | 41.6 | 85.6 | 70.9 | 144.3524
5673 | R-22 | 41.7 | 85.75 | 71.05 | 144.6578
5674 | R-22 | 41.8 | 85.9 | 71.2 | 144.9632
5675 | R-22 | 41.9 | 86.05 | 71.35 | 145.2686
5676 | R-22 | 42 | 86.2 | 71.5 | 145.574
5677 | R-22 | 42.1 | 86.35 | 71.65 | 145.8794
5678 | R-22 | 42.2 | 86.5 | 71.8 | 146.1848
5679 | R-22 | 42.3 | 86.65 | 71.95 | 146.4902
5680 | R-22 | 42.4 | 86.8 | 72.1 | 146.7956
5681 | R-22 | 42.5 | 86.95 | 72.25 | 147.101
5682 | R-22 | 42.6 | 87.1 | 72.4 | 147.4064
5683 | R-22 | 42.7 | 87.25 | 72.55 | 147.7118
5684 | R-22 | 42.8 | 87.4 | 72.7 | 148.0172
5685 | R-22 | 42.9 | 87.55 | 72.85 | 148.3226
5686 | R-22 | 43 | 87.7 | 73 | 148.628
5687 | R-22 | 43.1 | 87.85 | 73.15 | 148.9334
5688 | R-22 | 43.2 | 88 | 73.3 | 149.2388
5689 | R-22 | 43.3 | 88.15 | 73.45 | 149.5442
5690 | R-22 | 43.4 | 88.31 | 73.61 | 149.87
5691 | R-22 | 43.5 | 88.46 | 73.76 | 150.1754
5692 | R-22 | 43.6 | 88.61 | 73.91 | 150.4808
5693 | R-22 | 43.7 | 88.76 | 74.06 | 150.7862
5694 | R-22 | 43.8 | 88.92 | 74.22 | 151.1119
5695 | R-22 | 43.9 | 89.07 | 74.37 | 151.4173
5696 | R-22 | 44 | 89.22 | 74.52 | 151.7227
5697 | R-22 | 44.1 | 89.37 | 74.67 | 152.0281
5698 | R-22 | 44.2 | 89.53 | 74.83 | 152.3539
5699 | R-22 | 44.3 | 89.68 | 74.98 | 152.6593
5700 | R-22 | 44.4 | 89.83 | 75.13 | 152.9647
5701 | R-22 | 44.5 | 89.99 | 75.29 | 153.2904
5702 | R-22 | 44.6 | 90.14 | 75.44 | 153.5958
5703 | R-22 | 44.7 | 90.3 | 75.6 | 153.9216
5704 | R-22 | 44.8 | 90.45 | 75.75 | 154.227
5705 | R-22 | 44.9 | 90.61 | 75.91 | 154.5528
5706 | R-22 | 45 | 90.76 | 76.06 | 154.8582
5707 | R-22 | 45.1 | 90.92 | 76.22 | 155.1839
5708 | R-22 | 45.2 | 91.07 | 76.37 | 155.4893
5709 | R-22 | 45.3 | 91.23 | 76.53 | 155.8151
5710 | R-22 | 45.4 | 91.38 | 76.68 | 156.1205
5711 | R-22 | 45.5 | 91.54 | 76.84 | 156.4462
5712 | R-22 | 45.6 | 91.7 | 77 | 156.772
5713 | R-22 | 45.7 | 91.85 | 77.15 | 157.0774
5714 | R-22 | 45.8 | 92.01 | 77.31 | 157.4032
5715 | R-22 | 45.9 | 92.16 | 77.46 | 157.7086
5716 | R-22 | 46 | 92.32 | 77.62 | 158.0343
5717 | R-22 | 46.1 | 92.48 | 77.78 | 158.3601
5718 | R-22 | 46.2 | 92.64 | 77.94 | 158.6858
5719 | R-22 | 46.3 | 92.79 | 78.09 | 158.9912
5720 | R-22 | 46.4 | 92.95 | 78.25 | 159.317
5721 | R-22 | 46.5 | 93.11 | 78.41 | 159.6428
5722 | R-22 | 46.6 | 93.27 | 78.57 | 159.9685
5723 | R-22 | 46.7 | 93.43 | 78.73 | 160.2943
5724 | R-22 | 46.8 | 93.58 | 78.88 | 160.5997
5725 | R-22 | 46.9 | 93.74 | 79.04 | 160.9254
5726 | R-22 | 47 | 93.9 | 79.2 | 161.2512
5727 | R-22 | 47.1 | 94.06 | 79.36 | 161.577
5728 | R-22 | 47.2 | 94.22 | 79.52 | 161.9027
5729 | R-22 | 47.3 | 94.38 | 79.68 | 162.2285
5730 | R-22 | 47.4 | 94.54 | 79.84 | 162.5542
5731 | R-22 | 47.5 | 94.7 | 80 | 162.88
5732 | R-22 | 47.6 | 94.86 | 80.16 | 163.2058
5733 | R-22 | 47.7 | 95.02 | 80.32 | 163.5315
5734 | R-22 | 47.8 | 95.18 | 80.48 | 163.8573
5735 | R-22 | 47.9 | 95.34 | 80.64 | 164.183
5736 | R-22 | 48 | 95.5 | 80.8 | 164.5088
5737 | R-22 | 48.1 | 95.66 | 80.96 | 164.8346
5738 | R-22 | 48.2 | 95.82 | 81.12 | 165.1603
5739 | R-22 | 48.3 | 95.99 | 81.29 | 165.5064
5740 | R-22 | 48.4 | 96.15 | 81.45 | 165.8322
5741 | R-22 | 48.5 | 96.31 | 81.61 | 166.158
5742 | R-22 | 48.6 | 96.47 | 81.77 | 166.4837
5743 | R-22 | 48.7 | 96.63 | 81.93 | 166.8095
5744 | R-22 | 48.8 | 96.8 | 82.1 | 167.1556
5745 | R-22 | 48.9 | 96.96 | 82.26 | 167.4814
5746 | R-22 | 49 | 97.12 | 82.42 | 167.8071
5747 | R-22 | 49.1 | 97.29 | 82.59 | 168.1532
5748 | R-22 | 49.2 | 97.45 | 82.75 | 168.479
5749 | R-22 | 49.3 | 97.61 | 82.91 | 168.8048
5750 | R-22 | 49.4 | 97.78 | 83.08 | 169.1509
5751 | R-22 | 49.5 | 97.94 | 83.24 | 169.4766
5752 | R-22 | 49.6 | 98.1 | 83.4 | 169.8024
5753 | R-22 | 49.7 | 98.27 | 83.57 | 170.1485
5754 | R-22 | 49.8 | 98.43 | 83.73 | 170.4743
5755 | R-22 | 49.9 | 98.6 | 83.9 | 170.8204
5756 | R-22 | 50 | 98.76 | 84.06 | 171.1462
5757 | R-22 | 50.1 | 98.93 | 84.23 | 171.4923
5758 | R-22 | 50.2 | 99.09 | 84.39 | 171.818
5759 | R-22 | 50.3 | 99.26 | 84.56 | 172.1642
5760 | R-22 | 50.4 | 99.43 | 84.73 | 172.5103
5761 | R-22 | 50.5 | 99.59 | 84.89 | 172.836
5762 | R-22 | 50.6 | 99.76 | 85.06 | 173.1822
5763 | R-22 | 50.7 | 99.92 | 85.22 | 173.5079
5764 | R-22 | 50.8 | 100.1 | 85.4 | 173.8744
5765 | R-22 | 50.9 | 100.3 | 85.6 | 174.2816
5766 | R-22 | 51 | 100.4 | 85.7 | 174.4852
5767 | R-22 | 51.1 | 100.6 | 85.9 | 174.8924
5768 | R-22 | 51.2 | 100.8 | 86.1 | 175.2996
5769 | R-22 | 51.3 | 100.9 | 86.2 | 175.5032
5770 | R-22 | 51.4 | 101.1 | 86.4 | 175.9104
5771 | R-22 | 51.5 | 101.3 | 86.6 | 176.3176
5772 | R-22 | 51.6 | 101.4 | 86.7 | 176.5212
5773 | R-22 | 51.7 | 101.6 | 86.9 | 176.9284
5774 | R-22 | 51.8 | 101.8 | 87.1 | 177.3356
5775 | R-22 | 51.9 | 101.9 | 87.2 | 177.5392
5776 | R-22 | 52 | 102.1 | 87.4 | 177.9464
5777 | R-22 | 52.1 | 102.3 | 87.6 | 178.3536
5778 | R-22 | 52.2 | 102.4 | 87.7 | 178.5572
5779 | R-22 | 52.3 | 102.6 | 87.9 | 178.9644
5780 | R-22 | 52.4 | 102.8 | 88.1 | 179.3716
5781 | R-22 | 52.5 | 103 | 88.3 | 179.7788
5782 | R-22 | 52.6 | 103.1 | 88.4 | 179.9824
5783 | R-22 | 52.7 | 103.3 | 88.6 | 180.3896
5784 | R-22 | 52.8 | 103.5 | 88.8 | 180.7968
5785 | R-22 | 52.9 | 103.6 | 88.9 | 181.0004
5786 | R-22 | 53 | 103.8 | 89.1 | 181.4076
5787 | R-22 | 53.1 | 104 | 89.3 | 181.8148
5788 | R-22 | 53.2 | 104.2 | 89.5 | 182.222
5789 | R-22 | 53.3 | 104.3 | 89.6 | 182.4256
5790 | R-22 | 53.4 | 104.5 | 89.8 | 182.8328
5791 | R-22 | 53.5 | 104.7 | 90 | 183.24
5792 | R-22 | 53.6 | 104.8 | 90.1 | 183.4436
5793 | R-22 | 53.7 | 105 | 90.3 | 183.8508
5794 | R-22 | 53.8 | 105.2 | 90.5 | 184.258
5795 | R-22 | 53.9 | 105.4 | 90.7 | 184.6652
5796 | R-22 | 54 | 105.5 | 90.8 | 184.8688
5797 | R-22 | 54.1 | 105.7 | 91 | 185.276
5798 | R-22 | 54.2 | 105.9 | 91.2 | 185.6832
5799 | R-22 | 54.3 | 106.1 | 91.4 | 186.0904
5800 | R-22 | 54.4 | 106.2 | 91.5 | 186.294
5801 | R-22 | 54.5 | 106.4 | 91.7 | 186.7012
5802 | R-22 | 54.6 | 106.6 | 91.9 | 187.1084
5803 | R-22 | 54.7 | 106.8 | 92.1 | 187.5156
5804 | R-22 | 54.8 | 106.9 | 92.2 | 187.7192
5805 | R-22 | 54.9 | 107.1 | 92.4 | 188.1264
5806 | R-22 | 55 | 107.3 | 92.6 | 188.5336
5807 | R-22 | 55.1 | 107.5 | 92.8 | 188.9408
5808 | R-22 | 55.2 | 107.6 | 92.9 | 189.1444
5809 | R-22 | 55.3 | 107.8 | 93.1 | 189.5516
5810 | R-22 | 55.4 | 108 | 93.3 | 189.9588
5811 | R-22 | 55.5 | 108.2 | 93.5 | 190.366
5812 | R-22 | 55.6 | 108.3 | 93.6 | 190.5696
5813 | R-22 | 55.7 | 108.5 | 93.8 | 190.9768
5814 | R-22 | 55.8 | 108.7 | 94 | 191.384
5815 | R-22 | 55.9 | 108.9 | 94.2 | 191.7912
5816 | R-22 | 56 | 109 | 94.3 | 191.9948
5817 | R-22 | 56.1 | 109.2 | 94.5 | 192.402
5818 | R-22 | 56.2 | 109.4 | 94.7 | 192.8092
5819 | R-22 | 56.3 | 109.6 | 94.9 | 193.2164
5820 | R-22 | 56.4 | 109.8 | 95.1 | 193.6236
5821 | R-22 | 56.5 | 109.9 | 95.2 | 193.8272
5822 | R-22 | 56.6 | 110.1 | 95.4 | 194.2344
5823 | R-22 | 56.7 | 110.3 | 95.6 | 194.6416
5824 | R-22 | 56.8 | 110.5 | 95.8 | 195.0488
5825 | R-22 | 56.9 | 110.7 | 96 | 195.456
5826 | R-22 | 57 | 110.8 | 96.1 | 195.6596
5827 | R-22 | 57.1 | 111 | 96.3 | 196.0668
5828 | R-22 | 57.2 | 111.2 | 96.5 | 196.474
5829 | R-22 | 57.3 | 111.4 | 96.7 | 196.8812
5830 | R-22 | 57.4 | 111.6 | 96.9 | 197.2884
5831 | R-22 | 57.5 | 111.7 | 97 | 197.492
5832 | R-22 | 57.6 | 111.9 | 97.2 | 197.8992
5833 | R-22 | 57.7 | 112.1 | 97.4 | 198.3064
5834 | R-22 | 57.8 | 112.3 | 97.6 | 198.7136
5835 | R-22 | 57.9 | 112.5 | 97.8 | 199.1208
5836 | R-22 | 58 | 112.6 | 97.9 | 199.3244
5837 | R-22 | 58.1 | 112.8 | 98.1 | 199.7316
5838 | R-22 | 58.2 | 113 | 98.3 | 200.1388
5839 | R-22 | 58.3 | 113.2 | 98.5 | 200.546
5840 | R-22 | 58.4 | 113.4 | 98.7 | 200.9532
5841 | R-22 | 58.5 | 113.6 | 98.9 | 201.3604
5842 | R-22 | 58.6 | 113.7 | 99 | 201.564
5843 | R-22 | 58.7 | 113.9 | 99.2 | 201.9712
5844 | R-22 | 58.8 | 114.1 | 99.4 | 202.3784
5845 | R-22 | 58.9 | 114.3 | 99.6 | 202.7856
5846 | R-22 | 59 | 114.5 | 99.8 | 203.1928
5847 | R-22 | 59.1 | 114.7 | 100 | 203.6
5848 | R-22 | 59.2 | 114.8 | 100.1 | 203.8036
5849 | R-22 | 59.3 | 115 | 100.3 | 204.2108
5850 | R-22 | 59.4 | 115.2 | 100.5 | 204.618
5851 | R-22 | 59.5 | 115.4 | 100.7 | 205.0252
5852 | R-22 | 59.6 | 115.6 | 100.9 | 205.4324
5853 | R-22 | 59.7 | 115.8 | 101.1 | 205.8396
5854 | R-22 | 59.8 | 116 | 101.3 | 206.2468
5855 | R-22 | 59.9 | 116.1 | 101.4 | 206.4504
5856 | R-22 | 60 | 116.3 | 101.6 | 206.8576
5857 | R-22 | 60.1 | 116.5 | 101.8 | 207.2648
5858 | R-22 | 60.2 | 116.7 | 102 | 207.672
5859 | R-22 | 60.3 | 116.9 | 102.2 | 208.0792
5860 | R-22 | 60.4 | 117.1 | 102.4 | 208.4864
5861 | R-22 | 60.5 | 117.3 | 102.6 | 208.8936
5862 | R-22 | 60.6 | 117.5 | 102.8 | 209.3008
5863 | R-22 | 60.7 | 117.6 | 102.9 | 209.5044
5864 | R-22 | 60.8 | 117.8 | 103.1 | 209.9116
5865 | R-22 | 60.9 | 118 | 103.3 | 210.3188
5866 | R-22 | 61 | 118.2 | 103.5 | 210.726
5867 | R-22 | 61.1 | 118.4 | 103.7 | 211.1332
5868 | R-22 | 61.2 | 118.6 | 103.9 | 211.5404
5869 | R-22 | 61.3 | 118.8 | 104.1 | 211.9476
5870 | R-22 | 61.4 | 119 | 104.3 | 212.3548
5871 | R-22 | 61.5 | 119.2 | 104.5 | 212.762
5872 | R-22 | 61.6 | 119.3 | 104.6 | 212.9656
5873 | R-22 | 61.7 | 119.5 | 104.8 | 213.3728
5874 | R-22 | 61.8 | 119.7 | 105 | 213.78
5875 | R-22 | 61.9 | 119.9 | 105.2 | 214.1872
5876 | R-22 | 62 | 120.1 | 105.4 | 214.5944
5877 | R-22 | 62.1 | 120.3 | 105.6 | 215.0016
5878 | R-22 | 62.2 | 120.5 | 105.8 | 215.4088
5879 | R-22 | 62.3 | 120.7 | 106 | 215.816
5880 | R-22 | 62.4 | 120.9 | 106.2 | 216.2232
5881 | R-22 | 62.5 | 121.1 | 106.4 | 216.6304
5882 | R-22 | 62.6 | 121.3 | 106.6 | 217.0376
5883 | R-22 | 62.7 | 121.5 | 106.8 | 217.4448
5884 | R-22 | 62.8 | 121.6 | 106.9 | 217.6484
5885 | R-22 | 62.9 | 121.8 | 107.1 | 218.0556
5886 | R-22 | 63 | 122 | 107.3 | 218.4628
5887 | R-22 | 63.1 | 122.2 | 107.5 | 218.87
5888 | R-22 | 63.2 | 122.4 | 107.7 | 219.2772
5889 | R-22 | 63.3 | 122.6 | 107.9 | 219.6844
5890 | R-22 | 63.4 | 122.8 | 108.1 | 220.0916
5891 | R-22 | 63.5 | 123 | 108.3 | 220.4988
5892 | R-22 | 63.6 | 123.2 | 108.5 | 220.906
5893 | R-22 | 63.7 | 123.4 | 108.7 | 221.3132
5894 | R-22 | 63.8 | 123.6 | 108.9 | 221.7204
5895 | R-22 | 63.9 | 123.8 | 109.1 | 222.1276
5896 | R-22 | 64 | 124 | 109.3 | 222.5348
5897 | R-22 | 64.1 | 124.2 | 109.5 | 222.942
5898 | R-22 | 64.2 | 124.4 | 109.7 | 223.3492
5899 | R-22 | 64.3 | 124.6 | 109.9 | 223.7564
5900 | R-22 | 64.4 | 124.8 | 110.1 | 224.1636
5901 | R-22 | 64.5 | 125 | 110.3 | 224.5708
5902 | R-22 | 64.6 | 125.2 | 110.5 | 224.978
5903 | R-22 | 64.7 | 125.4 | 110.7 | 225.3852
5904 | R-22 | 64.8 | 125.5 | 110.8 | 225.5888
5905 | R-22 | 64.9 | 125.7 | 111 | 225.996
5906 | R-22 | 65 | 125.9 | 111.2 | 226.4032
5907 | R-22 | 65.1 | 126.1 | 111.4 | 226.8104
5908 | R-22 | 65.2 | 126.3 | 111.6 | 227.2176
5909 | R-22 | 65.3 | 126.5 | 111.8 | 227.6248
5910 | R-22 | 65.4 | 126.7 | 112 | 228.032
5911 | R-22 | 65.5 | 126.9 | 112.2 | 228.4392
5912 | R-22 | 65.6 | 127.1 | 112.4 | 228.8464
5913 | R-22 | 65.7 | 127.3 | 112.6 | 229.2536
5914 | R-22 | 65.8 | 127.5 | 112.8 | 229.6608
5915 | R-22 | 65.9 | 127.7 | 113 | 230.068
5916 | R-22 | 66 | 127.9 | 113.2 | 230.4752
5917 | R-22 | 66.1 | 128.1 | 113.4 | 230.8824
5918 | R-22 | 66.2 | 128.3 | 113.6 | 231.2896
5919 | R-22 | 66.3 | 128.5 | 113.8 | 231.6968
5920 | R-22 | 66.4 | 128.7 | 114 | 232.104
5921 | R-22 | 66.5 | 128.9 | 114.2 | 232.5112
5922 | R-22 | 66.6 | 129.1 | 114.4 | 232.9184
5923 | R-22 | 66.7 | 129.3 | 114.6 | 233.3256
5924 | R-22 | 66.8 | 129.5 | 114.8 | 233.7328
5925 | R-22 | 66.9 | 129.7 | 115 | 234.14
5926 | R-22 | 67 | 129.9 | 115.2 | 234.5472
5927 | R-22 | 67.1 | 130.2 | 115.5 | 235.158
5928 | R-22 | 67.2 | 130.4 | 115.7 | 235.5652
5929 | R-22 | 67.3 | 130.6 | 115.9 | 235.9724
5930 | R-22 | 67.4 | 130.8 | 116.1 | 236.3796
5931 | R-22 | 67.5 | 131 | 116.3 | 236.7868
5932 | R-22 | 67.6 | 131.2 | 116.5 | 237.194
5933 | R-22 | 67.7 | 131.4 | 116.7 | 237.6012
5934 | R-22 | 67.8 | 131.6 | 116.9 | 238.0084
5935 | R-22 | 67.9 | 131.8 | 117.1 | 238.4156
5936 | R-22 | 68 | 132 | 117.3 | 238.8228
5937 | R-22 | 68.1 | 132.2 | 117.5 | 239.23
5938 | R-22 | 68.2 | 132.4 | 117.7 | 239.6372
5939 | R-22 | 68.3 | 132.6 | 117.9 | 240.0444
5940 | R-22 | 68.4 | 132.8 | 118.1 | 240.4516
5941 | R-22 | 68.5 | 133 | 118.3 | 240.8588
5942 | R-22 | 68.6 | 133.2 | 118.5 | 241.266
5943 | R-22 | 68.7 | 133.4 | 118.7 | 241.6732
5944 | R-22 | 68.8 | 133.6 | 118.9 | 242.0804
5945 | R-22 | 68.9 | 133.8 | 119.1 | 242.4876
5946 | R-22 | 69 | 134 | 119.3 | 242.8948
5947 | R-22 | 69.1 | 134.3 | 119.6 | 243.5056
5948 | R-22 | 69.2 | 134.5 | 119.8 | 243.9128
5949 | R-22 | 69.3 | 134.7 | 120 | 244.32
5950 | R-22 | 69.4 | 134.9 | 120.2 | 244.7272
5951 | R-22 | 69.5 | 135.1 | 120.4 | 245.1344
5952 | R-22 | 69.6 | 135.3 | 120.6 | 245.5416
5953 | R-22 | 69.7 | 135.5 | 120.8 | 245.9488
5954 | R-22 | 69.8 | 135.7 | 121 | 246.356
5955 | R-22 | 69.9 | 135.9 | 121.2 | 246.7632
5956 | R-22 | 70 | 136.1 | 121.4 | 247.1704
5957 | R-22 | 70.1 | 136.3 | 121.6 | 247.5776
5958 | R-22 | 70.2 | 136.6 | 121.9 | 248.1884
5959 | R-22 | 70.3 | 136.8 | 122.1 | 248.5956
5960 | R-22 | 70.4 | 137 | 122.3 | 249.0028
5961 | R-22 | 70.5 | 137.2 | 122.5 | 249.41
5962 | R-22 | 70.6 | 137.4 | 122.7 | 249.8172
5963 | R-22 | 70.7 | 137.6 | 122.9 | 250.2244
5964 | R-22 | 70.8 | 137.8 | 123.1 | 250.6316
5965 | R-22 | 70.9 | 138 | 123.3 | 251.0388
5966 | R-22 | 71 | 138.2 | 123.5 | 251.446
5967 | R-22 | 71.1 | 138.5 | 123.8 | 252.0568
5968 | R-22 | 71.2 | 138.7 | 124 | 252.464
5969 | R-22 | 71.3 | 138.9 | 124.2 | 252.8712
5970 | R-22 | 71.4 | 139.1 | 124.4 | 253.2784
5971 | R-22 | 71.5 | 139.3 | 124.6 | 253.6856
5972 | R-22 | 71.6 | 139.5 | 124.8 | 254.0928
5973 | R-22 | 71.7 | 139.7 | 125 | 254.5
5974 | R-22 | 71.8 | 139.9 | 125.2 | 254.9072
5975 | R-22 | 71.9 | 140.2 | 125.5 | 255.518
5976 | R-22 | 72 | 140.4 | 125.7 | 255.9252
5977 | R-22 | 72.1 | 140.6 | 125.9 | 256.3324
5978 | R-22 | 72.2 | 140.8 | 126.1 | 256.7396
5979 | R-22 | 72.3 | 141 | 126.3 | 257.1468
5980 | R-22 | 72.4 | 141.2 | 126.5 | 257.554
5981 | R-22 | 72.5 | 141.5 | 126.8 | 258.1648
5982 | R-22 | 72.6 | 141.7 | 127 | 258.572
5983 | R-22 | 72.7 | 141.9 | 127.2 | 258.9792
5984 | R-22 | 72.8 | 142.1 | 127.4 | 259.3864
5985 | R-22 | 72.9 | 142.3 | 127.6 | 259.7936
5986 | R-22 | 73 | 142.5 | 127.8 | 260.2008
5987 | R-22 | 73.1 | 142.7 | 128 | 260.608
5988 | R-22 | 73.2 | 143 | 128.3 | 261.2188
5989 | R-22 | 73.3 | 143.2 | 128.5 | 261.626
5990 | R-22 | 73.4 | 143.4 | 128.7 | 262.0332
5991 | R-22 | 73.5 | 143.6 | 128.9 | 262.4404
5992 | R-22 | 73.6 | 143.8 | 129.1 | 262.8476
5993 | R-22 | 73.7 | 144.1 | 129.4 | 263.4584
5994 | R-22 | 73.8 | 144.3 | 129.6 | 263.8656
5995 | R-22 | 73.9 | 144.5 | 129.8 | 264.2728
5996 | R-22 | 74 | 144.7 | 130 | 264.68
5997 | R-22 | 74.1 | 144.9 | 130.2 | 265.0872
5998 | R-22 | 74.2 | 145.2 | 130.5 | 265.698
5999 | R-22 | 74.3 | 145.4 | 130.7 | 266.1052
6000 | R-22 | 74.4 | 145.6 | 130.9 | 266.5124
6001 | R-22 | 74.5 | 145.8 | 131.1 | 266.9196
6002 | R-22 | 74.6 | 146 | 131.3 | 267.3268
6003 | R-22 | 74.7 | 146.3 | 131.6 | 267.9376
6004 | R-22 | 74.8 | 146.5 | 131.8 | 268.3448
6005 | R-22 | 74.9 | 146.7 | 132 | 268.752
6006 | R-22 | 75 | 146.9 | 132.2 | 269.1592
6007 | R-22 | 75.1 | 147.1 | 132.4 | 269.5664
6008 | R-22 | 75.2 | 147.4 | 132.7 | 270.1772
6009 | R-22 | 75.3 | 147.6 | 132.9 | 270.5844
6010 | R-22 | 75.4 | 147.8 | 133.1 | 270.9916
6011 | R-22 | 75.5 | 148 | 133.3 | 271.3988
6012 | R-22 | 75.6 | 148.3 | 133.6 | 272.0096
6013 | R-22 | 75.7 | 148.5 | 133.8 | 272.4168
6014 | R-22 | 75.8 | 148.7 | 134 | 272.824
6015 | R-22 | 75.9 | 148.9 | 134.2 | 273.2312
6016 | R-22 | 76 | 149.2 | 134.5 | 273.842
6017 | R-22 | 76.1 | 149.4 | 134.7 | 274.2492
6018 | R-22 | 76.2 | 149.6 | 134.9 | 274.6564
6019 | R-22 | 76.3 | 149.8 | 135.1 | 275.0636
6020 | R-22 | 76.4 | 150.1 | 135.4 | 275.6744
6021 | R-22 | 76.5 | 150.3 | 135.6 | 276.0816
6022 | R-22 | 76.6 | 150.5 | 135.8 | 276.4888
6023 | R-22 | 76.7 | 150.7 | 136 | 276.896
6024 | R-22 | 76.8 | 151 | 136.3 | 277.5068
6025 | R-22 | 76.9 | 151.2 | 136.5 | 277.914
6026 | R-22 | 77 | 151.4 | 136.7 | 278.3212
6027 | R-22 | 77.1 | 151.6 | 136.9 | 278.7284
6028 | R-22 | 77.2 | 151.9 | 137.2 | 279.3392
6029 | R-22 | 77.3 | 152.1 | 137.4 | 279.7464
6030 | R-22 | 77.4 | 152.3 | 137.6 | 280.1536
6031 | R-22 | 77.5 | 152.5 | 137.8 | 280.5608
6032 | R-22 | 77.6 | 152.8 | 138.1 | 281.1716
6033 | R-22 | 77.7 | 153 | 138.3 | 281.5788
6034 | R-22 | 77.8 | 153.2 | 138.5 | 281.986
6035 | R-22 | 77.9 | 153.5 | 138.8 | 282.5968
6036 | R-22 | 78 | 153.7 | 139 | 283.004
6037 | R-22 | 78.1 | 153.9 | 139.2 | 283.4112
6038 | R-22 | 78.2 | 154.1 | 139.4 | 283.8184
6039 | R-22 | 78.3 | 154.4 | 139.7 | 284.4292
6040 | R-22 | 78.4 | 154.6 | 139.9 | 284.8364
6041 | R-22 | 78.5 | 154.8 | 140.1 | 285.2436
6042 | R-22 | 78.6 | 155.1 | 140.4 | 285.8544
6043 | R-22 | 78.7 | 155.3 | 140.6 | 286.2616
6044 | R-22 | 78.8 | 155.5 | 140.8 | 286.6688
6045 | R-22 | 78.9 | 155.8 | 141.1 | 287.2796
6046 | R-22 | 79 | 156 | 141.3 | 287.6868
6047 | R-22 | 79.1 | 156.2 | 141.5 | 288.094
6048 | R-22 | 79.2 | 156.5 | 141.8 | 288.7048
6049 | R-22 | 79.3 | 156.7 | 142 | 289.112
6050 | R-22 | 79.4 | 156.9 | 142.2 | 289.5192
6051 | R-22 | 79.5 | 157.2 | 142.5 | 290.13
6052 | R-22 | 79.6 | 157.4 | 142.7 | 290.5372
6053 | R-22 | 79.7 | 157.6 | 142.9 | 290.9444
6054 | R-22 | 79.8 | 157.9 | 143.2 | 291.5552
6055 | R-22 | 79.9 | 158.1 | 143.4 | 291.9624
6056 | R-22 | 80 | 158.3 | 143.6 | 292.3696
6057 | R-22 | 80.1 | 158.6 | 143.9 | 292.9804
6058 | R-22 | 80.2 | 158.8 | 144.1 | 293.3876
6059 | R-22 | 80.3 | 159 | 144.3 | 293.7948
6060 | R-22 | 80.4 | 159.3 | 144.6 | 294.4056
6061 | R-22 | 80.5 | 159.5 | 144.8 | 294.8128
6062 | R-22 | 80.6 | 159.7 | 145 | 295.22
6063 | R-22 | 80.7 | 160 | 145.3 | 295.8308
6064 | R-22 | 80.8 | 160.2 | 145.5 | 296.238
6065 | R-22 | 80.9 | 160.4 | 145.7 | 296.6452
6066 | R-22 | 81 | 160.7 | 146 | 297.256
6067 | R-22 | 81.1 | 160.9 | 146.2 | 297.6632
6068 | R-22 | 81.2 | 161.2 | 146.5 | 298.274
6069 | R-22 | 81.3 | 161.4 | 146.7 | 298.6812
6070 | R-22 | 81.4 | 161.6 | 146.9 | 299.0884
6071 | R-22 | 81.5 | 161.9 | 147.2 | 299.6992
6072 | R-22 | 81.6 | 162.1 | 147.4 | 300.1064
6073 | R-22 | 81.7 | 162.4 | 147.7 | 300.7172
6074 | R-22 | 81.8 | 162.6 | 147.9 | 301.1244
6075 | R-22 | 81.9 | 162.8 | 148.1 | 301.5316
6076 | R-22 | 82 | 163.1 | 148.4 | 302.1424
6077 | R-22 | 82.1 | 163.3 | 148.6 | 302.5496
6078 | R-22 | 82.2 | 163.5 | 148.8 | 302.9568
6079 | R-22 | 82.3 | 163.8 | 149.1 | 303.5676
6080 | R-22 | 82.4 | 164 | 149.3 | 303.9748
6081 | R-22 | 82.5 | 164.3 | 149.6 | 304.5856
6082 | R-22 | 82.6 | 164.5 | 149.8 | 304.9928
6083 | R-22 | 82.7 | 164.8 | 150.1 | 305.6036
6084 | R-22 | 82.8 | 165 | 150.3 | 306.0108
6085 | R-22 | 82.9 | 165.2 | 150.5 | 306.418
6086 | R-22 | 83 | 165.5 | 150.8 | 307.0288
6087 | R-22 | 83.1 | 165.7 | 151 | 307.436
6088 | R-22 | 83.2 | 166 | 151.3 | 308.0468
6089 | R-22 | 83.3 | 166.2 | 151.5 | 308.454
6090 | R-22 | 83.4 | 166.5 | 151.8 | 309.0648
6091 | R-22 | 83.5 | 166.7 | 152 | 309.472
6092 | R-22 | 83.6 | 166.9 | 152.2 | 309.8792
6093 | R-22 | 83.7 | 167.2 | 152.5 | 310.49
6094 | R-22 | 83.8 | 167.4 | 152.7 | 310.8972
6095 | R-22 | 83.9 | 167.7 | 153 | 311.508
6096 | R-22 | 84 | 167.9 | 153.2 | 311.9152
6097 | R-22 | 84.1 | 168.2 | 153.5 | 312.526
6098 | R-22 | 84.2 | 168.4 | 153.7 | 312.9332
6099 | R-22 | 84.3 | 168.7 | 154 | 313.544
6100 | R-22 | 84.4 | 168.9 | 154.2 | 313.9512
6101 | R-22 | 84.5 | 169.1 | 154.4 | 314.3584
6102 | R-22 | 84.6 | 169.4 | 154.7 | 314.9692
6103 | R-22 | 84.7 | 169.6 | 154.9 | 315.3764
6104 | R-22 | 84.8 | 169.9 | 155.2 | 315.9872
6105 | R-22 | 84.9 | 170.1 | 155.4 | 316.3944
6106 | R-22 | 85 | 170.4 | 155.7 | 317.0052
6107 | R-22 | 85.1 | 170.6 | 155.9 | 317.4124
6108 | R-22 | 85.2 | 170.9 | 156.2 | 318.0232
6109 | R-22 | 85.3 | 171.1 | 156.4 | 318.4304
6110 | R-22 | 85.4 | 171.4 | 156.7 | 319.0412
6111 | R-22 | 85.5 | 171.6 | 156.9 | 319.4484
6112 | R-22 | 85.6 | 171.9 | 157.2 | 320.0592
6113 | R-22 | 85.7 | 172.1 | 157.4 | 320.4664
6114 | R-22 | 85.8 | 172.4 | 157.7 | 321.0772
6115 | R-22 | 85.9 | 172.6 | 157.9 | 321.4844
6116 | R-22 | 86 | 172.9 | 158.2 | 322.0952
6117 | R-22 | 86.1 | 173.1 | 158.4 | 322.5024
6118 | R-22 | 86.2 | 173.4 | 158.7 | 323.1132
6119 | R-22 | 86.3 | 173.6 | 158.9 | 323.5204
6120 | R-22 | 86.4 | 173.9 | 159.2 | 324.1312
6121 | R-22 | 86.5 | 174.1 | 159.4 | 324.5384
6122 | R-22 | 86.6 | 174.4 | 159.7 | 325.1492
6123 | R-22 | 86.7 | 174.6 | 159.9 | 325.5564
6124 | R-22 | 86.8 | 174.9 | 160.2 | 326.1672
6125 | R-22 | 86.9 | 175.1 | 160.4 | 326.5744
6126 | R-22 | 87 | 175.4 | 160.7 | 327.1852
6127 | R-22 | 87.1 | 175.6 | 160.9 | 327.5924
6128 | R-22 | 87.2 | 175.9 | 161.2 | 328.2032
6129 | R-22 | 87.3 | 176.1 | 161.4 | 328.6104
6130 | R-22 | 87.4 | 176.4 | 161.7 | 329.2212
6131 | R-22 | 87.5 | 176.7 | 162 | 329.832
6132 | R-22 | 87.6 | 176.9 | 162.2 | 330.2392
6133 | R-22 | 87.7 | 177.2 | 162.5 | 330.85
6134 | R-22 | 87.8 | 177.4 | 162.7 | 331.2572
6135 | R-22 | 87.9 | 177.7 | 163 | 331.868
6136 | R-22 | 88 | 177.9 | 163.2 | 332.2752
6137 | R-22 | 88.1 | 178.2 | 163.5 | 332.886
6138 | R-22 | 88.2 | 178.4 | 163.7 | 333.2932
6139 | R-22 | 88.3 | 178.7 | 164 | 333.904
6140 | R-22 | 88.4 | 179 | 164.3 | 334.5148
6141 | R-22 | 88.5 | 179.2 | 164.5 | 334.922
6142 | R-22 | 88.6 | 179.5 | 164.8 | 335.5328
6143 | R-22 | 88.7 | 179.7 | 165 | 335.94
6144 | R-22 | 88.8 | 180 | 165.3 | 336.5508
6145 | R-22 | 88.9 | 180.2 | 165.5 | 336.958
6146 | R-22 | 89 | 180.5 | 165.8 | 337.5688
6147 | R-22 | 89.1 | 180.8 | 166.1 | 338.1796
6148 | R-22 | 89.2 | 181 | 166.3 | 338.5868
6149 | R-22 | 89.3 | 181.3 | 166.6 | 339.1976
6150 | R-22 | 89.4 | 181.5 | 166.8 | 339.6048
6151 | R-22 | 89.5 | 181.8 | 167.1 | 340.2156
6152 | R-22 | 89.6 | 182.1 | 167.4 | 340.8264
6153 | R-22 | 89.7 | 182.3 | 167.6 | 341.2336
6154 | R-22 | 89.8 | 182.6 | 167.9 | 341.8444
6155 | R-22 | 89.9 | 182.8 | 168.1 | 342.2516
6156 | R-22 | 90 | 183.1 | 168.4 | 342.8624
6157 | R-22 | 90.1 | 183.4 | 168.7 | 343.4732
6158 | R-22 | 90.2 | 183.6 | 168.9 | 343.8804
6159 | R-22 | 90.3 | 183.9 | 169.2 | 344.4912
6160 | R-22 | 90.4 | 184.1 | 169.4 | 344.8984
6161 | R-22 | 90.5 | 184.4 | 169.7 | 345.5092
6162 | R-22 | 90.6 | 184.7 | 170 | 346.12
6163 | R-22 | 90.7 | 184.9 | 170.2 | 346.5272
6164 | R-22 | 90.8 | 185.2 | 170.5 | 347.138
6165 | R-22 | 90.9 | 185.5 | 170.8 | 347.7488
6166 | R-22 | 91 | 185.7 | 171 | 348.156
6167 | R-22 | 91.1 | 186 | 171.3 | 348.7668
6168 | R-22 | 91.2 | 186.2 | 171.5 | 349.174
6169 | R-22 | 91.3 | 186.5 | 171.8 | 349.7848
6170 | R-22 | 91.4 | 186.8 | 172.1 | 350.3956
6171 | R-22 | 91.5 | 187 | 172.3 | 350.8028
6172 | R-22 | 91.6 | 187.3 | 172.6 | 351.4136
6173 | R-22 | 91.7 | 187.6 | 172.9 | 352.0244
6174 | R-22 | 91.8 | 187.8 | 173.1 | 352.4316
6175 | R-22 | 91.9 | 188.1 | 173.4 | 353.0424
6176 | R-22 | 92 | 188.4 | 173.7 | 353.6532
6177 | R-22 | 92.1 | 188.6 | 173.9 | 354.0604
6178 | R-22 | 92.2 | 188.9 | 174.2 | 354.6712
6179 | R-22 | 92.3 | 189.2 | 174.5 | 355.282
6180 | R-22 | 92.4 | 189.4 | 174.7 | 355.6892
6181 | R-22 | 92.5 | 189.7 | 175 | 356.3
6182 | R-22 | 92.6 | 190 | 175.3 | 356.9108
6183 | R-22 | 92.7 | 190.2 | 175.5 | 357.318
6184 | R-22 | 92.8 | 190.5 | 175.8 | 357.9288
6185 | R-22 | 92.9 | 190.8 | 176.1 | 358.5396
6186 | R-22 | 93 | 191.1 | 176.4 | 359.1504
6187 | R-22 | 93.1 | 191.3 | 176.6 | 359.5576
6188 | R-22 | 93.2 | 191.6 | 176.9 | 360.1684
6189 | R-22 | 93.3 | 191.9 | 177.2 | 360.7792
6190 | R-22 | 93.4 | 192.1 | 177.4 | 361.1864
6191 | R-22 | 93.5 | 192.4 | 177.7 | 361.7972
6192 | R-22 | 93.6 | 192.7 | 178 | 362.408
6193 | R-22 | 93.7 | 192.9 | 178.2 | 362.8152
6194 | R-22 | 93.8 | 193.2 | 178.5 | 363.426
6195 | R-22 | 93.9 | 193.5 | 178.8 | 364.0368
6196 | R-22 | 94 | 193.8 | 179.1 | 364.6476
6197 | R-22 | 94.1 | 194 | 179.3 | 365.0548
6198 | R-22 | 94.2 | 194.3 | 179.6 | 365.6656
6199 | R-22 | 94.3 | 194.6 | 179.9 | 366.2764
6200 | R-22 | 94.4 | 194.9 | 180.2 | 366.8872
6201 | R-22 | 94.5 | 195.1 | 180.4 | 367.2944
6202 | R-22 | 94.6 | 195.4 | 180.7 | 367.9052
6203 | R-22 | 94.7 | 195.7 | 181 | 368.516
6204 | R-22 | 94.8 | 195.9 | 181.2 | 368.9232
6205 | R-22 | 94.9 | 196.2 | 181.5 | 369.534
6206 | R-22 | 95 | 196.5 | 181.8 | 370.1448
6207 | R-22 | 95.1 | 196.8 | 182.1 | 370.7556
6208 | R-22 | 95.2 | 197 | 182.3 | 371.1628
6209 | R-22 | 95.3 | 197.3 | 182.6 | 371.7736
6210 | R-22 | 95.4 | 197.6 | 182.9 | 372.3844
6211 | R-22 | 95.5 | 197.9 | 183.2 | 372.9952
6212 | R-22 | 95.6 | 198.2 | 183.5 | 373.606
6213 | R-22 | 95.7 | 198.4 | 183.7 | 374.0132
6214 | R-22 | 95.8 | 198.7 | 184 | 374.624
6215 | R-22 | 95.9 | 199 | 184.3 | 375.2348
6216 | R-22 | 96 | 199.3 | 184.6 | 375.8456
6217 | R-22 | 96.1 | 199.5 | 184.8 | 376.2528
6218 | R-22 | 96.2 | 199.8 | 185.1 | 376.8636
6219 | R-22 | 96.3 | 200.1 | 185.4 | 377.4744
6220 | R-22 | 96.4 | 200.4 | 185.7 | 378.0852
6221 | R-22 | 96.5 | 200.7 | 186 | 378.696
6222 | R-22 | 96.6 | 200.9 | 186.2 | 379.1032
6223 | R-22 | 96.7 | 201.2 | 186.5 | 379.714
6224 | R-22 | 96.8 | 201.5 | 186.8 | 380.3248
6225 | R-22 | 96.9 | 201.8 | 187.1 | 380.9356
6226 | R-22 | 97 | 202.1 | 187.4 | 381.5464
6227 | R-22 | 97.1 | 202.3 | 187.6 | 381.9536
6228 | R-22 | 97.2 | 202.6 | 187.9 | 382.5644
6229 | R-22 | 97.3 | 202.9 | 188.2 | 383.1752
6230 | R-22 | 97.4 | 203.2 | 188.5 | 383.786
6231 | R-22 | 97.5 | 203.5 | 188.8 | 384.3968
6232 | R-22 | 97.6 | 203.7 | 189 | 384.804
6233 | R-22 | 97.7 | 204 | 189.3 | 385.4148
6234 | R-22 | 97.8 | 204.3 | 189.6 | 386.0256
6235 | R-22 | 97.9 | 204.6 | 189.9 | 386.6364
6236 | R-22 | 98 | 204.9 | 190.2 | 387.2472
6237 | R-22 | 98.1 | 205.2 | 190.5 | 387.858
6238 | R-22 | 98.2 | 205.4 | 190.7 | 388.2652
6239 | R-22 | 98.3 | 205.7 | 191 | 388.876
6240 | R-22 | 98.4 | 206 | 191.3 | 389.4868
6241 | R-22 | 98.5 | 206.3 | 191.6 | 390.0976
6242 | R-22 | 98.6 | 206.6 | 191.9 | 390.7084
6243 | R-22 | 98.7 | 206.9 | 192.2 | 391.3192
6244 | R-22 | 98.8 | 207.2 | 192.5 | 391.93
6245 | R-22 | 98.9 | 207.4 | 192.7 | 392.3372
6246 | R-22 | 99 | 207.7 | 193 | 392.948
6247 | R-22 | 99.1 | 208 | 193.3 | 393.5588
6248 | R-22 | 99.2 | 208.3 | 193.6 | 394.1696
6249 | R-22 | 99.3 | 208.6 | 193.9 | 394.7804
6250 | R-22 | 99.4 | 208.9 | 194.2 | 395.3912
6251 | R-22 | 99.5 | 209.2 | 194.5 | 396.002
6252 | R-22 | 99.6 | 209.5 | 194.8 | 396.6128
6253 | R-22 | 99.7 | 209.7 | 195 | 397.02
6254 | R-22 | 99.8 | 210 | 195.3 | 397.6308
6255 | R-22 | 99.9 | 210.3 | 195.6 | 398.2416
6256 | R-22 | 100 | 210.6 | 195.9 | 398.8524
6257 | R-22 | 100.1 | 210.9 | 196.2 | 399.4632
6258 | R-22 | 100.2 | 211.2 | 196.5 | 400.074
6259 | R-22 | 100.3 | 211.5 | 196.8 | 400.6848
6260 | R-22 | 100.4 | 211.8 | 197.1 | 401.2956
6261 | R-22 | 100.5 | 212.1 | 197.4 | 401.9064
6262 | R-22 | 100.6 | 212.4 | 197.7 | 402.5172
6263 | R-22 | 100.7 | 212.6 | 197.9 | 402.9244
6264 | R-22 | 100.8 | 212.9 | 198.2 | 403.5352
6265 | R-22 | 100.9 | 213.2 | 198.5 | 404.146
6266 | R-22 | 101 | 213.5 | 198.8 | 404.7568
6267 | R-22 | 101.1 | 213.8 | 199.1 | 405.3676
6268 | R-22 | 101.2 | 214.1 | 199.4 | 405.9784
6269 | R-22 | 101.3 | 214.4 | 199.7 | 406.5892
6270 | R-22 | 101.4 | 214.7 | 200 | 407.2
6271 | R-22 | 101.5 | 215 | 200.3 | 407.8108
6272 | R-22 | 101.6 | 215.3 | 200.6 | 408.4216
6273 | R-22 | 101.7 | 215.6 | 200.9 | 409.0324
6274 | R-22 | 101.8 | 215.9 | 201.2 | 409.6432
6275 | R-22 | 101.9 | 216.2 | 201.5 | 410.254
6276 | R-22 | 102 | 216.5 | 201.8 | 410.8648
6277 | R-22 | 102.1 | 216.8 | 202.1 | 411.4756
6278 | R-22 | 102.2 | 217 | 202.3 | 411.8828
6279 | R-22 | 102.3 | 217.3 | 202.6 | 412.4936
6280 | R-22 | 102.4 | 217.6 | 202.9 | 413.1044
6281 | R-22 | 102.5 | 217.9 | 203.2 | 413.7152
6282 | R-22 | 102.6 | 218.2 | 203.5 | 414.326
6283 | R-22 | 102.7 | 218.5 | 203.8 | 414.9368
6284 | R-22 | 102.8 | 218.8 | 204.1 | 415.5476
6285 | R-22 | 102.9 | 219.1 | 204.4 | 416.1584
6286 | R-22 | 103 | 219.4 | 204.7 | 416.7692
6287 | R-22 | 103.1 | 219.7 | 205 | 417.38
6288 | R-22 | 103.2 | 220 | 205.3 | 417.9908
6289 | R-22 | 103.3 | 220.3 | 205.6 | 418.6016
6290 | R-22 | 103.4 | 220.6 | 205.9 | 419.2124
6291 | R-22 | 103.5 | 220.9 | 206.2 | 419.8232
6292 | R-22 | 103.6 | 221.2 | 206.5 | 420.434
6293 | R-22 | 103.7 | 221.5 | 206.8 | 421.0448
6294 | R-22 | 103.8 | 221.8 | 207.1 | 421.6556
6295 | R-22 | 103.9 | 222.1 | 207.4 | 422.2664
6296 | R-22 | 104 | 222.4 | 207.7 | 422.8772
6297 | R-22 | 104.1 | 222.7 | 208 | 423.488
6298 | R-22 | 104.2 | 223 | 208.3 | 424.0988
6299 | R-22 | 104.3 | 223.3 | 208.6 | 424.7096
6300 | R-22 | 104.4 | 223.6 | 208.9 | 425.3204
6301 | R-22 | 104.5 | 223.9 | 209.2 | 425.9312
6302 | R-22 | 104.6 | 224.2 | 209.5 | 426.542
6303 | R-22 | 104.7 | 224.5 | 209.8 | 427.1528
6304 | R-22 | 104.8 | 224.8 | 210.1 | 427.7636
6305 | R-22 | 104.9 | 225.2 | 210.5 | 428.578
6306 | R-22 | 105 | 225.5 | 210.8 | 429.1888
6307 | R-22 | 105.1 | 225.8 | 211.1 | 429.7996
6308 | R-22 | 105.2 | 226.1 | 211.4 | 430.4104
6309 | R-22 | 105.3 | 226.4 | 211.7 | 431.0212
6310 | R-22 | 105.4 | 226.7 | 212 | 431.632
6311 | R-22 | 105.5 | 227 | 212.3 | 432.2428
6312 | R-22 | 105.6 | 227.3 | 212.6 | 432.8536
6313 | R-22 | 105.7 | 227.6 | 212.9 | 433.4644
6314 | R-22 | 105.8 | 227.9 | 213.2 | 434.0752
6315 | R-22 | 105.9 | 228.2 | 213.5 | 434.686
6316 | R-22 | 106 | 228.5 | 213.8 | 435.2968
6317 | R-22 | 106.1 | 228.8 | 214.1 | 435.9076
6318 | R-22 | 106.2 | 229.1 | 214.4 | 436.5184
6319 | R-22 | 106.3 | 229.4 | 214.7 | 437.1292
6320 | R-22 | 106.4 | 229.7 | 215 | 437.74
6321 | R-22 | 106.5 | 230.1 | 215.4 | 438.5544
6322 | R-22 | 106.6 | 230.4 | 215.7 | 439.1652
6323 | R-22 | 106.7 | 230.7 | 216 | 439.776
6324 | R-22 | 106.8 | 231 | 216.3 | 440.3868
6325 | R-22 | 106.9 | 231.3 | 216.6 | 440.9976
6326 | R-22 | 107 | 231.6 | 216.9 | 441.6084
6327 | R-22 | 107.1 | 231.9 | 217.2 | 442.2192
6328 | R-22 | 107.2 | 232.2 | 217.5 | 442.83
6329 | R-22 | 107.3 | 232.5 | 217.8 | 443.4408
6330 | R-22 | 107.4 | 232.9 | 218.2 | 444.2552
6331 | R-22 | 107.5 | 233.2 | 218.5 | 444.866
6332 | R-22 | 107.6 | 233.5 | 218.8 | 445.4768
6333 | R-22 | 107.7 | 233.8 | 219.1 | 446.0876
6334 | R-22 | 107.8 | 234.1 | 219.4 | 446.6984
6335 | R-22 | 107.9 | 234.4 | 219.7 | 447.3092
6336 | R-22 | 108 | 234.7 | 220 | 447.92
6337 | R-22 | 108.1 | 235 | 220.3 | 448.5308
6338 | R-22 | 108.2 | 235.4 | 220.7 | 449.3452
6339 | R-22 | 108.3 | 235.7 | 221 | 449.956
6340 | R-22 | 108.4 | 236 | 221.3 | 450.5668
6341 | R-22 | 108.5 | 236.3 | 221.6 | 451.1776
6342 | R-22 | 108.6 | 236.6 | 221.9 | 451.7884
6343 | R-22 | 108.7 | 236.9 | 222.2 | 452.3992
6344 | R-22 | 108.8 | 237.2 | 222.5 | 453.01
6345 | R-22 | 108.9 | 237.6 | 222.9 | 453.8244
6346 | R-22 | 109 | 237.9 | 223.2 | 454.4352
6347 | R-22 | 109.1 | 238.2 | 223.5 | 455.046
6348 | R-22 | 109.2 | 238.5 | 223.8 | 455.6568
6349 | R-22 | 109.3 | 238.8 | 224.1 | 456.2676
6350 | R-22 | 109.4 | 239.1 | 224.4 | 456.8784
6351 | R-22 | 109.5 | 239.5 | 224.8 | 457.6928
6352 | R-22 | 109.6 | 239.8 | 225.1 | 458.3036
6353 | R-22 | 109.7 | 240.1 | 225.4 | 458.9144
6354 | R-22 | 109.8 | 240.4 | 225.7 | 459.5252
6355 | R-22 | 109.9 | 240.7 | 226 | 460.136
6356 | R-22 | 110 | 241.1 | 226.4 | 460.9504
6357 | R-22 | 110.1 | 241.4 | 226.7 | 461.5612
6358 | R-22 | 110.2 | 241.7 | 227 | 462.172
6359 | R-22 | 110.3 | 242 | 227.3 | 462.7828
6360 | R-22 | 110.4 | 242.3 | 227.6 | 463.3936
6361 | R-22 | 110.5 | 242.7 | 228 | 464.208
6362 | R-22 | 110.6 | 243 | 228.3 | 464.8188
6363 | R-22 | 110.7 | 243.3 | 228.6 | 465.4296
6364 | R-22 | 110.8 | 243.6 | 228.9 | 466.0404
6365 | R-22 | 110.9 | 244 | 229.3 | 466.8548
6366 | R-22 | 111 | 244.3 | 229.6 | 467.4656
6367 | R-22 | 111.1 | 244.6 | 229.9 | 468.0764
6368 | R-22 | 111.2 | 244.9 | 230.2 | 468.6872
6369 | R-22 | 111.3 | 245.2 | 230.5 | 469.298
6370 | R-22 | 111.4 | 245.6 | 230.9 | 470.1124
6371 | R-22 | 111.5 | 245.9 | 231.2 | 470.7232
6372 | R-22 | 111.6 | 246.2 | 231.5 | 471.334
6373 | R-22 | 111.7 | 246.5 | 231.8 | 471.9448
6374 | R-22 | 111.8 | 246.9 | 232.2 | 472.7592
6375 | R-22 | 111.9 | 247.2 | 232.5 | 473.37
6376 | R-22 | 112 | 247.5 | 232.8 | 473.9808
6377 | R-22 | 112.1 | 247.8 | 233.1 | 474.5916
6378 | R-22 | 112.2 | 248.2 | 233.5 | 475.406
6379 | R-22 | 112.3 | 248.5 | 233.8 | 476.0168
6380 | R-22 | 112.4 | 248.8 | 234.1 | 476.6276
6381 | R-22 | 112.5 | 249.2 | 234.5 | 477.442
6382 | R-22 | 112.6 | 249.5 | 234.8 | 478.0528
6383 | R-22 | 112.7 | 249.8 | 235.1 | 478.6636
6384 | R-22 | 112.8 | 250.1 | 235.4 | 479.2744
6385 | R-22 | 112.9 | 250.5 | 235.8 | 480.0888
6386 | R-22 | 113 | 250.8 | 236.1 | 480.6996
6387 | R-22 | 113.1 | 251.1 | 236.4 | 481.3104
6388 | R-22 | 113.2 | 251.5 | 236.8 | 482.1248
6389 | R-22 | 113.3 | 251.8 | 237.1 | 482.7356
6390 | R-22 | 113.4 | 252.1 | 237.4 | 483.3464
6391 | R-22 | 113.5 | 252.5 | 237.8 | 484.1608
6392 | R-22 | 113.6 | 252.8 | 238.1 | 484.7716
6393 | R-22 | 113.7 | 253.1 | 238.4 | 485.3824
6394 | R-22 | 113.8 | 253.4 | 238.7 | 485.9932
6395 | R-22 | 113.9 | 253.8 | 239.1 | 486.8076
6396 | R-22 | 114 | 254.1 | 239.4 | 487.4184
6397 | R-22 | 114.1 | 254.4 | 239.7 | 488.0292
6398 | R-22 | 114.2 | 254.8 | 240.1 | 488.8436
6399 | R-22 | 114.3 | 255.1 | 240.4 | 489.4544
6400 | R-22 | 114.4 | 255.4 | 240.7 | 490.0652
6401 | R-22 | 114.5 | 255.8 | 241.1 | 490.8796
6402 | R-22 | 114.6 | 256.1 | 241.4 | 491.4904
6403 | R-22 | 114.7 | 256.4 | 241.7 | 492.1012
6404 | R-22 | 114.8 | 256.8 | 242.1 | 492.9156
6405 | R-22 | 114.9 | 257.1 | 242.4 | 493.5264
6406 | R-22 | 115 | 257.5 | 242.8 | 494.3408
6407 | R-22 | 115.1 | 257.8 | 243.1 | 494.9516
6408 | R-22 | 115.2 | 258.1 | 243.4 | 495.5624
6409 | R-22 | 115.3 | 258.5 | 243.8 | 496.3768
6410 | R-22 | 115.4 | 258.8 | 244.1 | 496.9876
6411 | R-22 | 115.5 | 259.1 | 244.4 | 497.5984
6412 | R-22 | 115.6 | 259.5 | 244.8 | 498.4128
6413 | R-22 | 115.7 | 259.8 | 245.1 | 499.0236
6414 | R-22 | 115.8 | 260.1 | 245.4 | 499.6344
6415 | R-22 | 115.9 | 260.5 | 245.8 | 500.4488
6416 | R-22 | 116 | 260.8 | 246.1 | 501.0596
6417 | R-22 | 116.1 | 261.2 | 246.5 | 501.874
6418 | R-22 | 116.2 | 261.5 | 246.8 | 502.4848
6419 | R-22 | 116.3 | 261.8 | 247.1 | 503.0956
6420 | R-22 | 116.4 | 262.2 | 247.5 | 503.91
6421 | R-22 | 116.5 | 262.5 | 247.8 | 504.5208
6422 | R-22 | 116.6 | 262.9 | 248.2 | 505.3352
6423 | R-22 | 116.7 | 263.2 | 248.5 | 505.946
6424 | R-22 | 116.8 | 263.5 | 248.8 | 506.5568
6425 | R-22 | 116.9 | 263.9 | 249.2 | 507.3712
6426 | R-22 | 117 | 264.2 | 249.5 | 507.982
6427 | R-22 | 117.1 | 264.6 | 249.9 | 508.7964
6428 | R-22 | 117.2 | 264.9 | 250.2 | 509.4072
6429 | R-22 | 117.3 | 265.3 | 250.6 | 510.2216
6430 | R-22 | 117.4 | 265.6 | 250.9 | 510.8324
6431 | R-22 | 117.5 | 265.9 | 251.2 | 511.4432
6432 | R-22 | 117.6 | 266.3 | 251.6 | 512.2576
6433 | R-22 | 117.7 | 266.6 | 251.9 | 512.8684
6434 | R-22 | 117.8 | 267 | 252.3 | 513.6828
6435 | R-22 | 117.9 | 267.3 | 252.6 | 514.2936
6436 | R-22 | 118 | 267.7 | 253 | 515.108
6437 | R-22 | 118.1 | 268 | 253.3 | 515.7188
6438 | R-22 | 118.2 | 268.4 | 253.7 | 516.5332
6439 | R-22 | 118.3 | 268.7 | 254 | 517.144
6440 | R-22 | 118.4 | 269.1 | 254.4 | 517.9584
6441 | R-22 | 118.5 | 269.4 | 254.7 | 518.5692
6442 | R-22 | 118.6 | 269.8 | 255.1 | 519.3836
6443 | R-22 | 118.7 | 270.1 | 255.4 | 519.9944
6444 | R-22 | 118.8 | 270.4 | 255.7 | 520.6052
6445 | R-22 | 118.9 | 270.8 | 256.1 | 521.4196
6446 | R-22 | 119 | 271.1 | 256.4 | 522.0304
6447 | R-22 | 119.1 | 271.5 | 256.8 | 522.8448
6448 | R-22 | 119.2 | 271.8 | 257.1 | 523.4556
6449 | R-22 | 119.3 | 272.2 | 257.5 | 524.27
6450 | R-22 | 119.4 | 272.5 | 257.8 | 524.8808
6451 | R-22 | 119.5 | 272.9 | 258.2 | 525.6952
6452 | R-22 | 119.6 | 273.2 | 258.5 | 526.306
6453 | R-22 | 119.7 | 273.6 | 258.9 | 527.1204
6454 | R-22 | 119.8 | 273.9 | 259.2 | 527.7312
6455 | R-22 | 119.9 | 274.3 | 259.6 | 528.5456
6456 | R-22 | 120 | 274.7 | 260 | 529.36
6457 | R-500 | 10 | 34.62 | 19.92 | 40.5571
6458 | R-500 | 10.1 | 34.69 | 19.99 | 40.6996
6459 | R-500 | 10.2 | 34.76 | 20.06 | 40.8422
6460 | R-500 | 10.3 | 34.83 | 20.13 | 40.9847
6461 | R-500 | 10.4 | 34.9 | 20.2 | 41.1272
6462 | R-500 | 10.5 | 34.97 | 20.27 | 41.2697
6463 | R-500 | 10.6 | 35.04 | 20.34 | 41.4122
6464 | R-500 | 10.7 | 35.11 | 20.41 | 41.5548
6465 | R-500 | 10.8 | 35.18 | 20.48 | 41.6973
6466 | R-500 | 10.9 | 35.25 | 20.55 | 41.8398
6467 | R-500 | 11 | 35.32 | 20.62 | 41.9823
6468 | R-500 | 11.1 | 35.39 | 20.69 | 42.1248
6469 | R-500 | 11.2 | 35.47 | 20.77 | 42.2877
6470 | R-500 | 11.3 | 35.54 | 20.84 | 42.4302
6471 | R-500 | 11.4 | 35.61 | 20.91 | 42.5728
6472 | R-500 | 11.5 | 35.68 | 20.98 | 42.7153
6473 | R-500 | 11.6 | 35.75 | 21.05 | 42.8578
6474 | R-500 | 11.7 | 35.82 | 21.12 | 43.0003
6475 | R-500 | 11.8 | 35.9 | 21.2 | 43.1632
6476 | R-500 | 11.9 | 35.97 | 21.27 | 43.3057
6477 | R-500 | 12 | 36.04 | 21.34 | 43.4482
6478 | R-500 | 12.1 | 36.11 | 21.41 | 43.5908
6479 | R-500 | 12.2 | 36.18 | 21.48 | 43.7333
6480 | R-500 | 12.3 | 36.26 | 21.56 | 43.8962
6481 | R-500 | 12.4 | 36.33 | 21.63 | 44.0387
6482 | R-500 | 12.5 | 36.4 | 21.7 | 44.1812
6483 | R-500 | 12.6 | 36.48 | 21.78 | 44.3441
6484 | R-500 | 12.7 | 36.55 | 21.85 | 44.4866
6485 | R-500 | 12.8 | 36.62 | 21.92 | 44.6291
6486 | R-500 | 12.9 | 36.69 | 21.99 | 44.7716
6487 | R-500 | 13 | 36.77 | 22.07 | 44.9345
6488 | R-500 | 13.1 | 36.84 | 22.14 | 45.077
6489 | R-500 | 13.2 | 36.91 | 22.21 | 45.2196
6490 | R-500 | 13.3 | 36.99 | 22.29 | 45.3824
6491 | R-500 | 13.4 | 37.06 | 22.36 | 45.525
6492 | R-500 | 13.5 | 37.14 | 22.44 | 45.6878
6493 | R-500 | 13.6 | 37.21 | 22.51 | 45.8304
6494 | R-500 | 13.7 | 37.28 | 22.58 | 45.9729
6495 | R-500 | 13.8 | 37.36 | 22.66 | 46.1358
6496 | R-500 | 13.9 | 37.43 | 22.73 | 46.2783
6497 | R-500 | 14 | 37.51 | 22.81 | 46.4412
6498 | R-500 | 14.1 | 37.58 | 22.88 | 46.5837
6499 | R-500 | 14.2 | 37.66 | 22.96 | 46.7466
6500 | R-500 | 14.3 | 37.73 | 23.03 | 46.8891
6501 | R-500 | 14.4 | 37.81 | 23.11 | 47.052
6502 | R-500 | 14.5 | 37.88 | 23.18 | 47.1945
6503 | R-500 | 14.6 | 37.96 | 23.26 | 47.3574
6504 | R-500 | 14.7 | 38.03 | 23.33 | 47.4999
6505 | R-500 | 14.8 | 38.11 | 23.41 | 47.6628
6506 | R-500 | 14.9 | 38.18 | 23.48 | 47.8053
6507 | R-500 | 15 | 38.26 | 23.56 | 47.9682
6508 | R-500 | 15.1 | 38.33 | 23.63 | 48.1107
6509 | R-500 | 15.2 | 38.41 | 23.71 | 48.2736
6510 | R-500 | 15.3 | 38.48 | 23.78 | 48.4161
6511 | R-500 | 15.4 | 38.56 | 23.86 | 48.579
6512 | R-500 | 15.5 | 38.64 | 23.94 | 48.7418
6513 | R-500 | 15.6 | 38.71 | 24.01 | 48.8844
6514 | R-500 | 15.7 | 38.79 | 24.09 | 49.0472
6515 | R-500 | 15.8 | 38.86 | 24.16 | 49.1898
6516 | R-500 | 15.9 | 38.94 | 24.24 | 49.3526
6517 | R-500 | 16 | 39.02 | 24.32 | 49.5155
6518 | R-500 | 16.1 | 39.09 | 24.39 | 49.658
6519 | R-500 | 16.2 | 39.17 | 24.47 | 49.8209
6520 | R-500 | 16.3 | 39.25 | 24.55 | 49.9838
6521 | R-500 | 16.4 | 39.33 | 24.63 | 50.1467
6522 | R-500 | 16.5 | 39.4 | 24.7 | 50.2892
6523 | R-500 | 16.6 | 39.48 | 24.78 | 50.4521
6524 | R-500 | 16.7 | 39.56 | 24.86 | 50.615
6525 | R-500 | 16.8 | 39.64 | 24.94 | 50.7778
6526 | R-500 | 16.9 | 39.71 | 25.01 | 50.9204
6527 | R-500 | 17 | 39.79 | 25.09 | 51.0832
6528 | R-500 | 17.1 | 39.87 | 25.17 | 51.2461
6529 | R-500 | 17.2 | 39.95 | 25.25 | 51.409
6530 | R-500 | 17.3 | 40.03 | 25.33 | 51.5719
6531 | R-500 | 17.4 | 40.1 | 25.4 | 51.7144
6532 | R-500 | 17.5 | 40.18 | 25.48 | 51.8773
6533 | R-500 | 17.6 | 40.26 | 25.56 | 52.0402
6534 | R-500 | 17.7 | 40.34 | 25.64 | 52.203
6535 | R-500 | 17.8 | 40.42 | 25.72 | 52.3659
6536 | R-500 | 17.9 | 40.5 | 25.8 | 52.5288
6537 | R-500 | 18 | 40.58 | 25.88 | 52.6917
6538 | R-500 | 18.1 | 40.66 | 25.96 | 52.8546
6539 | R-500 | 18.2 | 40.73 | 26.03 | 52.9971
6540 | R-500 | 18.3 | 40.81 | 26.11 | 53.16
6541 | R-500 | 18.4 | 40.89 | 26.19 | 53.3228
6542 | R-500 | 18.5 | 40.97 | 26.27 | 53.4857
6543 | R-500 | 18.6 | 41.05 | 26.35 | 53.6486
6544 | R-500 | 18.7 | 41.13 | 26.43 | 53.8115
6545 | R-500 | 18.8 | 41.21 | 26.51 | 53.9744
6546 | R-500 | 18.9 | 41.29 | 26.59 | 54.1372
6547 | R-500 | 19 | 41.37 | 26.67 | 54.3001
6548 | R-500 | 19.1 | 41.45 | 26.75 | 54.463
6549 | R-500 | 19.2 | 41.53 | 26.83 | 54.6259
6550 | R-500 | 19.3 | 41.61 | 26.91 | 54.7888
6551 | R-500 | 19.4 | 41.69 | 26.99 | 54.9516
6552 | R-500 | 19.5 | 41.78 | 27.08 | 55.1349
6553 | R-500 | 19.6 | 41.86 | 27.16 | 55.2978
6554 | R-500 | 19.7 | 41.94 | 27.24 | 55.4606
6555 | R-500 | 19.8 | 42.02 | 27.32 | 55.6235
6556 | R-500 | 19.9 | 42.1 | 27.4 | 55.7864
6557 | R-500 | 20 | 42.18 | 27.48 | 55.9493
6558 | R-500 | 20.1 | 42.26 | 27.56 | 56.1122
6559 | R-500 | 20.2 | 42.34 | 27.64 | 56.275
6560 | R-500 | 20.3 | 42.43 | 27.73 | 56.4583
6561 | R-500 | 20.4 | 42.51 | 27.81 | 56.6212
6562 | R-500 | 20.5 | 42.59 | 27.89 | 56.784
6563 | R-500 | 20.6 | 42.67 | 27.97 | 56.9469
6564 | R-500 | 20.7 | 42.75 | 28.05 | 57.1098
6565 | R-500 | 20.8 | 42.84 | 28.14 | 57.293
6566 | R-500 | 20.9 | 42.92 | 28.22 | 57.4559
6567 | R-500 | 21 | 43 | 28.3 | 57.6188
6568 | R-500 | 21.1 | 43.08 | 28.38 | 57.7817
6569 | R-500 | 21.2 | 43.17 | 28.47 | 57.9649
6570 | R-500 | 21.3 | 43.25 | 28.55 | 58.1278
6571 | R-500 | 21.4 | 43.33 | 28.63 | 58.2907
6572 | R-500 | 21.5 | 43.42 | 28.72 | 58.4739
6573 | R-500 | 21.6 | 43.5 | 28.8 | 58.6368
6574 | R-500 | 21.7 | 43.58 | 28.88 | 58.7997
6575 | R-500 | 21.8 | 43.67 | 28.97 | 58.9829
6576 | R-500 | 21.9 | 43.75 | 29.05 | 59.1458
6577 | R-500 | 22 | 43.83 | 29.13 | 59.3087
6578 | R-500 | 22.1 | 43.92 | 29.22 | 59.4919
6579 | R-500 | 22.2 | 44 | 29.3 | 59.6548
6580 | R-500 | 22.3 | 44.09 | 29.39 | 59.838
6581 | R-500 | 22.4 | 44.17 | 29.47 | 60.0009
6582 | R-500 | 22.5 | 44.25 | 29.55 | 60.1638
6583 | R-500 | 22.6 | 44.34 | 29.64 | 60.347
6584 | R-500 | 22.7 | 44.42 | 29.72 | 60.5099
6585 | R-500 | 22.8 | 44.51 | 29.81 | 60.6932
6586 | R-500 | 22.9 | 44.59 | 29.89 | 60.856
6587 | R-500 | 23 | 44.68 | 29.98 | 61.0393
6588 | R-500 | 23.1 | 44.76 | 30.06 | 61.2022
6589 | R-500 | 23.2 | 44.85 | 30.15 | 61.3854
6590 | R-500 | 23.3 | 44.93 | 30.23 | 61.5483
6591 | R-500 | 23.4 | 45.02 | 30.32 | 61.7315
6592 | R-500 | 23.5 | 45.1 | 30.4 | 61.8944
6593 | R-500 | 23.6 | 45.19 | 30.49 | 62.0776
6594 | R-500 | 23.7 | 45.28 | 30.58 | 62.2609
6595 | R-500 | 23.8 | 45.36 | 30.66 | 62.4238
6596 | R-500 | 23.9 | 45.45 | 30.75 | 62.607
6597 | R-500 | 24 | 45.53 | 30.83 | 62.7699
6598 | R-500 | 24.1 | 45.62 | 30.92 | 62.9531
6599 | R-500 | 24.2 | 45.71 | 31.01 | 63.1364
6600 | R-500 | 24.3 | 45.79 | 31.09 | 63.2992
6601 | R-500 | 24.4 | 45.88 | 31.18 | 63.4825
6602 | R-500 | 24.5 | 45.97 | 31.27 | 63.6657
6603 | R-500 | 24.6 | 46.06 | 31.36 | 63.849
6604 | R-500 | 24.7 | 46.14 | 31.44 | 64.0118
6605 | R-500 | 24.8 | 46.23 | 31.53 | 64.1951
6606 | R-500 | 24.9 | 46.32 | 31.62 | 64.3783
6607 | R-500 | 25 | 46.4 | 31.7 | 64.5412
6608 | R-500 | 25.1 | 46.49 | 31.79 | 64.7244
6609 | R-500 | 25.2 | 46.58 | 31.88 | 64.9077
6610 | R-500 | 25.3 | 46.67 | 31.97 | 65.0909
6611 | R-500 | 25.4 | 46.76 | 32.06 | 65.2742
6612 | R-500 | 25.5 | 46.84 | 32.14 | 65.437
6613 | R-500 | 25.6 | 46.93 | 32.23 | 65.6203
6614 | R-500 | 25.7 | 47.02 | 32.32 | 65.8035
6615 | R-500 | 25.8 | 47.11 | 32.41 | 65.9868
6616 | R-500 | 25.9 | 47.2 | 32.5 | 66.17
6617 | R-500 | 26 | 47.29 | 32.59 | 66.3532
6618 | R-500 | 26.1 | 47.38 | 32.68 | 66.5365
6619 | R-500 | 26.2 | 47.46 | 32.76 | 66.6994
6620 | R-500 | 26.3 | 47.55 | 32.85 | 66.8826
6621 | R-500 | 26.4 | 47.64 | 32.94 | 67.0658
6622 | R-500 | 26.5 | 47.73 | 33.03 | 67.2491
6623 | R-500 | 26.6 | 47.82 | 33.12 | 67.4323
6624 | R-500 | 26.7 | 47.91 | 33.21 | 67.6156
6625 | R-500 | 26.8 | 48 | 33.3 | 67.7988
6626 | R-500 | 26.9 | 48.09 | 33.39 | 67.982
6627 | R-500 | 27 | 48.18 | 33.48 | 68.1653
6628 | R-500 | 27.1 | 48.27 | 33.57 | 68.3485
6629 | R-500 | 27.2 | 48.36 | 33.66 | 68.5318
6630 | R-500 | 27.3 | 48.45 | 33.75 | 68.715
6631 | R-500 | 27.4 | 48.54 | 33.84 | 68.8982
6632 | R-500 | 27.5 | 48.63 | 33.93 | 69.0815
6633 | R-500 | 27.6 | 48.72 | 34.02 | 69.2647
6634 | R-500 | 27.7 | 48.81 | 34.11 | 69.448
6635 | R-500 | 27.8 | 48.91 | 34.21 | 69.6516
6636 | R-500 | 27.9 | 49 | 34.3 | 69.8348
6637 | R-500 | 28 | 49.09 | 34.39 | 70.018
6638 | R-500 | 28.1 | 49.18 | 34.48 | 70.2013
6639 | R-500 | 28.2 | 49.27 | 34.57 | 70.3845
6640 | R-500 | 28.3 | 49.36 | 34.66 | 70.5678
6641 | R-500 | 28.4 | 49.45 | 34.75 | 70.751
6642 | R-500 | 28.5 | 49.55 | 34.85 | 70.9546
6643 | R-500 | 28.6 | 49.64 | 34.94 | 71.1378
6644 | R-500 | 28.7 | 49.73 | 35.03 | 71.3211
6645 | R-500 | 28.8 | 49.82 | 35.12 | 71.5043
6646 | R-500 | 28.9 | 49.92 | 35.22 | 71.7079
6647 | R-500 | 29 | 50.01 | 35.31 | 71.8912
6648 | R-500 | 29.1 | 50.1 | 35.4 | 72.0744
6649 | R-500 | 29.2 | 50.19 | 35.49 | 72.2576
6650 | R-500 | 29.3 | 50.29 | 35.59 | 72.4612
6651 | R-500 | 29.4 | 50.38 | 35.68 | 72.6445
6652 | R-500 | 29.5 | 50.47 | 35.77 | 72.8277
6653 | R-500 | 29.6 | 50.57 | 35.87 | 73.0313
6654 | R-500 | 29.7 | 50.66 | 35.96 | 73.2146
6655 | R-500 | 29.8 | 50.75 | 36.05 | 73.3978
6656 | R-500 | 29.9 | 50.85 | 36.15 | 73.6014
6657 | R-500 | 30 | 50.94 | 36.24 | 73.7846
6658 | R-500 | 30.1 | 51.04 | 36.34 | 73.9882
6659 | R-500 | 30.2 | 51.13 | 36.43 | 74.1715
6660 | R-500 | 30.3 | 51.22 | 36.52 | 74.3547
6661 | R-500 | 30.4 | 51.32 | 36.62 | 74.5583
6662 | R-500 | 30.5 | 51.41 | 36.71 | 74.7416
6663 | R-500 | 30.6 | 51.51 | 36.81 | 74.9452
6664 | R-500 | 30.7 | 51.6 | 36.9 | 75.1284
6665 | R-500 | 30.8 | 51.7 | 37 | 75.332
6666 | R-500 | 30.9 | 51.79 | 37.09 | 75.5152
6667 | R-500 | 31 | 51.89 | 37.19 | 75.7188
6668 | R-500 | 31.1 | 51.98 | 37.28 | 75.9021
6669 | R-500 | 31.2 | 52.08 | 37.38 | 76.1057
6670 | R-500 | 31.3 | 52.17 | 37.47 | 76.2889
6671 | R-500 | 31.4 | 52.27 | 37.57 | 76.4925
6672 | R-500 | 31.5 | 52.37 | 37.67 | 76.6961
6673 | R-500 | 31.6 | 52.46 | 37.76 | 76.8794
6674 | R-500 | 31.7 | 52.56 | 37.86 | 77.083
6675 | R-500 | 31.8 | 52.66 | 37.96 | 77.2866
6676 | R-500 | 31.9 | 52.75 | 38.05 | 77.4698
6677 | R-500 | 32 | 52.85 | 38.15 | 77.6734
6678 | R-500 | 32.1 | 52.94 | 38.24 | 77.8566
6679 | R-500 | 32.2 | 53.04 | 38.34 | 78.0602
6680 | R-500 | 32.3 | 53.14 | 38.44 | 78.2638
6681 | R-500 | 32.4 | 53.24 | 38.54 | 78.4674
6682 | R-500 | 32.5 | 53.33 | 38.63 | 78.6507
6683 | R-500 | 32.6 | 53.43 | 38.73 | 78.8543
6684 | R-500 | 32.7 | 53.53 | 38.83 | 79.0579
6685 | R-500 | 32.8 | 53.63 | 38.93 | 79.2615
6686 | R-500 | 32.9 | 53.72 | 39.02 | 79.4447
6687 | R-500 | 33 | 53.82 | 39.12 | 79.6483
6688 | R-500 | 33.1 | 53.92 | 39.22 | 79.8519
6689 | R-500 | 33.2 | 54.02 | 39.32 | 80.0555
6690 | R-500 | 33.3 | 54.12 | 39.42 | 80.2591
6691 | R-500 | 33.4 | 54.21 | 39.51 | 80.4424
6692 | R-500 | 33.5 | 54.31 | 39.61 | 80.646
6693 | R-500 | 33.6 | 54.41 | 39.71 | 80.8496
6694 | R-500 | 33.7 | 54.51 | 39.81 | 81.0532
6695 | R-500 | 33.8 | 54.61 | 39.91 | 81.2568
6696 | R-500 | 33.9 | 54.71 | 40.01 | 81.4604
6697 | R-500 | 34 | 54.81 | 40.11 | 81.664
6698 | R-500 | 34.1 | 54.91 | 40.21 | 81.8676
6699 | R-500 | 34.2 | 55.01 | 40.31 | 82.0712
6700 | R-500 | 34.3 | 55.11 | 40.41 | 82.2748
6701 | R-500 | 34.4 | 55.21 | 40.51 | 82.4784
6702 | R-500 | 34.5 | 55.31 | 40.61 | 82.682
6703 | R-500 | 34.6 | 55.41 | 40.71 | 82.8856
6704 | R-500 | 34.7 | 55.51 | 40.81 | 83.0892
6705 | R-500 | 34.8 | 55.61 | 40.91 | 83.2928
6706 | R-500 | 34.9 | 55.71 | 41.01 | 83.4964
6707 | R-500 | 35 | 55.81 | 41.11 | 83.7
6708 | R-500 | 35.1 | 55.91 | 41.21 | 83.9036
6709 | R-500 | 35.2 | 56.01 | 41.31 | 84.1072
6710 | R-500 | 35.3 | 56.11 | 41.41 | 84.3108
6711 | R-500 | 35.4 | 56.21 | 41.51 | 84.5144
6712 | R-500 | 35.5 | 56.31 | 41.61 | 84.718
6713 | R-500 | 35.6 | 56.41 | 41.71 | 84.9216
6714 | R-500 | 35.7 | 56.52 | 41.82 | 85.1455
6715 | R-500 | 35.8 | 56.62 | 41.92 | 85.3491
6716 | R-500 | 35.9 | 56.72 | 42.02 | 85.5527
6717 | R-500 | 36 | 56.82 | 42.12 | 85.7563
6718 | R-500 | 36.1 | 56.92 | 42.22 | 85.9599
6719 | R-500 | 36.2 | 57.03 | 42.33 | 86.1839
6720 | R-500 | 36.3 | 57.13 | 42.43 | 86.3875
6721 | R-500 | 36.4 | 57.23 | 42.53 | 86.5911
6722 | R-500 | 36.5 | 57.33 | 42.63 | 86.7947
6723 | R-500 | 36.6 | 57.44 | 42.74 | 87.0186
6724 | R-500 | 36.7 | 57.54 | 42.84 | 87.2222
6725 | R-500 | 36.8 | 57.64 | 42.94 | 87.4258
6726 | R-500 | 36.9 | 57.75 | 43.05 | 87.6498
6727 | R-500 | 37 | 57.85 | 43.15 | 87.8534
6728 | R-500 | 37.1 | 57.95 | 43.25 | 88.057
6729 | R-500 | 37.2 | 58.06 | 43.36 | 88.281
6730 | R-500 | 37.3 | 58.16 | 43.46 | 88.4846
6731 | R-500 | 37.4 | 58.26 | 43.56 | 88.6882
6732 | R-500 | 37.5 | 58.37 | 43.67 | 88.9121
6733 | R-500 | 37.6 | 58.47 | 43.77 | 89.1157
6734 | R-500 | 37.7 | 58.58 | 43.88 | 89.3397
6735 | R-500 | 37.8 | 58.68 | 43.98 | 89.5433
6736 | R-500 | 37.9 | 58.79 | 44.09 | 89.7672
6737 | R-500 | 38 | 58.89 | 44.19 | 89.9708
6738 | R-500 | 38.1 | 59 | 44.3 | 90.1948
6739 | R-500 | 38.2 | 59.1 | 44.4 | 90.3984
6740 | R-500 | 38.3 | 59.21 | 44.51 | 90.6224
6741 | R-500 | 38.4 | 59.31 | 44.61 | 90.826
6742 | R-500 | 38.5 | 59.42 | 44.72 | 91.0499
6743 | R-500 | 38.6 | 59.52 | 44.82 | 91.2535
6744 | R-500 | 38.7 | 59.63 | 44.93 | 91.4775
6745 | R-500 | 38.8 | 59.74 | 45.04 | 91.7014
6746 | R-500 | 38.9 | 59.84 | 45.14 | 91.905
6747 | R-500 | 39 | 59.95 | 45.25 | 92.129
6748 | R-500 | 39.1 | 60.05 | 45.35 | 92.3326
6749 | R-500 | 39.2 | 60.16 | 45.46 | 92.5566
6750 | R-500 | 39.3 | 60.27 | 45.57 | 92.7805
6751 | R-500 | 39.4 | 60.37 | 45.67 | 92.9841
6752 | R-500 | 39.5 | 60.48 | 45.78 | 93.2081
6753 | R-500 | 39.6 | 60.59 | 45.89 | 93.432
6754 | R-500 | 39.7 | 60.7 | 46 | 93.656
6755 | R-500 | 39.8 | 60.8 | 46.1 | 93.8596
6756 | R-500 | 39.9 | 60.91 | 46.21 | 94.0836
6757 | R-500 | 40 | 61.02 | 46.32 | 94.3075
6758 | R-500 | 40.1 | 61.13 | 46.43 | 94.5315
6759 | R-500 | 40.2 | 61.23 | 46.53 | 94.7351
6760 | R-500 | 40.3 | 61.34 | 46.64 | 94.959
6761 | R-500 | 40.4 | 61.45 | 46.75 | 95.183
6762 | R-500 | 40.5 | 61.56 | 46.86 | 95.407
6763 | R-500 | 40.6 | 61.67 | 46.97 | 95.6309
6764 | R-500 | 40.7 | 61.78 | 47.08 | 95.8549
6765 | R-500 | 40.8 | 61.88 | 47.18 | 96.0585
6766 | R-500 | 40.9 | 61.99 | 47.29 | 96.2824
6767 | R-500 | 41 | 62.1 | 47.4 | 96.5064
6768 | R-500 | 41.1 | 62.21 | 47.51 | 96.7304
6769 | R-500 | 41.2 | 62.32 | 47.62 | 96.9543
6770 | R-500 | 41.3 | 62.43 | 47.73 | 97.1783
6771 | R-500 | 41.4 | 62.54 | 47.84 | 97.4022
6772 | R-500 | 41.5 | 62.65 | 47.95 | 97.6262
6773 | R-500 | 41.6 | 62.76 | 48.06 | 97.8502
6774 | R-500 | 41.7 | 62.87 | 48.17 | 98.0741
6775 | R-500 | 41.8 | 62.98 | 48.28 | 98.2981
6776 | R-500 | 41.9 | 63.09 | 48.39 | 98.522
6777 | R-500 | 42 | 63.2 | 48.5 | 98.746
6778 | R-500 | 42.1 | 63.31 | 48.61 | 98.97
6779 | R-500 | 42.2 | 63.42 | 48.72 | 99.1939
6780 | R-500 | 42.3 | 63.53 | 48.83 | 99.4179
6781 | R-500 | 42.4 | 63.64 | 48.94 | 99.6418
6782 | R-500 | 42.5 | 63.76 | 49.06 | 99.8862
6783 | R-500 | 42.6 | 63.87 | 49.17 | 100.1101
6784 | R-500 | 42.7 | 63.98 | 49.28 | 100.3341
6785 | R-500 | 42.8 | 64.09 | 49.39 | 100.558
6786 | R-500 | 42.9 | 64.2 | 49.5 | 100.782
6787 | R-500 | 43 | 64.31 | 49.61 | 101.006
6788 | R-500 | 43.1 | 64.43 | 49.73 | 101.2503
6789 | R-500 | 43.2 | 64.54 | 49.84 | 101.4742
6790 | R-500 | 43.3 | 64.65 | 49.95 | 101.6982
6791 | R-500 | 43.4 | 64.76 | 50.06 | 101.9222
6792 | R-500 | 43.5 | 64.88 | 50.18 | 102.1665
6793 | R-500 | 43.6 | 64.99 | 50.29 | 102.3904
6794 | R-500 | 43.7 | 65.1 | 50.4 | 102.6144
6795 | R-500 | 43.8 | 65.22 | 50.52 | 102.8587
6796 | R-500 | 43.9 | 65.33 | 50.63 | 103.0827
6797 | R-500 | 44 | 65.44 | 50.74 | 103.3066
6798 | R-500 | 44.1 | 65.56 | 50.86 | 103.551
6799 | R-500 | 44.2 | 65.67 | 50.97 | 103.7749
6800 | R-500 | 44.3 | 65.78 | 51.08 | 103.9989
6801 | R-500 | 44.4 | 65.9 | 51.2 | 104.2432
6802 | R-500 | 44.5 | 66.01 | 51.31 | 104.4672
6803 | R-500 | 44.6 | 66.13 | 51.43 | 104.7115
6804 | R-500 | 44.7 | 66.24 | 51.54 | 104.9354
6805 | R-500 | 44.8 | 66.36 | 51.66 | 105.1798
6806 | R-500 | 44.9 | 66.47 | 51.77 | 105.4037
6807 | R-500 | 45 | 66.59 | 51.89 | 105.648
6808 | R-500 | 45.1 | 66.7 | 52 | 105.872
6809 | R-500 | 45.2 | 66.82 | 52.12 | 106.1163
6810 | R-500 | 45.3 | 66.93 | 52.23 | 106.3403
6811 | R-500 | 45.4 | 67.05 | 52.35 | 106.5846
6812 | R-500 | 45.5 | 67.16 | 52.46 | 106.8086
6813 | R-500 | 45.6 | 67.28 | 52.58 | 107.0529
6814 | R-500 | 45.7 | 67.39 | 52.69 | 107.2768
6815 | R-500 | 45.8 | 67.51 | 52.81 | 107.5212
6816 | R-500 | 45.9 | 67.63 | 52.93 | 107.7655
6817 | R-500 | 46 | 67.74 | 53.04 | 107.9894
6818 | R-500 | 46.1 | 67.86 | 53.16 | 108.2338
6819 | R-500 | 46.2 | 67.98 | 53.28 | 108.4781
6820 | R-500 | 46.3 | 68.09 | 53.39 | 108.702
6821 | R-500 | 46.4 | 68.21 | 53.51 | 108.9464
6822 | R-500 | 46.5 | 68.33 | 53.63 | 109.1907
6823 | R-500 | 46.6 | 68.45 | 53.75 | 109.435
6824 | R-500 | 46.7 | 68.56 | 53.86 | 109.659
6825 | R-500 | 46.8 | 68.68 | 53.98 | 109.9033
6826 | R-500 | 46.9 | 68.8 | 54.1 | 110.1476
6827 | R-500 | 47 | 68.92 | 54.22 | 110.3919
6828 | R-500 | 47.1 | 69.04 | 54.34 | 110.6362
6829 | R-500 | 47.2 | 69.15 | 54.45 | 110.8602
6830 | R-500 | 47.3 | 69.27 | 54.57 | 111.1045
6831 | R-500 | 47.4 | 69.39 | 54.69 | 111.3488
6832 | R-500 | 47.5 | 69.51 | 54.81 | 111.5932
6833 | R-500 | 47.6 | 69.63 | 54.93 | 111.8375
6834 | R-500 | 47.7 | 69.75 | 55.05 | 112.0818
6835 | R-500 | 47.8 | 69.87 | 55.17 | 112.3261
6836 | R-500 | 47.9 | 69.99 | 55.29 | 112.5704
6837 | R-500 | 48 | 70.11 | 55.41 | 112.8148
6838 | R-500 | 48.1 | 70.22 | 55.52 | 113.0387
6839 | R-500 | 48.2 | 70.34 | 55.64 | 113.283
6840 | R-500 | 48.3 | 70.46 | 55.76 | 113.5274
6841 | R-500 | 48.4 | 70.58 | 55.88 | 113.7717
6842 | R-500 | 48.5 | 70.71 | 56.01 | 114.0364
6843 | R-500 | 48.6 | 70.83 | 56.13 | 114.2807
6844 | R-500 | 48.7 | 70.95 | 56.25 | 114.525
6845 | R-500 | 48.8 | 71.07 | 56.37 | 114.7693
6846 | R-500 | 48.9 | 71.19 | 56.49 | 115.0136
6847 | R-500 | 49 | 71.31 | 56.61 | 115.258
6848 | R-500 | 49.1 | 71.43 | 56.73 | 115.5023
6849 | R-500 | 49.2 | 71.55 | 56.85 | 115.7466
6850 | R-500 | 49.3 | 71.67 | 56.97 | 115.9909
6851 | R-500 | 49.4 | 71.79 | 57.09 | 116.2352
6852 | R-500 | 49.5 | 71.92 | 57.22 | 116.4999
6853 | R-500 | 49.6 | 72.04 | 57.34 | 116.7442
6854 | R-500 | 49.7 | 72.16 | 57.46 | 116.9886
6855 | R-500 | 49.8 | 72.28 | 57.58 | 117.2329
6856 | R-500 | 49.9 | 72.41 | 57.71 | 117.4976
6857 | R-500 | 50 | 72.53 | 57.83 | 117.7419
6858 | R-500 | 50.1 | 72.65 | 57.95 | 117.9862
6859 | R-500 | 50.2 | 72.77 | 58.07 | 118.2305
6860 | R-500 | 50.3 | 72.9 | 58.2 | 118.4952
6861 | R-500 | 50.4 | 73.02 | 58.32 | 118.7395
6862 | R-500 | 50.5 | 73.14 | 58.44 | 118.9838
6863 | R-500 | 50.6 | 73.27 | 58.57 | 119.2485
6864 | R-500 | 50.7 | 73.39 | 58.69 | 119.4928
6865 | R-500 | 50.8 | 73.51 | 58.81 | 119.7372
6866 | R-500 | 50.9 | 73.64 | 58.94 | 120.0018
6867 | R-500 | 51 | 73.76 | 59.06 | 120.2462
6868 | R-500 | 51.1 | 73.89 | 59.19 | 120.5108
6869 | R-500 | 51.2 | 74.01 | 59.31 | 120.7552
6870 | R-500 | 51.3 | 74.14 | 59.44 | 121.0198
6871 | R-500 | 51.4 | 74.26 | 59.56 | 121.2642
6872 | R-500 | 51.5 | 74.39 | 59.69 | 121.5288
6873 | R-500 | 51.6 | 74.51 | 59.81 | 121.7732
6874 | R-500 | 51.7 | 74.64 | 59.94 | 122.0378
6875 | R-500 | 51.8 | 74.76 | 60.06 | 122.2822
6876 | R-500 | 51.9 | 74.89 | 60.19 | 122.5468
6877 | R-500 | 52 | 75.01 | 60.31 | 122.7912
6878 | R-500 | 52.1 | 75.14 | 60.44 | 123.0558
6879 | R-500 | 52.2 | 75.27 | 60.57 | 123.3205
6880 | R-500 | 52.3 | 75.39 | 60.69 | 123.5648
6881 | R-500 | 52.4 | 75.52 | 60.82 | 123.8295
6882 | R-500 | 52.5 | 75.64 | 60.94 | 124.0738
6883 | R-500 | 52.6 | 75.77 | 61.07 | 124.3385
6884 | R-500 | 52.7 | 75.9 | 61.2 | 124.6032
6885 | R-500 | 52.8 | 76.02 | 61.32 | 124.8475
6886 | R-500 | 52.9 | 76.15 | 61.45 | 125.1122
6887 | R-500 | 53 | 76.28 | 61.58 | 125.3769
6888 | R-500 | 53.1 | 76.41 | 61.71 | 125.6416
6889 | R-500 | 53.2 | 76.53 | 61.83 | 125.8859
6890 | R-500 | 53.3 | 76.66 | 61.96 | 126.1506
6891 | R-500 | 53.4 | 76.79 | 62.09 | 126.4152
6892 | R-500 | 53.5 | 76.92 | 62.22 | 126.6799
6893 | R-500 | 53.6 | 77.05 | 62.35 | 126.9446
6894 | R-500 | 53.7 | 77.18 | 62.48 | 127.2093
6895 | R-500 | 53.8 | 77.3 | 62.6 | 127.4536
6896 | R-500 | 53.9 | 77.43 | 62.73 | 127.7183
6897 | R-500 | 54 | 77.56 | 62.86 | 127.983
6898 | R-500 | 54.1 | 77.69 | 62.99 | 128.2476
6899 | R-500 | 54.2 | 77.82 | 63.12 | 128.5123
6900 | R-500 | 54.3 | 77.95 | 63.25 | 128.777
6901 | R-500 | 54.4 | 78.08 | 63.38 | 129.0417
6902 | R-500 | 54.5 | 78.21 | 63.51 | 129.3064
6903 | R-500 | 54.6 | 78.34 | 63.64 | 129.571
6904 | R-500 | 54.7 | 78.47 | 63.77 | 129.8357
6905 | R-500 | 54.8 | 78.6 | 63.9 | 130.1004
6906 | R-500 | 54.9 | 78.73 | 64.03 | 130.3651
6907 | R-500 | 55 | 78.86 | 64.16 | 130.6298
6908 | R-500 | 55.1 | 78.99 | 64.29 | 130.8944
6909 | R-500 | 55.2 | 79.12 | 64.42 | 131.1591
6910 | R-500 | 55.3 | 79.25 | 64.55 | 131.4238
6911 | R-500 | 55.4 | 79.38 | 64.68 | 131.6885
6912 | R-500 | 55.5 | 79.52 | 64.82 | 131.9735
6913 | R-500 | 55.6 | 79.65 | 64.95 | 132.2382
6914 | R-500 | 55.7 | 79.78 | 65.08 | 132.5029
6915 | R-500 | 55.8 | 79.91 | 65.21 | 132.7676
6916 | R-500 | 55.9 | 80.04 | 65.34 | 133.0322
6917 | R-500 | 56 | 80.17 | 65.47 | 133.2969
6918 | R-500 | 56.1 | 80.31 | 65.61 | 133.582
6919 | R-500 | 56.2 | 80.44 | 65.74 | 133.8466
6920 | R-500 | 56.3 | 80.57 | 65.87 | 134.1113
6921 | R-500 | 56.4 | 80.7 | 66 | 134.376
6922 | R-500 | 56.5 | 80.84 | 66.14 | 134.661
6923 | R-500 | 56.6 | 80.97 | 66.27 | 134.9257
6924 | R-500 | 56.7 | 81.1 | 66.4 | 135.1904
6925 | R-500 | 56.8 | 81.24 | 66.54 | 135.4754
6926 | R-500 | 56.9 | 81.37 | 66.67 | 135.7401
6927 | R-500 | 57 | 81.51 | 66.81 | 136.0252
6928 | R-500 | 57.1 | 81.64 | 66.94 | 136.2898
6929 | R-500 | 57.2 | 81.77 | 67.07 | 136.5545
6930 | R-500 | 57.3 | 81.91 | 67.21 | 136.8396
6931 | R-500 | 57.4 | 82.04 | 67.34 | 137.1042
6932 | R-500 | 57.5 | 82.18 | 67.48 | 137.3893
6933 | R-500 | 57.6 | 82.31 | 67.61 | 137.654
6934 | R-500 | 57.7 | 82.45 | 67.75 | 137.939
6935 | R-500 | 57.8 | 82.58 | 67.88 | 138.2037
6936 | R-500 | 57.9 | 82.72 | 68.02 | 138.4887
6937 | R-500 | 58 | 82.85 | 68.15 | 138.7534
6938 | R-500 | 58.1 | 82.99 | 68.29 | 139.0384
6939 | R-500 | 58.2 | 83.12 | 68.42 | 139.3031
6940 | R-500 | 58.3 | 83.26 | 68.56 | 139.5882
6941 | R-500 | 58.4 | 83.4 | 68.7 | 139.8732
6942 | R-500 | 58.5 | 83.53 | 68.83 | 140.1379
6943 | R-500 | 58.6 | 83.67 | 68.97 | 140.4229
6944 | R-500 | 58.7 | 83.81 | 69.11 | 140.708
6945 | R-500 | 58.8 | 83.94 | 69.24 | 140.9726
6946 | R-500 | 58.9 | 84.08 | 69.38 | 141.2577
6947 | R-500 | 59 | 84.22 | 69.52 | 141.5427
6948 | R-500 | 59.1 | 84.35 | 69.65 | 141.8074
6949 | R-500 | 59.2 | 84.49 | 69.79 | 142.0924
6950 | R-500 | 59.3 | 84.63 | 69.93 | 142.3775
6951 | R-500 | 59.4 | 84.77 | 70.07 | 142.6625
6952 | R-500 | 59.5 | 84.9 | 70.2 | 142.9272
6953 | R-500 | 59.6 | 85.04 | 70.34 | 143.2122
6954 | R-500 | 59.7 | 85.18 | 70.48 | 143.4973
6955 | R-500 | 59.8 | 85.32 | 70.62 | 143.7823
6956 | R-500 | 59.9 | 85.46 | 70.76 | 144.0674
6957 | R-500 | 60 | 85.6 | 70.9 | 144.3524
6958 | R-500 | 60.1 | 85.74 | 71.04 | 144.6374
6959 | R-500 | 60.2 | 85.88 | 71.18 | 144.9225
6960 | R-500 | 60.3 | 86.01 | 71.31 | 145.1872
6961 | R-500 | 60.4 | 86.15 | 71.45 | 145.4722
6962 | R-500 | 60.5 | 86.29 | 71.59 | 145.7572
6963 | R-500 | 60.6 | 86.43 | 71.73 | 146.0423
6964 | R-500 | 60.7 | 86.57 | 71.87 | 146.3273
6965 | R-500 | 60.8 | 86.71 | 72.01 | 146.6124
6966 | R-500 | 60.9 | 86.85 | 72.15 | 146.8974
6967 | R-500 | 61 | 86.99 | 72.29 | 147.1824
6968 | R-500 | 61.1 | 87.14 | 72.44 | 147.4878
6969 | R-500 | 61.2 | 87.28 | 72.58 | 147.7729
6970 | R-500 | 61.3 | 87.42 | 72.72 | 148.0579
6971 | R-500 | 61.4 | 87.56 | 72.86 | 148.343
6972 | R-500 | 61.5 | 87.7 | 73 | 148.628
6973 | R-500 | 61.6 | 87.84 | 73.14 | 148.913
6974 | R-500 | 61.7 | 87.98 | 73.28 | 149.1981
6975 | R-500 | 61.8 | 88.12 | 73.42 | 149.4831
6976 | R-500 | 61.9 | 88.27 | 73.57 | 149.7885
6977 | R-500 | 62 | 88.41 | 73.71 | 150.0736
6978 | R-500 | 62.1 | 88.55 | 73.85 | 150.3586
6979 | R-500 | 62.2 | 88.69 | 73.99 | 150.6436
6980 | R-500 | 62.3 | 88.84 | 74.14 | 150.949
6981 | R-500 | 62.4 | 88.98 | 74.28 | 151.2341
6982 | R-500 | 62.5 | 89.12 | 74.42 | 151.5191
6983 | R-500 | 62.6 | 89.27 | 74.57 | 151.8245
6984 | R-500 | 62.7 | 89.41 | 74.71 | 152.1096
6985 | R-500 | 62.8 | 89.55 | 74.85 | 152.3946
6986 | R-500 | 62.9 | 89.7 | 75 | 152.7
6987 | R-500 | 63 | 89.84 | 75.14 | 152.985
6988 | R-500 | 63.1 | 89.98 | 75.28 | 153.2701
6989 | R-500 | 63.2 | 90.13 | 75.43 | 153.5755
6990 | R-500 | 63.3 | 90.27 | 75.57 | 153.8605
6991 | R-500 | 63.4 | 90.42 | 75.72 | 154.1659
6992 | R-500 | 63.5 | 90.56 | 75.86 | 154.451
6993 | R-500 | 63.6 | 90.71 | 76.01 | 154.7564
6994 | R-500 | 63.7 | 90.85 | 76.15 | 155.0414
6995 | R-500 | 63.8 | 91 | 76.3 | 155.3468
6996 | R-500 | 63.9 | 91.14 | 76.44 | 155.6318
6997 | R-500 | 64 | 91.29 | 76.59 | 155.9372
6998 | R-500 | 64.1 | 91.44 | 76.74 | 156.2426
6999 | R-500 | 64.2 | 91.58 | 76.88 | 156.5277
7000 | R-500 | 64.3 | 91.73 | 77.03 | 156.8331
7001 | R-500 | 64.4 | 91.87 | 77.17 | 157.1181
7002 | R-500 | 64.5 | 92.02 | 77.32 | 157.4235
7003 | R-500 | 64.6 | 92.17 | 77.47 | 157.7289
7004 | R-500 | 64.7 | 92.31 | 77.61 | 158.014
7005 | R-500 | 64.8 | 92.46 | 77.76 | 158.3194
7006 | R-500 | 64.9 | 92.61 | 77.91 | 158.6248
7007 | R-500 | 65 | 92.76 | 78.06 | 158.9302
7008 | R-500 | 65.1 | 92.9 | 78.2 | 159.2152
7009 | R-500 | 65.2 | 93.05 | 78.35 | 159.5206
7010 | R-500 | 65.3 | 93.2 | 78.5 | 159.826
7011 | R-500 | 65.4 | 93.35 | 78.65 | 160.1314
7012 | R-500 | 65.5 | 93.5 | 78.8 | 160.4368
7013 | R-500 | 65.6 | 93.64 | 78.94 | 160.7218
7014 | R-500 | 65.7 | 93.79 | 79.09 | 161.0272
7015 | R-500 | 65.8 | 93.94 | 79.24 | 161.3326
7016 | R-500 | 65.9 | 94.09 | 79.39 | 161.638
7017 | R-500 | 66 | 94.24 | 79.54 | 161.9434
7018 | R-500 | 66.1 | 94.39 | 79.69 | 162.2488
7019 | R-500 | 66.2 | 94.54 | 79.84 | 162.5542
7020 | R-500 | 66.3 | 94.69 | 79.99 | 162.8596
7021 | R-500 | 66.4 | 94.84 | 80.14 | 163.165
7022 | R-500 | 66.5 | 94.99 | 80.29 | 163.4704
7023 | R-500 | 66.6 | 95.14 | 80.44 | 163.7758
7024 | R-500 | 66.7 | 95.29 | 80.59 | 164.0812
7025 | R-500 | 66.8 | 95.44 | 80.74 | 164.3866
7026 | R-500 | 66.9 | 95.59 | 80.89 | 164.692
7027 | R-500 | 67 | 95.74 | 81.04 | 164.9974
7028 | R-500 | 67.1 | 95.89 | 81.19 | 165.3028
7029 | R-500 | 67.2 | 96.04 | 81.34 | 165.6082
7030 | R-500 | 67.3 | 96.19 | 81.49 | 165.9136
7031 | R-500 | 67.4 | 96.35 | 81.65 | 166.2394
7032 | R-500 | 67.5 | 96.5 | 81.8 | 166.5448
7033 | R-500 | 67.6 | 96.65 | 81.95 | 166.8502
7034 | R-500 | 67.7 | 96.8 | 82.1 | 167.1556
7035 | R-500 | 67.8 | 96.95 | 82.25 | 167.461
7036 | R-500 | 67.9 | 97.11 | 82.41 | 167.7868
7037 | R-500 | 68 | 97.26 | 82.56 | 168.0922
7038 | R-500 | 68.1 | 97.41 | 82.71 | 168.3976
7039 | R-500 | 68.2 | 97.57 | 82.87 | 168.7233
7040 | R-500 | 68.3 | 97.72 | 83.02 | 169.0287
7041 | R-500 | 68.4 | 97.87 | 83.17 | 169.3341
7042 | R-500 | 68.5 | 98.03 | 83.33 | 169.6599
7043 | R-500 | 68.6 | 98.18 | 83.48 | 169.9653
7044 | R-500 | 68.7 | 98.33 | 83.63 | 170.2707
7045 | R-500 | 68.8 | 98.49 | 83.79 | 170.5964
7046 | R-500 | 68.9 | 98.64 | 83.94 | 170.9018
7047 | R-500 | 69 | 98.8 | 84.1 | 171.2276
7048 | R-500 | 69.1 | 98.95 | 84.25 | 171.533
7049 | R-500 | 69.2 | 99.11 | 84.41 | 171.8588
7050 | R-500 | 69.3 | 99.26 | 84.56 | 172.1642
7051 | R-500 | 69.4 | 99.42 | 84.72 | 172.4899
7052 | R-500 | 69.5 | 99.57 | 84.87 | 172.7953
7053 | R-500 | 69.6 | 99.73 | 85.03 | 173.1211
7054 | R-500 | 69.7 | 99.88 | 85.18 | 173.4265
7055 | R-500 | 69.8 | 100 | 85.3 | 173.6708
7056 | R-500 | 69.9 | 100.2 | 85.5 | 174.078
7057 | R-500 | 70 | 100.4 | 85.7 | 174.4852
7058 | R-500 | 70.1 | 100.5 | 85.8 | 174.6888
7059 | R-500 | 70.2 | 100.7 | 86 | 175.096
7060 | R-500 | 70.3 | 100.8 | 86.1 | 175.2996
7061 | R-500 | 70.4 | 101 | 86.3 | 175.7068
7062 | R-500 | 70.5 | 101.1 | 86.4 | 175.9104
7063 | R-500 | 70.6 | 101.3 | 86.6 | 176.3176
7064 | R-500 | 70.7 | 101.5 | 86.8 | 176.7248
7065 | R-500 | 70.8 | 101.6 | 86.9 | 176.9284
7066 | R-500 | 70.9 | 101.8 | 87.1 | 177.3356
7067 | R-500 | 71 | 101.9 | 87.2 | 177.5392
7068 | R-500 | 71.1 | 102.1 | 87.4 | 177.9464
7069 | R-500 | 71.2 | 102.2 | 87.5 | 178.15
7070 | R-500 | 71.3 | 102.4 | 87.7 | 178.5572
7071 | R-500 | 71.4 | 102.6 | 87.9 | 178.9644
7072 | R-500 | 71.5 | 102.7 | 88 | 179.168
7073 | R-500 | 71.6 | 102.9 | 88.2 | 179.5752
7074 | R-500 | 71.7 | 103 | 88.3 | 179.7788
7075 | R-500 | 71.8 | 103.2 | 88.5 | 180.186
7076 | R-500 | 71.9 | 103.4 | 88.7 | 180.5932
7077 | R-500 | 72 | 103.5 | 88.8 | 180.7968
7078 | R-500 | 72.1 | 103.7 | 89 | 181.204
7079 | R-500 | 72.2 | 103.8 | 89.1 | 181.4076
7080 | R-500 | 72.3 | 104 | 89.3 | 181.8148
7081 | R-500 | 72.4 | 104.2 | 89.5 | 182.222
7082 | R-500 | 72.5 | 104.3 | 89.6 | 182.4256
7083 | R-500 | 72.6 | 104.5 | 89.8 | 182.8328
7084 | R-500 | 72.7 | 104.6 | 89.9 | 183.0364
7085 | R-500 | 72.8 | 104.8 | 90.1 | 183.4436
7086 | R-500 | 72.9 | 105 | 90.3 | 183.8508
7087 | R-500 | 73 | 105.1 | 90.4 | 184.0544
7088 | R-500 | 73.1 | 105.3 | 90.6 | 184.4616
7089 | R-500 | 73.2 | 105.5 | 90.8 | 184.8688
7090 | R-500 | 73.3 | 105.6 | 90.9 | 185.0724
7091 | R-500 | 73.4 | 105.8 | 91.1 | 185.4796
7092 | R-500 | 73.5 | 105.9 | 91.2 | 185.6832
7093 | R-500 | 73.6 | 106.1 | 91.4 | 186.0904
7094 | R-500 | 73.7 | 106.3 | 91.6 | 186.4976
7095 | R-500 | 73.8 | 106.4 | 91.7 | 186.7012
7096 | R-500 | 73.9 | 106.6 | 91.9 | 187.1084
7097 | R-500 | 74 | 106.8 | 92.1 | 187.5156
7098 | R-500 | 74.1 | 106.9 | 92.2 | 187.7192
7099 | R-500 | 74.2 | 107.1 | 92.4 | 188.1264
7100 | R-500 | 74.3 | 107.2 | 92.5 | 188.33
7101 | R-500 | 74.4 | 107.4 | 92.7 | 188.7372
7102 | R-500 | 74.5 | 107.6 | 92.9 | 189.1444
7103 | R-500 | 74.6 | 107.7 | 93 | 189.348
7104 | R-500 | 74.7 | 107.9 | 93.2 | 189.7552
7105 | R-500 | 74.8 | 108.1 | 93.4 | 190.1624
7106 | R-500 | 74.9 | 108.2 | 93.5 | 190.366
7107 | R-500 | 75 | 108.4 | 93.7 | 190.7732
7108 | R-500 | 75.1 | 108.6 | 93.9 | 191.1804
7109 | R-500 | 75.2 | 108.7 | 94 | 191.384
7110 | R-500 | 75.3 | 108.9 | 94.2 | 191.7912
7111 | R-500 | 75.4 | 109.1 | 94.4 | 192.1984
7112 | R-500 | 75.5 | 109.2 | 94.5 | 192.402
7113 | R-500 | 75.6 | 109.4 | 94.7 | 192.8092
7114 | R-500 | 75.7 | 109.6 | 94.9 | 193.2164
7115 | R-500 | 75.8 | 109.7 | 95 | 193.42
7116 | R-500 | 75.9 | 109.9 | 95.2 | 193.8272
7117 | R-500 | 76 | 110.1 | 95.4 | 194.2344
7118 | R-500 | 76.1 | 110.2 | 95.5 | 194.438
7119 | R-500 | 76.2 | 110.4 | 95.7 | 194.8452
7120 | R-500 | 76.3 | 110.6 | 95.9 | 195.2524
7121 | R-500 | 76.4 | 110.7 | 96 | 195.456
7122 | R-500 | 76.5 | 110.9 | 96.2 | 195.8632
7123 | R-500 | 76.6 | 111.1 | 96.4 | 196.2704
7124 | R-500 | 76.7 | 111.2 | 96.5 | 196.474
7125 | R-500 | 76.8 | 111.4 | 96.7 | 196.8812
7126 | R-500 | 76.9 | 111.6 | 96.9 | 197.2884
7127 | R-500 | 77 | 111.8 | 97.1 | 197.6956
7128 | R-500 | 77.1 | 111.9 | 97.2 | 197.8992
7129 | R-500 | 77.2 | 112.1 | 97.4 | 198.3064
7130 | R-500 | 77.3 | 112.3 | 97.6 | 198.7136
7131 | R-500 | 77.4 | 112.4 | 97.7 | 198.9172
7132 | R-500 | 77.5 | 112.6 | 97.9 | 199.3244
7133 | R-500 | 77.6 | 112.8 | 98.1 | 199.7316
7134 | R-500 | 77.7 | 112.9 | 98.2 | 199.9352
7135 | R-500 | 77.8 | 113.1 | 98.4 | 200.3424
7136 | R-500 | 77.9 | 113.3 | 98.6 | 200.7496
7137 | R-500 | 78 | 113.5 | 98.8 | 201.1568
7138 | R-500 | 78.1 | 113.6 | 98.9 | 201.3604
7139 | R-500 | 78.2 | 113.8 | 99.1 | 201.7676
7140 | R-500 | 78.3 | 114 | 99.3 | 202.1748
7141 | R-500 | 78.4 | 114.1 | 99.4 | 202.3784
7142 | R-500 | 78.5 | 114.3 | 99.6 | 202.7856
7143 | R-500 | 78.6 | 114.5 | 99.8 | 203.1928
7144 | R-500 | 78.7 | 114.7 | 100 | 203.6
7145 | R-500 | 78.8 | 114.8 | 100.1 | 203.8036
7146 | R-500 | 78.9 | 115 | 100.3 | 204.2108
7147 | R-500 | 79 | 115.2 | 100.5 | 204.618
7148 | R-500 | 79.1 | 115.4 | 100.7 | 205.0252
7149 | R-500 | 79.2 | 115.5 | 100.8 | 205.2288
7150 | R-500 | 79.3 | 115.7 | 101 | 205.636
7151 | R-500 | 79.4 | 115.9 | 101.2 | 206.0432
7152 | R-500 | 79.5 | 116 | 101.3 | 206.2468
7153 | R-500 | 79.6 | 116.2 | 101.5 | 206.654
7154 | R-500 | 79.7 | 116.4 | 101.7 | 207.0612
7155 | R-500 | 79.8 | 116.6 | 101.9 | 207.4684
7156 | R-500 | 79.9 | 116.7 | 102 | 207.672
7157 | R-500 | 80 | 116.9 | 102.2 | 208.0792
7158 | R-500 | 80.1 | 117.1 | 102.4 | 208.4864
7159 | R-500 | 80.2 | 117.3 | 102.6 | 208.8936
7160 | R-500 | 80.3 | 117.4 | 102.7 | 209.0972
7161 | R-500 | 80.4 | 117.6 | 102.9 | 209.5044
7162 | R-500 | 80.5 | 117.8 | 103.1 | 209.9116
7163 | R-500 | 80.6 | 118 | 103.3 | 210.3188
7164 | R-500 | 80.7 | 118.2 | 103.5 | 210.726
7165 | R-500 | 80.8 | 118.3 | 103.6 | 210.9296
7166 | R-500 | 80.9 | 118.5 | 103.8 | 211.3368
7167 | R-500 | 81 | 118.7 | 104 | 211.744
7168 | R-500 | 81.1 | 118.9 | 104.2 | 212.1512
7169 | R-500 | 81.2 | 119 | 104.3 | 212.3548
7170 | R-500 | 81.3 | 119.2 | 104.5 | 212.762
7171 | R-500 | 81.4 | 119.4 | 104.7 | 213.1692
7172 | R-500 | 81.5 | 119.6 | 104.9 | 213.5764
7173 | R-500 | 81.6 | 119.8 | 105.1 | 213.9836
7174 | R-500 | 81.7 | 119.9 | 105.2 | 214.1872
7175 | R-500 | 81.8 | 120.1 | 105.4 | 214.5944
7176 | R-500 | 81.9 | 120.3 | 105.6 | 215.0016
7177 | R-500 | 82 | 120.5 | 105.8 | 215.4088
7178 | R-500 | 82.1 | 120.6 | 105.9 | 215.6124
7179 | R-500 | 82.2 | 120.8 | 106.1 | 216.0196
7180 | R-500 | 82.3 | 121 | 106.3 | 216.4268
7181 | R-500 | 82.4 | 121.2 | 106.5 | 216.834
7182 | R-500 | 82.5 | 121.4 | 106.7 | 217.2412
7183 | R-500 | 82.6 | 121.5 | 106.8 | 217.4448
7184 | R-500 | 82.7 | 121.7 | 107 | 217.852
7185 | R-500 | 82.8 | 121.9 | 107.2 | 218.2592
7186 | R-500 | 82.9 | 122.1 | 107.4 | 218.6664
7187 | R-500 | 83 | 122.3 | 107.6 | 219.0736
7188 | R-500 | 83.1 | 122.5 | 107.8 | 219.4808
7189 | R-500 | 83.2 | 122.6 | 107.9 | 219.6844
7190 | R-500 | 83.3 | 122.8 | 108.1 | 220.0916
7191 | R-500 | 83.4 | 123 | 108.3 | 220.4988
7192 | R-500 | 83.5 | 123.2 | 108.5 | 220.906
7193 | R-500 | 83.6 | 123.4 | 108.7 | 221.3132
7194 | R-500 | 83.7 | 123.5 | 108.8 | 221.5168
7195 | R-500 | 83.8 | 123.7 | 109 | 221.924
7196 | R-500 | 83.9 | 123.9 | 109.2 | 222.3312
7197 | R-500 | 84 | 124.1 | 109.4 | 222.7384
7198 | R-500 | 84.1 | 124.3 | 109.6 | 223.1456
7199 | R-500 | 84.2 | 124.5 | 109.8 | 223.5528
7200 | R-500 | 84.3 | 124.6 | 109.9 | 223.7564
7201 | R-500 | 84.4 | 124.8 | 110.1 | 224.1636
7202 | R-500 | 84.5 | 125 | 110.3 | 224.5708
7203 | R-500 | 84.6 | 125.2 | 110.5 | 224.978
7204 | R-500 | 84.7 | 125.4 | 110.7 | 225.3852
7205 | R-500 | 84.8 | 125.6 | 110.9 | 225.7924
7206 | R-500 | 84.9 | 125.7 | 111 | 225.996
7207 | R-500 | 85 | 125.9 | 111.2 | 226.4032
7208 | R-500 | 85.1 | 126.1 | 111.4 | 226.8104
7209 | R-500 | 85.2 | 126.3 | 111.6 | 227.2176
7210 | R-500 | 85.3 | 126.5 | 111.8 | 227.6248
7211 | R-500 | 85.4 | 126.7 | 112 | 228.032
7212 | R-500 | 85.5 | 126.9 | 112.2 | 228.4392
7213 | R-500 | 85.6 | 127 | 112.3 | 228.6428
7214 | R-500 | 85.7 | 127.2 | 112.5 | 229.05
7215 | R-500 | 85.8 | 127.4 | 112.7 | 229.4572
7216 | R-500 | 85.9 | 127.6 | 112.9 | 229.8644
7217 | R-500 | 86 | 127.8 | 113.1 | 230.2716
7218 | R-500 | 86.1 | 128 | 113.3 | 230.6788
7219 | R-500 | 86.2 | 128.2 | 113.5 | 231.086
7220 | R-500 | 86.3 | 128.4 | 113.7 | 231.4932
7221 | R-500 | 86.4 | 128.5 | 113.8 | 231.6968
7222 | R-500 | 86.5 | 128.7 | 114 | 232.104
7223 | R-500 | 86.6 | 128.9 | 114.2 | 232.5112
7224 | R-500 | 86.7 | 129.1 | 114.4 | 232.9184
7225 | R-500 | 86.8 | 129.3 | 114.6 | 233.3256
7226 | R-500 | 86.9 | 129.5 | 114.8 | 233.7328
7227 | R-500 | 87 | 129.7 | 115 | 234.14
7228 | R-500 | 87.1 | 129.9 | 115.2 | 234.5472
7229 | R-500 | 87.2 | 130.1 | 115.4 | 234.9544
7230 | R-500 | 87.3 | 130.2 | 115.5 | 235.158
7231 | R-500 | 87.4 | 130.4 | 115.7 | 235.5652
7232 | R-500 | 87.5 | 130.6 | 115.9 | 235.9724
7233 | R-500 | 87.6 | 130.8 | 116.1 | 236.3796
7234 | R-500 | 87.7 | 131 | 116.3 | 236.7868
7235 | R-500 | 87.8 | 131.2 | 116.5 | 237.194
7236 | R-500 | 87.9 | 131.4 | 116.7 | 237.6012
7237 | R-500 | 88 | 131.6 | 116.9 | 238.0084
7238 | R-500 | 88.1 | 131.8 | 117.1 | 238.4156
7239 | R-500 | 88.2 | 132 | 117.3 | 238.8228
7240 | R-500 | 88.3 | 132.2 | 117.5 | 239.23
7241 | R-500 | 88.4 | 132.3 | 117.6 | 239.4336
7242 | R-500 | 88.5 | 132.5 | 117.8 | 239.8408
7243 | R-500 | 88.6 | 132.7 | 118 | 240.248
7244 | R-500 | 88.7 | 132.9 | 118.2 | 240.6552
7245 | R-500 | 88.8 | 133.1 | 118.4 | 241.0624
7246 | R-500 | 88.9 | 133.3 | 118.6 | 241.4696
7247 | R-500 | 89 | 133.5 | 118.8 | 241.8768
7248 | R-500 | 89.1 | 133.7 | 119 | 242.284
7249 | R-500 | 89.2 | 133.9 | 119.2 | 242.6912
7250 | R-500 | 89.3 | 134.1 | 119.4 | 243.0984
7251 | R-500 | 89.4 | 134.3 | 119.6 | 243.5056
7252 | R-500 | 89.5 | 134.5 | 119.8 | 243.9128
7253 | R-500 | 89.6 | 134.7 | 120 | 244.32
7254 | R-500 | 89.7 | 134.9 | 120.2 | 244.7272
7255 | R-500 | 89.8 | 135.1 | 120.4 | 245.1344
7256 | R-500 | 89.9 | 135.3 | 120.6 | 245.5416
7257 | R-500 | 90 | 135.4 | 120.7 | 245.7452
7258 | R-500 | 90.1 | 135.6 | 120.9 | 246.1524
7259 | R-500 | 90.2 | 135.8 | 121.1 | 246.5596
7260 | R-500 | 90.3 | 136 | 121.3 | 246.9668
7261 | R-500 | 90.4 | 136.2 | 121.5 | 247.374
7262 | R-500 | 90.5 | 136.4 | 121.7 | 247.7812
7263 | R-500 | 90.6 | 136.6 | 121.9 | 248.1884
7264 | R-500 | 90.7 | 136.8 | 122.1 | 248.5956
7265 | R-500 | 90.8 | 137 | 122.3 | 249.0028
7266 | R-500 | 90.9 | 137.2 | 122.5 | 249.41
7267 | R-500 | 91 | 137.4 | 122.7 | 249.8172
7268 | R-500 | 91.1 | 137.6 | 122.9 | 250.2244
7269 | R-500 | 91.2 | 137.8 | 123.1 | 250.6316
7270 | R-500 | 91.3 | 138 | 123.3 | 251.0388
7271 | R-500 | 91.4 | 138.2 | 123.5 | 251.446
7272 | R-500 | 91.5 | 138.4 | 123.7 | 251.8532
7273 | R-500 | 91.6 | 138.6 | 123.9 | 252.2604
7274 | R-500 | 91.7 | 138.8 | 124.1 | 252.6676
7275 | R-500 | 91.8 | 139 | 124.3 | 253.0748
7276 | R-500 | 91.9 | 139.2 | 124.5 | 253.482
7277 | R-500 | 92 | 139.4 | 124.7 | 253.8892
7278 | R-500 | 92.1 | 139.6 | 124.9 | 254.2964
7279 | R-500 | 92.2 | 139.8 | 125.1 | 254.7036
7280 | R-500 | 92.3 | 140 | 125.3 | 255.1108
7281 | R-500 | 92.4 | 140.2 | 125.5 | 255.518
7282 | R-500 | 92.5 | 140.4 | 125.7 | 255.9252
7283 | R-500 | 92.6 | 140.6 | 125.9 | 256.3324
7284 | R-500 | 92.7 | 140.8 | 126.1 | 256.7396
7285 | R-500 | 92.8 | 141 | 126.3 | 257.1468
7286 | R-500 | 92.9 | 141.2 | 126.5 | 257.554
7287 | R-500 | 93 | 141.4 | 126.7 | 257.9612
7288 | R-500 | 93.1 | 141.6 | 126.9 | 258.3684
7289 | R-500 | 93.2 | 141.8 | 127.1 | 258.7756
7290 | R-500 | 93.3 | 142 | 127.3 | 259.1828
7291 | R-500 | 93.4 | 142.2 | 127.5 | 259.59
7292 | R-500 | 93.5 | 142.4 | 127.7 | 259.9972
7293 | R-500 | 93.6 | 142.6 | 127.9 | 260.4044
7294 | R-500 | 93.7 | 142.8 | 128.1 | 260.8116
7295 | R-500 | 93.8 | 143 | 128.3 | 261.2188
7296 | R-500 | 93.9 | 143.2 | 128.5 | 261.626
7297 | R-500 | 94 | 143.4 | 128.7 | 262.0332
7298 | R-500 | 94.1 | 143.6 | 128.9 | 262.4404
7299 | R-500 | 94.2 | 143.8 | 129.1 | 262.8476
7300 | R-500 | 94.3 | 144 | 129.3 | 263.2548
7301 | R-500 | 94.4 | 144.2 | 129.5 | 263.662
7302 | R-500 | 94.5 | 144.5 | 129.8 | 264.2728
7303 | R-500 | 94.6 | 144.7 | 130 | 264.68
7304 | R-500 | 94.7 | 144.9 | 130.2 | 265.0872
7305 | R-500 | 94.8 | 145.1 | 130.4 | 265.4944
7306 | R-500 | 94.9 | 145.3 | 130.6 | 265.9016
7307 | R-500 | 95 | 145.5 | 130.8 | 266.3088
7308 | R-500 | 95.1 | 145.7 | 131 | 266.716
7309 | R-500 | 95.2 | 145.9 | 131.2 | 267.1232
7310 | R-500 | 95.3 | 146.1 | 131.4 | 267.5304
7311 | R-500 | 95.4 | 146.3 | 131.6 | 267.9376
7312 | R-500 | 95.5 | 146.5 | 131.8 | 268.3448
7313 | R-500 | 95.6 | 146.7 | 132 | 268.752
7314 | R-500 | 95.7 | 146.9 | 132.2 | 269.1592
7315 | R-500 | 95.8 | 147.1 | 132.4 | 269.5664
7316 | R-500 | 95.9 | 147.3 | 132.6 | 269.9736
7317 | R-500 | 96 | 147.6 | 132.9 | 270.5844
7318 | R-500 | 96.1 | 147.8 | 133.1 | 270.9916
7319 | R-500 | 96.2 | 148 | 133.3 | 271.3988
7320 | R-500 | 96.3 | 148.2 | 133.5 | 271.806
7321 | R-500 | 96.4 | 148.4 | 133.7 | 272.2132
7322 | R-500 | 96.5 | 148.6 | 133.9 | 272.6204
7323 | R-500 | 96.6 | 148.8 | 134.1 | 273.0276
7324 | R-500 | 96.7 | 149 | 134.3 | 273.4348
7325 | R-500 | 96.8 | 149.2 | 134.5 | 273.842
7326 | R-500 | 96.9 | 149.4 | 134.7 | 274.2492
7327 | R-500 | 97 | 149.6 | 134.9 | 274.6564
7328 | R-500 | 97.1 | 149.9 | 135.2 | 275.2672
7329 | R-500 | 97.2 | 150.1 | 135.4 | 275.6744
7330 | R-500 | 97.3 | 150.3 | 135.6 | 276.0816
7331 | R-500 | 97.4 | 150.5 | 135.8 | 276.4888
7332 | R-500 | 97.5 | 150.7 | 136 | 276.896
7333 | R-500 | 97.6 | 150.9 | 136.2 | 277.3032
7334 | R-500 | 97.7 | 151.1 | 136.4 | 277.7104
7335 | R-500 | 97.8 | 151.3 | 136.6 | 278.1176
7336 | R-500 | 97.9 | 151.6 | 136.9 | 278.7284
7337 | R-500 | 98 | 151.8 | 137.1 | 279.1356
7338 | R-500 | 98.1 | 152 | 137.3 | 279.5428
7339 | R-500 | 98.2 | 152.2 | 137.5 | 279.95
7340 | R-500 | 98.3 | 152.4 | 137.7 | 280.3572
7341 | R-500 | 98.4 | 152.6 | 137.9 | 280.7644
7342 | R-500 | 98.5 | 152.8 | 138.1 | 281.1716
7343 | R-500 | 98.6 | 153 | 138.3 | 281.5788
7344 | R-500 | 98.7 | 153.3 | 138.6 | 282.1896
7345 | R-500 | 98.8 | 153.5 | 138.8 | 282.5968
7346 | R-500 | 98.9 | 153.7 | 139 | 283.004
7347 | R-500 | 99 | 153.9 | 139.2 | 283.4112
7348 | R-500 | 99.1 | 154.1 | 139.4 | 283.8184
7349 | R-500 | 99.2 | 154.3 | 139.6 | 284.2256
7350 | R-500 | 99.3 | 154.5 | 139.8 | 284.6328
7351 | R-500 | 99.4 | 154.8 | 140.1 | 285.2436
7352 | R-500 | 99.5 | 155 | 140.3 | 285.6508
7353 | R-500 | 99.6 | 155.2 | 140.5 | 286.058
7354 | R-500 | 99.7 | 155.4 | 140.7 | 286.4652
7355 | R-500 | 99.8 | 155.6 | 140.9 | 286.8724
7356 | R-500 | 99.9 | 155.8 | 141.1 | 287.2796
7357 | R-500 | 100 | 156.1 | 141.4 | 287.8904
7358 | R-500 | 100.1 | 156.3 | 141.6 | 288.2976
7359 | R-500 | 100.2 | 156.5 | 141.8 | 288.7048
7360 | R-500 | 100.3 | 156.7 | 142 | 289.112
7361 | R-500 | 100.4 | 156.9 | 142.2 | 289.5192
7362 | R-500 | 100.5 | 157.1 | 142.4 | 289.9264
7363 | R-500 | 100.6 | 157.4 | 142.7 | 290.5372
7364 | R-500 | 100.7 | 157.6 | 142.9 | 290.9444
7365 | R-500 | 100.8 | 157.8 | 143.1 | 291.3516
7366 | R-500 | 100.9 | 158 | 143.3 | 291.7588
7367 | R-500 | 101 | 158.2 | 143.5 | 292.166
7368 | R-500 | 101.1 | 158.5 | 143.8 | 292.7768
7369 | R-500 | 101.2 | 158.7 | 144 | 293.184
7370 | R-500 | 101.3 | 158.9 | 144.2 | 293.5912
7371 | R-500 | 101.4 | 159.1 | 144.4 | 293.9984
7372 | R-500 | 101.5 | 159.3 | 144.6 | 294.4056
7373 | R-500 | 101.6 | 159.6 | 144.9 | 295.0164
7374 | R-500 | 101.7 | 159.8 | 145.1 | 295.4236
7375 | R-500 | 101.8 | 160 | 145.3 | 295.8308
7376 | R-500 | 101.9 | 160.2 | 145.5 | 296.238
7377 | R-500 | 102 | 160.4 | 145.7 | 296.6452
7378 | R-500 | 102.1 | 160.7 | 146 | 297.256
7379 | R-500 | 102.2 | 160.9 | 146.2 | 297.6632
7380 | R-500 | 102.3 | 161.1 | 146.4 | 298.0704
7381 | R-500 | 102.4 | 161.3 | 146.6 | 298.4776
7382 | R-500 | 102.5 | 161.6 | 146.9 | 299.0884
7383 | R-500 | 102.6 | 161.8 | 147.1 | 299.4956
7384 | R-500 | 102.7 | 162 | 147.3 | 299.9028
7385 | R-500 | 102.8 | 162.2 | 147.5 | 300.31
7386 | R-500 | 102.9 | 162.4 | 147.7 | 300.7172
7387 | R-500 | 103 | 162.7 | 148 | 301.328
7388 | R-500 | 103.1 | 162.9 | 148.2 | 301.7352
7389 | R-500 | 103.2 | 163.1 | 148.4 | 302.1424
7390 | R-500 | 103.3 | 163.3 | 148.6 | 302.5496
7391 | R-500 | 103.4 | 163.6 | 148.9 | 303.1604
7392 | R-500 | 103.5 | 163.8 | 149.1 | 303.5676
7393 | R-500 | 103.6 | 164 | 149.3 | 303.9748
7394 | R-500 | 103.7 | 164.2 | 149.5 | 304.382
7395 | R-500 | 103.8 | 164.5 | 149.8 | 304.9928
7396 | R-500 | 103.9 | 164.7 | 150 | 305.4
7397 | R-500 | 104 | 164.9 | 150.2 | 305.8072
7398 | R-500 | 104.1 | 165.1 | 150.4 | 306.2144
7399 | R-500 | 104.2 | 165.4 | 150.7 | 306.8252
7400 | R-500 | 104.3 | 165.6 | 150.9 | 307.2324
7401 | R-500 | 104.4 | 165.8 | 151.1 | 307.6396
7402 | R-500 | 104.5 | 166.1 | 151.4 | 308.2504
7403 | R-500 | 104.6 | 166.3 | 151.6 | 308.6576
7404 | R-500 | 104.7 | 166.5 | 151.8 | 309.0648
7405 | R-500 | 104.8 | 166.7 | 152 | 309.472
7406 | R-500 | 104.9 | 167 | 152.3 | 310.0828
7407 | R-500 | 105 | 167.2 | 152.5 | 310.49
7408 | R-500 | 105.1 | 167.4 | 152.7 | 310.8972
7409 | R-500 | 105.2 | 167.7 | 153 | 311.508
7410 | R-500 | 105.3 | 167.9 | 153.2 | 311.9152
7411 | R-500 | 105.4 | 168.1 | 153.4 | 312.3224
7412 | R-500 | 105.5 | 168.3 | 153.6 | 312.7296
7413 | R-500 | 105.6 | 168.6 | 153.9 | 313.3404
7414 | R-500 | 105.7 | 168.8 | 154.1 | 313.7476
7415 | R-500 | 105.8 | 169 | 154.3 | 314.1548
7416 | R-500 | 105.9 | 169.3 | 154.6 | 314.7656
7417 | R-500 | 106 | 169.5 | 154.8 | 315.1728
7418 | R-500 | 106.1 | 169.7 | 155 | 315.58
7419 | R-500 | 106.2 | 170 | 155.3 | 316.1908
7420 | R-500 | 106.3 | 170.2 | 155.5 | 316.598
7421 | R-500 | 106.4 | 170.4 | 155.7 | 317.0052
7422 | R-500 | 106.5 | 170.6 | 155.9 | 317.4124
7423 | R-500 | 106.6 | 170.9 | 156.2 | 318.0232
7424 | R-500 | 106.7 | 171.1 | 156.4 | 318.4304
7425 | R-500 | 106.8 | 171.3 | 156.6 | 318.8376
7426 | R-500 | 106.9 | 171.6 | 156.9 | 319.4484
7427 | R-500 | 107 | 171.8 | 157.1 | 319.8556
7428 | R-500 | 107.1 | 172 | 157.3 | 320.2628
7429 | R-500 | 107.2 | 172.3 | 157.6 | 320.8736
7430 | R-500 | 107.3 | 172.5 | 157.8 | 321.2808
7431 | R-500 | 107.4 | 172.7 | 158 | 321.688
7432 | R-500 | 107.5 | 173 | 158.3 | 322.2988
7433 | R-500 | 107.6 | 173.2 | 158.5 | 322.706
7434 | R-500 | 107.7 | 173.4 | 158.7 | 323.1132
7435 | R-500 | 107.8 | 173.7 | 159 | 323.724
7436 | R-500 | 107.9 | 173.9 | 159.2 | 324.1312
7437 | R-500 | 108 | 174.2 | 159.5 | 324.742
7438 | R-500 | 108.1 | 174.4 | 159.7 | 325.1492
7439 | R-500 | 108.2 | 174.6 | 159.9 | 325.5564
7440 | R-500 | 108.3 | 174.9 | 160.2 | 326.1672
7441 | R-500 | 108.4 | 175.1 | 160.4 | 326.5744
7442 | R-500 | 108.5 | 175.3 | 160.6 | 326.9816
7443 | R-500 | 108.6 | 175.6 | 160.9 | 327.5924
7444 | R-500 | 108.7 | 175.8 | 161.1 | 327.9996
7445 | R-500 | 108.8 | 176 | 161.3 | 328.4068
7446 | R-500 | 108.9 | 176.3 | 161.6 | 329.0176
7447 | R-500 | 109 | 176.5 | 161.8 | 329.4248
7448 | R-500 | 109.1 | 176.8 | 162.1 | 330.0356
7449 | R-500 | 109.2 | 177 | 162.3 | 330.4428
7450 | R-500 | 109.3 | 177.2 | 162.5 | 330.85
7451 | R-500 | 109.4 | 177.5 | 162.8 | 331.4608
7452 | R-500 | 109.5 | 177.7 | 163 | 331.868
7453 | R-500 | 109.6 | 177.9 | 163.2 | 332.2752
7454 | R-500 | 109.7 | 178.2 | 163.5 | 332.886
7455 | R-500 | 109.8 | 178.4 | 163.7 | 333.2932
7456 | R-500 | 109.9 | 178.7 | 164 | 333.904
7457 | R-500 | 110 | 178.9 | 164.2 | 334.3112
7458 | R-500 | 110.1 | 179.1 | 164.4 | 334.7184
7459 | R-500 | 110.2 | 179.4 | 164.7 | 335.3292
7460 | R-500 | 110.3 | 179.6 | 164.9 | 335.7364
7461 | R-500 | 110.4 | 179.9 | 165.2 | 336.3472
7462 | R-500 | 110.5 | 180.1 | 165.4 | 336.7544
7463 | R-500 | 110.6 | 180.4 | 165.7 | 337.3652
7464 | R-500 | 110.7 | 180.6 | 165.9 | 337.7724
7465 | R-500 | 110.8 | 180.8 | 166.1 | 338.1796
7466 | R-500 | 110.9 | 181.1 | 166.4 | 338.7904
7467 | R-500 | 111 | 181.3 | 166.6 | 339.1976
7468 | R-500 | 111.1 | 181.6 | 166.9 | 339.8084
7469 | R-500 | 111.2 | 181.8 | 167.1 | 340.2156
7470 | R-500 | 111.3 | 182 | 167.3 | 340.6228
7471 | R-500 | 111.4 | 182.3 | 167.6 | 341.2336
7472 | R-500 | 111.5 | 182.5 | 167.8 | 341.6408
7473 | R-500 | 111.6 | 182.8 | 168.1 | 342.2516
7474 | R-500 | 111.7 | 183 | 168.3 | 342.6588
7475 | R-500 | 111.8 | 183.3 | 168.6 | 343.2696
7476 | R-500 | 111.9 | 183.5 | 168.8 | 343.6768
7477 | R-500 | 112 | 183.8 | 169.1 | 344.2876
7478 | R-500 | 112.1 | 184 | 169.3 | 344.6948
7479 | R-500 | 112.2 | 184.2 | 169.5 | 345.102
7480 | R-500 | 112.3 | 184.5 | 169.8 | 345.7128
7481 | R-500 | 112.4 | 184.7 | 170 | 346.12
7482 | R-500 | 112.5 | 185 | 170.3 | 346.7308
7483 | R-500 | 112.6 | 185.2 | 170.5 | 347.138
7484 | R-500 | 112.7 | 185.5 | 170.8 | 347.7488
7485 | R-500 | 112.8 | 185.7 | 171 | 348.156
7486 | R-500 | 112.9 | 186 | 171.3 | 348.7668
7487 | R-500 | 113 | 186.2 | 171.5 | 349.174
7488 | R-500 | 113.1 | 186.5 | 171.8 | 349.7848
7489 | R-500 | 113.2 | 186.7 | 172 | 350.192
7490 | R-500 | 113.3 | 187 | 172.3 | 350.8028
7491 | R-500 | 113.4 | 187.2 | 172.5 | 351.21
7492 | R-500 | 113.5 | 187.5 | 172.8 | 351.8208
7493 | R-500 | 113.6 | 187.7 | 173 | 352.228
7494 | R-500 | 113.7 | 188 | 173.3 | 352.8388
7495 | R-500 | 113.8 | 188.2 | 173.5 | 353.246
7496 | R-500 | 113.9 | 188.5 | 173.8 | 353.8568
7497 | R-500 | 114 | 188.7 | 174 | 354.264
7498 | R-500 | 114.1 | 189 | 174.3 | 354.8748
7499 | R-500 | 114.2 | 189.2 | 174.5 | 355.282
7500 | R-500 | 114.3 | 189.5 | 174.8 | 355.8928
7501 | R-500 | 114.4 | 189.7 | 175 | 356.3
7502 | R-500 | 114.5 | 190 | 175.3 | 356.9108
7503 | R-500 | 114.6 | 190.2 | 175.5 | 357.318
7504 | R-500 | 114.7 | 190.5 | 175.8 | 357.9288
7505 | R-500 | 114.8 | 190.7 | 176 | 358.336
7506 | R-500 | 114.9 | 191 | 176.3 | 358.9468
7507 | R-500 | 115 | 191.2 | 176.5 | 359.354
7508 | R-500 | 115.1 | 191.5 | 176.8 | 359.9648
7509 | R-500 | 115.2 | 191.7 | 177 | 360.372
7510 | R-500 | 115.3 | 192 | 177.3 | 360.9828
7511 | R-500 | 115.4 | 192.2 | 177.5 | 361.39
7512 | R-500 | 115.5 | 192.5 | 177.8 | 362.0008
7513 | R-500 | 115.6 | 192.7 | 178 | 362.408
7514 | R-500 | 115.7 | 193 | 178.3 | 363.0188
7515 | R-500 | 115.8 | 193.2 | 178.5 | 363.426
7516 | R-500 | 115.9 | 193.5 | 178.8 | 364.0368
7517 | R-500 | 116 | 193.7 | 179 | 364.444
7518 | R-500 | 116.1 | 194 | 179.3 | 365.0548
7519 | R-500 | 116.2 | 194.3 | 179.6 | 365.6656
7520 | R-500 | 116.3 | 194.5 | 179.8 | 366.0728
7521 | R-500 | 116.4 | 194.8 | 180.1 | 366.6836
7522 | R-500 | 116.5 | 195 | 180.3 | 367.0908
7523 | R-500 | 116.6 | 195.3 | 180.6 | 367.7016
7524 | R-500 | 116.7 | 195.5 | 180.8 | 368.1088
7525 | R-500 | 116.8 | 195.8 | 181.1 | 368.7196
7526 | R-500 | 116.9 | 196.1 | 181.4 | 369.3304
7527 | R-500 | 117 | 196.3 | 181.6 | 369.7376
7528 | R-500 | 117.1 | 196.6 | 181.9 | 370.3484
7529 | R-500 | 117.2 | 196.8 | 182.1 | 370.7556
7530 | R-500 | 117.3 | 197.1 | 182.4 | 371.3664
7531 | R-500 | 117.4 | 197.3 | 182.6 | 371.7736
7532 | R-500 | 117.5 | 197.6 | 182.9 | 372.3844
7533 | R-500 | 117.6 | 197.9 | 183.2 | 372.9952
7534 | R-500 | 117.7 | 198.1 | 183.4 | 373.4024
7535 | R-500 | 117.8 | 198.4 | 183.7 | 374.0132
7536 | R-500 | 117.9 | 198.6 | 183.9 | 374.4204
7537 | R-500 | 118 | 198.9 | 184.2 | 375.0312
7538 | R-500 | 118.1 | 199.2 | 184.5 | 375.642
7539 | R-500 | 118.2 | 199.4 | 184.7 | 376.0492
7540 | R-500 | 118.3 | 199.7 | 185 | 376.66
7541 | R-500 | 118.4 | 199.9 | 185.2 | 377.0672
7542 | R-500 | 118.5 | 200.2 | 185.5 | 377.678
7543 | R-500 | 118.6 | 200.5 | 185.8 | 378.2888
7544 | R-500 | 118.7 | 200.7 | 186 | 378.696
7545 | R-500 | 118.8 | 201 | 186.3 | 379.3068
7546 | R-500 | 118.9 | 201.2 | 186.5 | 379.714
7547 | R-500 | 119 | 201.5 | 186.8 | 380.3248
7548 | R-500 | 119.1 | 201.8 | 187.1 | 380.9356
7549 | R-500 | 119.2 | 202 | 187.3 | 381.3428
7550 | R-500 | 119.3 | 202.3 | 187.6 | 381.9536
7551 | R-500 | 119.4 | 202.6 | 187.9 | 382.5644
7552 | R-500 | 119.5 | 202.8 | 188.1 | 382.9716
7553 | R-500 | 119.6 | 203.1 | 188.4 | 383.5824
7554 | R-500 | 119.7 | 203.3 | 188.6 | 383.9896
7555 | R-500 | 119.8 | 203.6 | 188.9 | 384.6004
7556 | R-500 | 119.9 | 203.9 | 189.2 | 385.2112
7557 | R-500 | 120 | 204.1 | 189.4 | 385.6184
7558 | R-12 | 10 | 29.29 | 14.59 | 29.7052
7559 | R-12 | 10.1 | 29.35 | 14.65 | 29.8274
7560 | R-12 | 10.2 | 29.41 | 14.71 | 29.9496
7561 | R-12 | 10.3 | 29.47 | 14.77 | 30.0717
7562 | R-12 | 10.4 | 29.53 | 14.83 | 30.1939
7563 | R-12 | 10.5 | 29.59 | 14.89 | 30.316
7564 | R-12 | 10.6 | 29.65 | 14.95 | 30.4382
7565 | R-12 | 10.7 | 29.71 | 15.01 | 30.5604
7566 | R-12 | 10.8 | 29.77 | 15.07 | 30.6825
7567 | R-12 | 10.9 | 29.83 | 15.13 | 30.8047
7568 | R-12 | 11 | 29.89 | 15.19 | 30.9268
7569 | R-12 | 11.1 | 29.95 | 15.25 | 31.049
7570 | R-12 | 11.2 | 30.01 | 15.31 | 31.1712
7571 | R-12 | 11.3 | 30.07 | 15.37 | 31.2933
7572 | R-12 | 11.4 | 30.13 | 15.43 | 31.4155
7573 | R-12 | 11.5 | 30.19 | 15.49 | 31.5376
7574 | R-12 | 11.6 | 30.25 | 15.55 | 31.6598
7575 | R-12 | 11.7 | 30.31 | 15.61 | 31.782
7576 | R-12 | 11.8 | 30.37 | 15.67 | 31.9041
7577 | R-12 | 11.9 | 30.43 | 15.73 | 32.0263
7578 | R-12 | 12 | 30.49 | 15.79 | 32.1484
7579 | R-12 | 12.1 | 30.55 | 15.85 | 32.2706
7580 | R-12 | 12.2 | 30.61 | 15.91 | 32.3928
7581 | R-12 | 12.3 | 30.68 | 15.98 | 32.5353
7582 | R-12 | 12.4 | 30.74 | 16.04 | 32.6574
7583 | R-12 | 12.5 | 30.8 | 16.1 | 32.7796
7584 | R-12 | 12.6 | 30.86 | 16.16 | 32.9018
7585 | R-12 | 12.7 | 30.92 | 16.22 | 33.0239
7586 | R-12 | 12.8 | 30.98 | 16.28 | 33.1461
7587 | R-12 | 12.9 | 31.04 | 16.34 | 33.2682
7588 | R-12 | 13 | 31.11 | 16.41 | 33.4108
7589 | R-12 | 13.1 | 31.17 | 16.47 | 33.5329
7590 | R-12 | 13.2 | 31.23 | 16.53 | 33.6551
7591 | R-12 | 13.3 | 31.29 | 16.59 | 33.7772
7592 | R-12 | 13.4 | 31.36 | 16.66 | 33.9198
7593 | R-12 | 13.5 | 31.42 | 16.72 | 34.0419
7594 | R-12 | 13.6 | 31.48 | 16.78 | 34.1641
7595 | R-12 | 13.7 | 31.54 | 16.84 | 34.2862
7596 | R-12 | 13.8 | 31.61 | 16.91 | 34.4288
7597 | R-12 | 13.9 | 31.67 | 16.97 | 34.5509
7598 | R-12 | 14 | 31.73 | 17.03 | 34.6731
7599 | R-12 | 14.1 | 31.79 | 17.09 | 34.7952
7600 | R-12 | 14.2 | 31.86 | 17.16 | 34.9378
7601 | R-12 | 14.3 | 31.92 | 17.22 | 35.0599
7602 | R-12 | 14.4 | 31.98 | 17.28 | 35.1821
7603 | R-12 | 14.5 | 32.05 | 17.35 | 35.3246
7604 | R-12 | 14.6 | 32.11 | 17.41 | 35.4468
7605 | R-12 | 14.7 | 32.17 | 17.47 | 35.5689
7606 | R-12 | 14.8 | 32.24 | 17.54 | 35.7114
7607 | R-12 | 14.9 | 32.3 | 17.6 | 35.8336
7608 | R-12 | 15 | 32.37 | 17.67 | 35.9761
7609 | R-12 | 15.1 | 32.43 | 17.73 | 36.0983
7610 | R-12 | 15.2 | 32.49 | 17.79 | 36.2204
7611 | R-12 | 15.3 | 32.56 | 17.86 | 36.363
7612 | R-12 | 15.4 | 32.62 | 17.92 | 36.4851
7613 | R-12 | 15.5 | 32.69 | 17.99 | 36.6276
7614 | R-12 | 15.6 | 32.75 | 18.05 | 36.7498
7615 | R-12 | 15.7 | 32.82 | 18.12 | 36.8923
7616 | R-12 | 15.8 | 32.88 | 18.18 | 37.0145
7617 | R-12 | 15.9 | 32.94 | 18.24 | 37.1366
7618 | R-12 | 16 | 33.01 | 18.31 | 37.2792
7619 | R-12 | 16.1 | 33.07 | 18.37 | 37.4013
7620 | R-12 | 16.2 | 33.14 | 18.44 | 37.5438
7621 | R-12 | 16.3 | 33.2 | 18.5 | 37.666
7622 | R-12 | 16.4 | 33.27 | 18.57 | 37.8085
7623 | R-12 | 16.5 | 33.33 | 18.63 | 37.9307
7624 | R-12 | 16.6 | 33.4 | 18.7 | 38.0732
7625 | R-12 | 16.7 | 33.47 | 18.77 | 38.2157
7626 | R-12 | 16.8 | 33.53 | 18.83 | 38.3379
7627 | R-12 | 16.9 | 33.6 | 18.9 | 38.4804
7628 | R-12 | 17 | 33.66 | 18.96 | 38.6026
7629 | R-12 | 17.1 | 33.73 | 19.03 | 38.7451
7630 | R-12 | 17.2 | 33.79 | 19.09 | 38.8672
7631 | R-12 | 17.3 | 33.86 | 19.16 | 39.0098
7632 | R-12 | 17.4 | 33.93 | 19.23 | 39.1523
7633 | R-12 | 17.5 | 33.99 | 19.29 | 39.2744
7634 | R-12 | 17.6 | 34.06 | 19.36 | 39.417
7635 | R-12 | 17.7 | 34.13 | 19.43 | 39.5595
7636 | R-12 | 17.8 | 34.19 | 19.49 | 39.6816
7637 | R-12 | 17.9 | 34.26 | 19.56 | 39.8242
7638 | R-12 | 18 | 34.33 | 19.63 | 39.9667
7639 | R-12 | 18.1 | 34.39 | 19.69 | 40.0888
7640 | R-12 | 18.2 | 34.46 | 19.76 | 40.2314
7641 | R-12 | 18.3 | 34.53 | 19.83 | 40.3739
7642 | R-12 | 18.4 | 34.59 | 19.89 | 40.496
7643 | R-12 | 18.5 | 34.66 | 19.96 | 40.6386
7644 | R-12 | 18.6 | 34.73 | 20.03 | 40.7811
7645 | R-12 | 18.7 | 34.8 | 20.1 | 40.9236
7646 | R-12 | 18.8 | 34.86 | 20.16 | 41.0458
7647 | R-12 | 18.9 | 34.93 | 20.23 | 41.1883
7648 | R-12 | 19 | 35 | 20.3 | 41.3308
7649 | R-12 | 19.1 | 35.07 | 20.37 | 41.4733
7650 | R-12 | 19.2 | 35.13 | 20.43 | 41.5955
7651 | R-12 | 19.3 | 35.2 | 20.5 | 41.738
7652 | R-12 | 19.4 | 35.27 | 20.57 | 41.8805
7653 | R-12 | 19.5 | 35.34 | 20.64 | 42.023
7654 | R-12 | 19.6 | 35.41 | 20.71 | 42.1656
7655 | R-12 | 19.7 | 35.48 | 20.78 | 42.3081
7656 | R-12 | 19.8 | 35.54 | 20.84 | 42.4302
7657 | R-12 | 19.9 | 35.61 | 20.91 | 42.5728
7658 | R-12 | 20 | 35.68 | 20.98 | 42.7153
7659 | R-12 | 20.1 | 35.75 | 21.05 | 42.8578
7660 | R-12 | 20.2 | 35.82 | 21.12 | 43.0003
7661 | R-12 | 20.3 | 35.89 | 21.19 | 43.1428
7662 | R-12 | 20.4 | 35.96 | 21.26 | 43.2854
7663 | R-12 | 20.5 | 36.03 | 21.33 | 43.4279
7664 | R-12 | 20.6 | 36.1 | 21.4 | 43.5704
7665 | R-12 | 20.7 | 36.17 | 21.47 | 43.7129
7666 | R-12 | 20.8 | 36.24 | 21.54 | 43.8554
7667 | R-12 | 20.9 | 36.31 | 21.61 | 43.998
7668 | R-12 | 21 | 36.37 | 21.67 | 44.1201
7669 | R-12 | 21.1 | 36.44 | 21.74 | 44.2626
7670 | R-12 | 21.2 | 36.51 | 21.81 | 44.4052
7671 | R-12 | 21.3 | 36.58 | 21.88 | 44.5477
7672 | R-12 | 21.4 | 36.66 | 21.96 | 44.7106
7673 | R-12 | 21.5 | 36.73 | 22.03 | 44.8531
7674 | R-12 | 21.6 | 36.8 | 22.1 | 44.9956
7675 | R-12 | 21.7 | 36.87 | 22.17 | 45.1381
7676 | R-12 | 21.8 | 36.94 | 22.24 | 45.2806
7677 | R-12 | 21.9 | 37.01 | 22.31 | 45.4232
7678 | R-12 | 22 | 37.08 | 22.38 | 45.5657
7679 | R-12 | 22.1 | 37.15 | 22.45 | 45.7082
7680 | R-12 | 22.2 | 37.22 | 22.52 | 45.8507
7681 | R-12 | 22.3 | 37.29 | 22.59 | 45.9932
7682 | R-12 | 22.4 | 37.36 | 22.66 | 46.1358
7683 | R-12 | 22.5 | 37.43 | 22.73 | 46.2783
7684 | R-12 | 22.6 | 37.51 | 22.81 | 46.4412
7685 | R-12 | 22.7 | 37.58 | 22.88 | 46.5837
7686 | R-12 | 22.8 | 37.65 | 22.95 | 46.7262
7687 | R-12 | 22.9 | 37.72 | 23.02 | 46.8687
7688 | R-12 | 23 | 37.79 | 23.09 | 47.0112
7689 | R-12 | 23.1 | 37.86 | 23.16 | 47.1538
7690 | R-12 | 23.2 | 37.94 | 23.24 | 47.3166
7691 | R-12 | 23.3 | 38.01 | 23.31 | 47.4592
7692 | R-12 | 23.4 | 38.08 | 23.38 | 47.6017
7693 | R-12 | 23.5 | 38.15 | 23.45 | 47.7442
7694 | R-12 | 23.6 | 38.23 | 23.53 | 47.9071
7695 | R-12 | 23.7 | 38.3 | 23.6 | 48.0496
7696 | R-12 | 23.8 | 38.37 | 23.67 | 48.1921
7697 | R-12 | 23.9 | 38.44 | 23.74 | 48.3346
7698 | R-12 | 24 | 38.52 | 23.82 | 48.4975
7699 | R-12 | 24.1 | 38.59 | 23.89 | 48.64
7700 | R-12 | 24.2 | 38.66 | 23.96 | 48.7826
7701 | R-12 | 24.3 | 38.74 | 24.04 | 48.9454
7702 | R-12 | 24.4 | 38.81 | 24.11 | 49.088
7703 | R-12 | 24.5 | 38.88 | 24.18 | 49.2305
7704 | R-12 | 24.6 | 38.96 | 24.26 | 49.3934
7705 | R-12 | 24.7 | 39.03 | 24.33 | 49.5359
7706 | R-12 | 24.8 | 39.1 | 24.4 | 49.6784
7707 | R-12 | 24.9 | 39.18 | 24.48 | 49.8413
7708 | R-12 | 25 | 39.25 | 24.55 | 49.9838
7709 | R-12 | 25.1 | 39.32 | 24.62 | 50.1263
7710 | R-12 | 25.2 | 39.4 | 24.7 | 50.2892
7711 | R-12 | 25.3 | 39.47 | 24.77 | 50.4317
7712 | R-12 | 25.4 | 39.55 | 24.85 | 50.5946
7713 | R-12 | 25.5 | 39.62 | 24.92 | 50.7371
7714 | R-12 | 25.6 | 39.7 | 25 | 50.9
7715 | R-12 | 25.7 | 39.77 | 25.07 | 51.0425
7716 | R-12 | 25.8 | 39.85 | 25.15 | 51.2054
7717 | R-12 | 25.9 | 39.92 | 25.22 | 51.3479
7718 | R-12 | 26 | 40 | 25.3 | 51.5108
7719 | R-12 | 26.1 | 40.07 | 25.37 | 51.6533
7720 | R-12 | 26.2 | 40.15 | 25.45 | 51.8162
7721 | R-12 | 26.3 | 40.22 | 25.52 | 51.9587
7722 | R-12 | 26.4 | 40.3 | 25.6 | 52.1216
7723 | R-12 | 26.5 | 40.37 | 25.67 | 52.2641
7724 | R-12 | 26.6 | 40.45 | 25.75 | 52.427
7725 | R-12 | 26.7 | 40.52 | 25.82 | 52.5695
7726 | R-12 | 26.8 | 40.6 | 25.9 | 52.7324
7727 | R-12 | 26.9 | 40.67 | 25.97 | 52.8749
7728 | R-12 | 27 | 40.75 | 26.05 | 53.0378
7729 | R-12 | 27.1 | 40.83 | 26.13 | 53.2007
7730 | R-12 | 27.2 | 40.9 | 26.2 | 53.3432
7731 | R-12 | 27.3 | 40.98 | 26.28 | 53.5061
7732 | R-12 | 27.4 | 41.06 | 26.36 | 53.669
7733 | R-12 | 27.5 | 41.13 | 26.43 | 53.8115
7734 | R-12 | 27.6 | 41.21 | 26.51 | 53.9744
7735 | R-12 | 27.7 | 41.29 | 26.59 | 54.1372
7736 | R-12 | 27.8 | 41.36 | 26.66 | 54.2798
7737 | R-12 | 27.9 | 41.44 | 26.74 | 54.4426
7738 | R-12 | 28 | 41.52 | 26.82 | 54.6055
7739 | R-12 | 28.1 | 41.59 | 26.89 | 54.748
7740 | R-12 | 28.2 | 41.67 | 26.97 | 54.9109
7741 | R-12 | 28.3 | 41.75 | 27.05 | 55.0738
7742 | R-12 | 28.4 | 41.83 | 27.13 | 55.2367
7743 | R-12 | 28.5 | 41.9 | 27.2 | 55.3792
7744 | R-12 | 28.6 | 41.98 | 27.28 | 55.5421
7745 | R-12 | 28.7 | 42.06 | 27.36 | 55.705
7746 | R-12 | 28.8 | 42.14 | 27.44 | 55.8678
7747 | R-12 | 28.9 | 42.22 | 27.52 | 56.0307
7748 | R-12 | 29 | 42.29 | 27.59 | 56.1732
7749 | R-12 | 29.1 | 42.37 | 27.67 | 56.3361
7750 | R-12 | 29.2 | 42.45 | 27.75 | 56.499
7751 | R-12 | 29.3 | 42.53 | 27.83 | 56.6619
7752 | R-12 | 29.4 | 42.61 | 27.91 | 56.8248
7753 | R-12 | 29.5 | 42.69 | 27.99 | 56.9876
7754 | R-12 | 29.6 | 42.77 | 28.07 | 57.1505
7755 | R-12 | 29.7 | 42.85 | 28.15 | 57.3134
7756 | R-12 | 29.8 | 42.92 | 28.22 | 57.4559
7757 | R-12 | 29.9 | 43 | 28.3 | 57.6188
7758 | R-12 | 30 | 43.08 | 28.38 | 57.7817
7759 | R-12 | 30.1 | 43.16 | 28.46 | 57.9446
7760 | R-12 | 30.2 | 43.24 | 28.54 | 58.1074
7761 | R-12 | 30.3 | 43.32 | 28.62 | 58.2703
7762 | R-12 | 30.4 | 43.4 | 28.7 | 58.4332
7763 | R-12 | 30.5 | 43.48 | 28.78 | 58.5961
7764 | R-12 | 30.6 | 43.56 | 28.86 | 58.759
7765 | R-12 | 30.7 | 43.64 | 28.94 | 58.9218
7766 | R-12 | 30.8 | 43.72 | 29.02 | 59.0847
7767 | R-12 | 30.9 | 43.8 | 29.1 | 59.2476
7768 | R-12 | 31 | 43.88 | 29.18 | 59.4105
7769 | R-12 | 31.1 | 43.96 | 29.26 | 59.5734
7770 | R-12 | 31.2 | 44.04 | 29.34 | 59.7362
7771 | R-12 | 31.3 | 44.12 | 29.42 | 59.8991
7772 | R-12 | 31.4 | 44.21 | 29.51 | 60.0824
7773 | R-12 | 31.5 | 44.29 | 29.59 | 60.2452
7774 | R-12 | 31.6 | 44.37 | 29.67 | 60.4081
7775 | R-12 | 31.7 | 44.45 | 29.75 | 60.571
7776 | R-12 | 31.8 | 44.53 | 29.83 | 60.7339
7777 | R-12 | 31.9 | 44.61 | 29.91 | 60.8968
7778 | R-12 | 32 | 44.69 | 29.99 | 61.0596
7779 | R-12 | 32.1 | 44.77 | 30.07 | 61.2225
7780 | R-12 | 32.2 | 44.86 | 30.16 | 61.4058
7781 | R-12 | 32.3 | 44.94 | 30.24 | 61.5686
7782 | R-12 | 32.4 | 45.02 | 30.32 | 61.7315
7783 | R-12 | 32.5 | 45.1 | 30.4 | 61.8944
7784 | R-12 | 32.6 | 45.18 | 30.48 | 62.0573
7785 | R-12 | 32.7 | 45.27 | 30.57 | 62.2405
7786 | R-12 | 32.8 | 45.35 | 30.65 | 62.4034
7787 | R-12 | 32.9 | 45.43 | 30.73 | 62.5663
7788 | R-12 | 33 | 45.51 | 30.81 | 62.7292
7789 | R-12 | 33.1 | 45.6 | 30.9 | 62.9124
7790 | R-12 | 33.2 | 45.68 | 30.98 | 63.0753
7791 | R-12 | 33.3 | 45.76 | 31.06 | 63.2382
7792 | R-12 | 33.4 | 45.85 | 31.15 | 63.4214
7793 | R-12 | 33.5 | 45.93 | 31.23 | 63.5843
7794 | R-12 | 33.6 | 46.01 | 31.31 | 63.7472
7795 | R-12 | 33.7 | 46.1 | 31.4 | 63.9304
7796 | R-12 | 33.8 | 46.18 | 31.48 | 64.0933
7797 | R-12 | 33.9 | 46.26 | 31.56 | 64.2562
7798 | R-12 | 34 | 46.35 | 31.65 | 64.4394
7799 | R-12 | 34.1 | 46.43 | 31.73 | 64.6023
7800 | R-12 | 34.2 | 46.52 | 31.82 | 64.7855
7801 | R-12 | 34.3 | 46.6 | 31.9 | 64.9484
7802 | R-12 | 34.4 | 46.68 | 31.98 | 65.1113
7803 | R-12 | 34.5 | 46.77 | 32.07 | 65.2945
7804 | R-12 | 34.6 | 46.85 | 32.15 | 65.4574
7805 | R-12 | 34.7 | 46.94 | 32.24 | 65.6406
7806 | R-12 | 34.8 | 47.02 | 32.32 | 65.8035
7807 | R-12 | 34.9 | 47.11 | 32.41 | 65.9868
7808 | R-12 | 35 | 47.19 | 32.49 | 66.1496
7809 | R-12 | 35.1 | 47.28 | 32.58 | 66.3329
7810 | R-12 | 35.2 | 47.36 | 32.66 | 66.4958
7811 | R-12 | 35.3 | 47.45 | 32.75 | 66.679
7812 | R-12 | 35.4 | 47.53 | 32.83 | 66.8419
7813 | R-12 | 35.5 | 47.62 | 32.92 | 67.0251
7814 | R-12 | 35.6 | 47.7 | 33 | 67.188
7815 | R-12 | 35.7 | 47.79 | 33.09 | 67.3712
7816 | R-12 | 35.8 | 47.88 | 33.18 | 67.5545
7817 | R-12 | 35.9 | 47.96 | 33.26 | 67.7174
7818 | R-12 | 36 | 48.05 | 33.35 | 67.9006
7819 | R-12 | 36.1 | 48.13 | 33.43 | 68.0635
7820 | R-12 | 36.2 | 48.22 | 33.52 | 68.2467
7821 | R-12 | 36.3 | 48.31 | 33.61 | 68.43
7822 | R-12 | 36.4 | 48.39 | 33.69 | 68.5928
7823 | R-12 | 36.5 | 48.48 | 33.78 | 68.7761
7824 | R-12 | 36.6 | 48.57 | 33.87 | 68.9593
7825 | R-12 | 36.7 | 48.65 | 33.95 | 69.1222
7826 | R-12 | 36.8 | 48.74 | 34.04 | 69.3054
7827 | R-12 | 36.9 | 48.83 | 34.13 | 69.4887
7828 | R-12 | 37 | 48.92 | 34.22 | 69.6719
7829 | R-12 | 37.1 | 49 | 34.3 | 69.8348
7830 | R-12 | 37.2 | 49.09 | 34.39 | 70.018
7831 | R-12 | 37.3 | 49.18 | 34.48 | 70.2013
7832 | R-12 | 37.4 | 49.27 | 34.57 | 70.3845
7833 | R-12 | 37.5 | 49.35 | 34.65 | 70.5474
7834 | R-12 | 37.6 | 49.44 | 34.74 | 70.7306
7835 | R-12 | 37.7 | 49.53 | 34.83 | 70.9139
7836 | R-12 | 37.8 | 49.62 | 34.92 | 71.0971
7837 | R-12 | 37.9 | 49.71 | 35.01 | 71.2804
7838 | R-12 | 38 | 49.8 | 35.1 | 71.4636
7839 | R-12 | 38.1 | 49.88 | 35.18 | 71.6265
7840 | R-12 | 38.2 | 49.97 | 35.27 | 71.8097
7841 | R-12 | 38.3 | 50.06 | 35.36 | 71.993
7842 | R-12 | 38.4 | 50.15 | 35.45 | 72.1762
7843 | R-12 | 38.5 | 50.24 | 35.54 | 72.3594
7844 | R-12 | 38.6 | 50.33 | 35.63 | 72.5427
7845 | R-12 | 38.7 | 50.42 | 35.72 | 72.7259
7846 | R-12 | 38.8 | 50.51 | 35.81 | 72.9092
7847 | R-12 | 38.9 | 50.6 | 35.9 | 73.0924
7848 | R-12 | 39 | 50.69 | 35.99 | 73.2756
7849 | R-12 | 39.1 | 50.78 | 36.08 | 73.4589
7850 | R-12 | 39.2 | 50.87 | 36.17 | 73.6421
7851 | R-12 | 39.3 | 50.96 | 36.26 | 73.8254
7852 | R-12 | 39.4 | 51.05 | 36.35 | 74.0086
7853 | R-12 | 39.5 | 51.14 | 36.44 | 74.1918
7854 | R-12 | 39.6 | 51.23 | 36.53 | 74.3751
7855 | R-12 | 39.7 | 51.32 | 36.62 | 74.5583
7856 | R-12 | 39.8 | 51.41 | 36.71 | 74.7416
7857 | R-12 | 39.9 | 51.5 | 36.8 | 74.9248
7858 | R-12 | 40 | 51.59 | 36.89 | 75.108
7859 | R-12 | 40.1 | 51.68 | 36.98 | 75.2913
7860 | R-12 | 40.2 | 51.77 | 37.07 | 75.4745
7861 | R-12 | 40.3 | 51.86 | 37.16 | 75.6578
7862 | R-12 | 40.4 | 51.95 | 37.25 | 75.841
7863 | R-12 | 40.5 | 52.05 | 37.35 | 76.0446
7864 | R-12 | 40.6 | 52.14 | 37.44 | 76.2278
7865 | R-12 | 40.7 | 52.23 | 37.53 | 76.4111
7866 | R-12 | 40.8 | 52.32 | 37.62 | 76.5943
7867 | R-12 | 40.9 | 52.41 | 37.71 | 76.7776
7868 | R-12 | 41 | 52.51 | 37.81 | 76.9812
7869 | R-12 | 41.1 | 52.6 | 37.9 | 77.1644
7870 | R-12 | 41.2 | 52.69 | 37.99 | 77.3476
7871 | R-12 | 41.3 | 52.78 | 38.08 | 77.5309
7872 | R-12 | 41.4 | 52.87 | 38.17 | 77.7141
7873 | R-12 | 41.5 | 52.97 | 38.27 | 77.9177
7874 | R-12 | 41.6 | 53.06 | 38.36 | 78.101
7875 | R-12 | 41.7 | 53.15 | 38.45 | 78.2842
7876 | R-12 | 41.8 | 53.25 | 38.55 | 78.4878
7877 | R-12 | 41.9 | 53.34 | 38.64 | 78.671
7878 | R-12 | 42 | 53.43 | 38.73 | 78.8543
7879 | R-12 | 42.1 | 53.53 | 38.83 | 79.0579
7880 | R-12 | 42.2 | 53.62 | 38.92 | 79.2411
7881 | R-12 | 42.3 | 53.71 | 39.01 | 79.4244
7882 | R-12 | 42.4 | 53.81 | 39.11 | 79.628
7883 | R-12 | 42.5 | 53.9 | 39.2 | 79.8112
7884 | R-12 | 42.6 | 54 | 39.3 | 80.0148
7885 | R-12 | 42.7 | 54.09 | 39.39 | 80.198
7886 | R-12 | 42.8 | 54.18 | 39.48 | 80.3813
7887 | R-12 | 42.9 | 54.28 | 39.58 | 80.5849
7888 | R-12 | 43 | 54.37 | 39.67 | 80.7681
7889 | R-12 | 43.1 | 54.47 | 39.77 | 80.9717
7890 | R-12 | 43.2 | 54.56 | 39.86 | 81.155
7891 | R-12 | 43.3 | 54.66 | 39.96 | 81.3586
7892 | R-12 | 43.4 | 54.75 | 40.05 | 81.5418
7893 | R-12 | 43.5 | 54.85 | 40.15 | 81.7454
7894 | R-12 | 43.6 | 54.94 | 40.24 | 81.9286
7895 | R-12 | 43.7 | 55.04 | 40.34 | 82.1322
7896 | R-12 | 43.8 | 55.13 | 40.43 | 82.3155
7897 | R-12 | 43.9 | 55.23 | 40.53 | 82.5191
7898 | R-12 | 44 | 55.32 | 40.62 | 82.7023
7899 | R-12 | 44.1 | 55.42 | 40.72 | 82.9059
7900 | R-12 | 44.2 | 55.52 | 40.82 | 83.1095
7901 | R-12 | 44.3 | 55.61 | 40.91 | 83.2928
7902 | R-12 | 44.4 | 55.71 | 41.01 | 83.4964
7903 | R-12 | 44.5 | 55.81 | 41.11 | 83.7
7904 | R-12 | 44.6 | 55.9 | 41.2 | 83.8832
7905 | R-12 | 44.7 | 56 | 41.3 | 84.0868
7906 | R-12 | 44.8 | 56.1 | 41.4 | 84.2904
7907 | R-12 | 44.9 | 56.19 | 41.49 | 84.4736
7908 | R-12 | 45 | 56.29 | 41.59 | 84.6772
7909 | R-12 | 45.1 | 56.39 | 41.69 | 84.8808
7910 | R-12 | 45.2 | 56.48 | 41.78 | 85.0641
7911 | R-12 | 45.3 | 56.58 | 41.88 | 85.2677
7912 | R-12 | 45.4 | 56.68 | 41.98 | 85.4713
7913 | R-12 | 45.5 | 56.78 | 42.08 | 85.6749
7914 | R-12 | 45.6 | 56.87 | 42.17 | 85.8581
7915 | R-12 | 45.7 | 56.97 | 42.27 | 86.0617
7916 | R-12 | 45.8 | 57.07 | 42.37 | 86.2653
7917 | R-12 | 45.9 | 57.17 | 42.47 | 86.4689
7918 | R-12 | 46 | 57.27 | 42.57 | 86.6725
7919 | R-12 | 46.1 | 57.36 | 42.66 | 86.8558
7920 | R-12 | 46.2 | 57.46 | 42.76 | 87.0594
7921 | R-12 | 46.3 | 57.56 | 42.86 | 87.263
7922 | R-12 | 46.4 | 57.66 | 42.96 | 87.4666
7923 | R-12 | 46.5 | 57.76 | 43.06 | 87.6702
7924 | R-12 | 46.6 | 57.86 | 43.16 | 87.8738
7925 | R-12 | 46.7 | 57.96 | 43.26 | 88.0774
7926 | R-12 | 46.8 | 58.06 | 43.36 | 88.281
7927 | R-12 | 46.9 | 58.16 | 43.46 | 88.4846
7928 | R-12 | 47 | 58.26 | 43.56 | 88.6882
7929 | R-12 | 47.1 | 58.36 | 43.66 | 88.8918
7930 | R-12 | 47.2 | 58.46 | 43.76 | 89.0954
7931 | R-12 | 47.3 | 58.56 | 43.86 | 89.299
7932 | R-12 | 47.4 | 58.66 | 43.96 | 89.5026
7933 | R-12 | 47.5 | 58.76 | 44.06 | 89.7062
7934 | R-12 | 47.6 | 58.86 | 44.16 | 89.9098
7935 | R-12 | 47.7 | 58.96 | 44.26 | 90.1134
7936 | R-12 | 47.8 | 59.06 | 44.36 | 90.317
7937 | R-12 | 47.9 | 59.16 | 44.46 | 90.5206
7938 | R-12 | 48 | 59.26 | 44.56 | 90.7242
7939 | R-12 | 48.1 | 59.36 | 44.66 | 90.9278
7940 | R-12 | 48.2 | 59.46 | 44.76 | 91.1314
7941 | R-12 | 48.3 | 59.56 | 44.86 | 91.335
7942 | R-12 | 48.4 | 59.66 | 44.96 | 91.5386
7943 | R-12 | 48.5 | 59.76 | 45.06 | 91.7422
7944 | R-12 | 48.6 | 59.87 | 45.17 | 91.9661
7945 | R-12 | 48.7 | 59.97 | 45.27 | 92.1697
7946 | R-12 | 48.8 | 60.07 | 45.37 | 92.3733
7947 | R-12 | 48.9 | 60.17 | 45.47 | 92.5769
7948 | R-12 | 49 | 60.27 | 45.57 | 92.7805
7949 | R-12 | 49.1 | 60.38 | 45.68 | 93.0045
7950 | R-12 | 49.2 | 60.48 | 45.78 | 93.2081
7951 | R-12 | 49.3 | 60.58 | 45.88 | 93.4117
7952 | R-12 | 49.4 | 60.68 | 45.98 | 93.6153
7953 | R-12 | 49.5 | 60.79 | 46.09 | 93.8392
7954 | R-12 | 49.6 | 60.89 | 46.19 | 94.0428
7955 | R-12 | 49.7 | 60.99 | 46.29 | 94.2464
7956 | R-12 | 49.8 | 61.1 | 46.4 | 94.4704
7957 | R-12 | 49.9 | 61.2 | 46.5 | 94.674
7958 | R-12 | 50 | 61.3 | 46.6 | 94.8776
7959 | R-12 | 50.1 | 61.41 | 46.71 | 95.1016
7960 | R-12 | 50.2 | 61.51 | 46.81 | 95.3052
7961 | R-12 | 50.3 | 61.61 | 46.91 | 95.5088
7962 | R-12 | 50.4 | 61.72 | 47.02 | 95.7327
7963 | R-12 | 50.5 | 61.82 | 47.12 | 95.9363
7964 | R-12 | 50.6 | 61.93 | 47.23 | 96.1603
7965 | R-12 | 50.7 | 62.03 | 47.33 | 96.3639
7966 | R-12 | 50.8 | 62.13 | 47.43 | 96.5675
7967 | R-12 | 50.9 | 62.24 | 47.54 | 96.7914
7968 | R-12 | 51 | 62.34 | 47.64 | 96.995
7969 | R-12 | 51.1 | 62.45 | 47.75 | 97.219
7970 | R-12 | 51.2 | 62.55 | 47.85 | 97.4226
7971 | R-12 | 51.3 | 62.66 | 47.96 | 97.6466
7972 | R-12 | 51.4 | 62.76 | 48.06 | 97.8502
7973 | R-12 | 51.5 | 62.87 | 48.17 | 98.0741
7974 | R-12 | 51.6 | 62.98 | 48.28 | 98.2981
7975 | R-12 | 51.7 | 63.08 | 48.38 | 98.5017
7976 | R-12 | 51.8 | 63.19 | 48.49 | 98.7256
7977 | R-12 | 51.9 | 63.29 | 48.59 | 98.9292
7978 | R-12 | 52 | 63.4 | 48.7 | 99.1532
7979 | R-12 | 52.1 | 63.51 | 48.81 | 99.3772
7980 | R-12 | 52.2 | 63.61 | 48.91 | 99.5808
7981 | R-12 | 52.3 | 63.72 | 49.02 | 99.8047
7982 | R-12 | 52.4 | 63.82 | 49.12 | 100.0083
7983 | R-12 | 52.5 | 63.93 | 49.23 | 100.2323
7984 | R-12 | 52.6 | 64.04 | 49.34 | 100.4562
7985 | R-12 | 52.7 | 64.15 | 49.45 | 100.6802
7986 | R-12 | 52.8 | 64.25 | 49.55 | 100.8838
7987 | R-12 | 52.9 | 64.36 | 49.66 | 101.1078
7988 | R-12 | 53 | 64.47 | 49.77 | 101.3317
7989 | R-12 | 53.1 | 64.57 | 49.87 | 101.5353
7990 | R-12 | 53.2 | 64.68 | 49.98 | 101.7593
7991 | R-12 | 53.3 | 64.79 | 50.09 | 101.9832
7992 | R-12 | 53.4 | 64.9 | 50.2 | 102.2072
7993 | R-12 | 53.5 | 65.01 | 50.31 | 102.4312
7994 | R-12 | 53.6 | 65.11 | 50.41 | 102.6348
7995 | R-12 | 53.7 | 65.22 | 50.52 | 102.8587
7996 | R-12 | 53.8 | 65.33 | 50.63 | 103.0827
7997 | R-12 | 53.9 | 65.44 | 50.74 | 103.3066
7998 | R-12 | 54 | 65.55 | 50.85 | 103.5306
7999 | R-12 | 54.1 | 65.66 | 50.96 | 103.7546
8000 | R-12 | 54.2 | 65.77 | 51.07 | 103.9785
8001 | R-12 | 54.3 | 65.88 | 51.18 | 104.2025
8002 | R-12 | 54.4 | 65.98 | 51.28 | 104.4061
8003 | R-12 | 54.5 | 66.09 | 51.39 | 104.63
8004 | R-12 | 54.6 | 66.2 | 51.5 | 104.854
8005 | R-12 | 54.7 | 66.31 | 51.61 | 105.078
8006 | R-12 | 54.8 | 66.42 | 51.72 | 105.3019
8007 | R-12 | 54.9 | 66.53 | 51.83 | 105.5259
8008 | R-12 | 55 | 66.64 | 51.94 | 105.7498
8009 | R-12 | 55.1 | 66.75 | 52.05 | 105.9738
8010 | R-12 | 55.2 | 66.86 | 52.16 | 106.1978
8011 | R-12 | 55.3 | 66.97 | 52.27 | 106.4217
8012 | R-12 | 55.4 | 67.08 | 52.38 | 106.6457
8013 | R-12 | 55.5 | 67.2 | 52.5 | 106.89
8014 | R-12 | 55.6 | 67.31 | 52.61 | 107.114
8015 | R-12 | 55.7 | 67.42 | 52.72 | 107.3379
8016 | R-12 | 55.8 | 67.53 | 52.83 | 107.5619
8017 | R-12 | 55.9 | 67.64 | 52.94 | 107.7858
8018 | R-12 | 56 | 67.75 | 53.05 | 108.0098
8019 | R-12 | 56.1 | 67.86 | 53.16 | 108.2338
8020 | R-12 | 56.2 | 67.97 | 53.27 | 108.4577
8021 | R-12 | 56.3 | 68.09 | 53.39 | 108.702
8022 | R-12 | 56.4 | 68.2 | 53.5 | 108.926
8023 | R-12 | 56.5 | 68.31 | 53.61 | 109.15
8024 | R-12 | 56.6 | 68.42 | 53.72 | 109.3739
8025 | R-12 | 56.7 | 68.54 | 53.84 | 109.6182
8026 | R-12 | 56.8 | 68.65 | 53.95 | 109.8422
8027 | R-12 | 56.9 | 68.76 | 54.06 | 110.0662
8028 | R-12 | 57 | 68.87 | 54.17 | 110.2901
8029 | R-12 | 57.1 | 68.99 | 54.29 | 110.5344
8030 | R-12 | 57.2 | 69.1 | 54.4 | 110.7584
8031 | R-12 | 57.3 | 69.21 | 54.51 | 110.9824
8032 | R-12 | 57.4 | 69.33 | 54.63 | 111.2267
8033 | R-12 | 57.5 | 69.44 | 54.74 | 111.4506
8034 | R-12 | 57.6 | 69.55 | 54.85 | 111.6746
8035 | R-12 | 57.7 | 69.67 | 54.97 | 111.9189
8036 | R-12 | 57.8 | 69.78 | 55.08 | 112.1429
8037 | R-12 | 57.9 | 69.9 | 55.2 | 112.3872
8038 | R-12 | 58 | 70.01 | 55.31 | 112.6112
8039 | R-12 | 58.1 | 70.12 | 55.42 | 112.8351
8040 | R-12 | 58.2 | 70.24 | 55.54 | 113.0794
8041 | R-12 | 58.3 | 70.35 | 55.65 | 113.3034
8042 | R-12 | 58.4 | 70.47 | 55.77 | 113.5477
8043 | R-12 | 58.5 | 70.58 | 55.88 | 113.7717
8044 | R-12 | 58.6 | 70.7 | 56 | 114.016
8045 | R-12 | 58.7 | 70.81 | 56.11 | 114.24
8046 | R-12 | 58.8 | 70.93 | 56.23 | 114.4843
8047 | R-12 | 58.9 | 71.04 | 56.34 | 114.7082
8048 | R-12 | 59 | 71.16 | 56.46 | 114.9526
8049 | R-12 | 59.1 | 71.28 | 56.58 | 115.1969
8050 | R-12 | 59.2 | 71.39 | 56.69 | 115.4208
8051 | R-12 | 59.3 | 71.51 | 56.81 | 115.6652
8052 | R-12 | 59.4 | 71.62 | 56.92 | 115.8891
8053 | R-12 | 59.5 | 71.74 | 57.04 | 116.1334
8054 | R-12 | 59.6 | 71.86 | 57.16 | 116.3778
8055 | R-12 | 59.7 | 71.97 | 57.27 | 116.6017
8056 | R-12 | 59.8 | 72.09 | 57.39 | 116.846
8057 | R-12 | 59.9 | 72.21 | 57.51 | 117.0904
8058 | R-12 | 60 | 72.32 | 57.62 | 117.3143
8059 | R-12 | 60.1 | 72.44 | 57.74 | 117.5586
8060 | R-12 | 60.2 | 72.56 | 57.86 | 117.803
8061 | R-12 | 60.3 | 72.68 | 57.98 | 118.0473
8062 | R-12 | 60.4 | 72.79 | 58.09 | 118.2712
8063 | R-12 | 60.5 | 72.91 | 58.21 | 118.5156
8064 | R-12 | 60.6 | 73.03 | 58.33 | 118.7599
8065 | R-12 | 60.7 | 73.15 | 58.45 | 119.0042
8066 | R-12 | 60.8 | 73.26 | 58.56 | 119.2282
8067 | R-12 | 60.9 | 73.38 | 58.68 | 119.4725
8068 | R-12 | 61 | 73.5 | 58.8 | 119.7168
8069 | R-12 | 61.1 | 73.62 | 58.92 | 119.9611
8070 | R-12 | 61.2 | 73.74 | 59.04 | 120.2054
8071 | R-12 | 61.3 | 73.86 | 59.16 | 120.4498
8072 | R-12 | 61.4 | 73.98 | 59.28 | 120.6941
8073 | R-12 | 61.5 | 74.1 | 59.4 | 120.9384
8074 | R-12 | 61.6 | 74.21 | 59.51 | 121.1624
8075 | R-12 | 61.7 | 74.33 | 59.63 | 121.4067
8076 | R-12 | 61.8 | 74.45 | 59.75 | 121.651
8077 | R-12 | 61.9 | 74.57 | 59.87 | 121.8953
8078 | R-12 | 62 | 74.69 | 59.99 | 122.1396
8079 | R-12 | 62.1 | 74.81 | 60.11 | 122.384
8080 | R-12 | 62.2 | 74.93 | 60.23 | 122.6283
8081 | R-12 | 62.3 | 75.05 | 60.35 | 122.8726
8082 | R-12 | 62.4 | 75.17 | 60.47 | 123.1169
8083 | R-12 | 62.5 | 75.29 | 60.59 | 123.3612
8084 | R-12 | 62.6 | 75.42 | 60.72 | 123.6259
8085 | R-12 | 62.7 | 75.54 | 60.84 | 123.8702
8086 | R-12 | 62.8 | 75.66 | 60.96 | 124.1146
8087 | R-12 | 62.9 | 75.78 | 61.08 | 124.3589
8088 | R-12 | 63 | 75.9 | 61.2 | 124.6032
8089 | R-12 | 63.1 | 76.02 | 61.32 | 124.8475
8090 | R-12 | 63.2 | 76.14 | 61.44 | 125.0918
8091 | R-12 | 63.3 | 76.26 | 61.56 | 125.3362
8092 | R-12 | 63.4 | 76.39 | 61.69 | 125.6008
8093 | R-12 | 63.5 | 76.51 | 61.81 | 125.8452
8094 | R-12 | 63.6 | 76.63 | 61.93 | 126.0895
8095 | R-12 | 63.7 | 76.75 | 62.05 | 126.3338
8096 | R-12 | 63.8 | 76.88 | 62.18 | 126.5985
8097 | R-12 | 63.9 | 77 | 62.3 | 126.8428
8098 | R-12 | 64 | 77.12 | 62.42 | 127.0871
8099 | R-12 | 64.1 | 77.24 | 62.54 | 127.3314
8100 | R-12 | 64.2 | 77.37 | 62.67 | 127.5961
8101 | R-12 | 64.3 | 77.49 | 62.79 | 127.8404
8102 | R-12 | 64.4 | 77.61 | 62.91 | 128.0848
8103 | R-12 | 64.5 | 77.74 | 63.04 | 128.3494
8104 | R-12 | 64.6 | 77.86 | 63.16 | 128.5938
8105 | R-12 | 64.7 | 77.98 | 63.28 | 128.8381
8106 | R-12 | 64.8 | 78.11 | 63.41 | 129.1028
8107 | R-12 | 64.9 | 78.23 | 63.53 | 129.3471
8108 | R-12 | 65 | 78.36 | 63.66 | 129.6118
8109 | R-12 | 65.1 | 78.48 | 63.78 | 129.8561
8110 | R-12 | 65.2 | 78.61 | 63.91 | 130.1208
8111 | R-12 | 65.3 | 78.73 | 64.03 | 130.3651
8112 | R-12 | 65.4 | 78.85 | 64.15 | 130.6094
8113 | R-12 | 65.5 | 78.98 | 64.28 | 130.8741
8114 | R-12 | 65.6 | 79.11 | 64.41 | 131.1388
8115 | R-12 | 65.7 | 79.23 | 64.53 | 131.3831
8116 | R-12 | 65.8 | 79.36 | 64.66 | 131.6478
8117 | R-12 | 65.9 | 79.48 | 64.78 | 131.8921
8118 | R-12 | 66 | 79.61 | 64.91 | 132.1568
8119 | R-12 | 66.1 | 79.73 | 65.03 | 132.4011
8120 | R-12 | 66.2 | 79.86 | 65.16 | 132.6658
8121 | R-12 | 66.3 | 79.98 | 65.28 | 132.9101
8122 | R-12 | 66.4 | 80.11 | 65.41 | 133.1748
8123 | R-12 | 66.5 | 80.24 | 65.54 | 133.4394
8124 | R-12 | 66.6 | 80.36 | 65.66 | 133.6838
8125 | R-12 | 66.7 | 80.49 | 65.79 | 133.9484
8126 | R-12 | 66.8 | 80.62 | 65.92 | 134.2131
8127 | R-12 | 66.9 | 80.74 | 66.04 | 134.4574
8128 | R-12 | 67 | 80.87 | 66.17 | 134.7221
8129 | R-12 | 67.1 | 81 | 66.3 | 134.9868
8130 | R-12 | 67.2 | 81.13 | 66.43 | 135.2515
8131 | R-12 | 67.3 | 81.25 | 66.55 | 135.4958
8132 | R-12 | 67.4 | 81.38 | 66.68 | 135.7605
8133 | R-12 | 67.5 | 81.51 | 66.81 | 136.0252
8134 | R-12 | 67.6 | 81.64 | 66.94 | 136.2898
8135 | R-12 | 67.7 | 81.77 | 67.07 | 136.5545
8136 | R-12 | 67.8 | 81.89 | 67.19 | 136.7988
8137 | R-12 | 67.9 | 82.02 | 67.32 | 137.0635
8138 | R-12 | 68 | 82.15 | 67.45 | 137.3282
8139 | R-12 | 68.1 | 82.28 | 67.58 | 137.5929
8140 | R-12 | 68.2 | 82.41 | 67.71 | 137.8576
8141 | R-12 | 68.3 | 82.54 | 67.84 | 138.1222
8142 | R-12 | 68.4 | 82.67 | 67.97 | 138.3869
8143 | R-12 | 68.5 | 82.8 | 68.1 | 138.6516
8144 | R-12 | 68.6 | 82.93 | 68.23 | 138.9163
8145 | R-12 | 68.7 | 83.06 | 68.36 | 139.181
8146 | R-12 | 68.8 | 83.19 | 68.49 | 139.4456
8147 | R-12 | 68.9 | 83.32 | 68.62 | 139.7103
8148 | R-12 | 69 | 83.45 | 68.75 | 139.975
8149 | R-12 | 69.1 | 83.58 | 68.88 | 140.2397
8150 | R-12 | 69.2 | 83.71 | 69.01 | 140.5044
8151 | R-12 | 69.3 | 83.84 | 69.14 | 140.769
8152 | R-12 | 69.4 | 83.97 | 69.27 | 141.0337
8153 | R-12 | 69.5 | 84.1 | 69.4 | 141.2984
8154 | R-12 | 69.6 | 84.23 | 69.53 | 141.5631
8155 | R-12 | 69.7 | 84.36 | 69.66 | 141.8278
8156 | R-12 | 69.8 | 84.49 | 69.79 | 142.0924
8157 | R-12 | 69.9 | 84.62 | 69.92 | 142.3571
8158 | R-12 | 70 | 84.76 | 70.06 | 142.6422
8159 | R-12 | 70.1 | 84.89 | 70.19 | 142.9068
8160 | R-12 | 70.2 | 85.02 | 70.32 | 143.1715
8161 | R-12 | 70.3 | 85.15 | 70.45 | 143.4362
8162 | R-12 | 70.4 | 85.28 | 70.58 | 143.7009
8163 | R-12 | 70.5 | 85.42 | 70.72 | 143.9859
8164 | R-12 | 70.6 | 85.55 | 70.85 | 144.2506
8165 | R-12 | 70.7 | 85.68 | 70.98 | 144.5153
8166 | R-12 | 70.8 | 85.82 | 71.12 | 144.8003
8167 | R-12 | 70.9 | 85.95 | 71.25 | 145.065
8168 | R-12 | 71 | 86.08 | 71.38 | 145.3297
8169 | R-12 | 71.1 | 86.22 | 71.52 | 145.6147
8170 | R-12 | 71.2 | 86.35 | 71.65 | 145.8794
8171 | R-12 | 71.3 | 86.48 | 71.78 | 146.1441
8172 | R-12 | 71.4 | 86.62 | 71.92 | 146.4291
8173 | R-12 | 71.5 | 86.75 | 72.05 | 146.6938
8174 | R-12 | 71.6 | 86.88 | 72.18 | 146.9585
8175 | R-12 | 71.7 | 87.02 | 72.32 | 147.2435
8176 | R-12 | 71.8 | 87.15 | 72.45 | 147.5082
8177 | R-12 | 71.9 | 87.29 | 72.59 | 147.7932
8178 | R-12 | 72 | 87.42 | 72.72 | 148.0579
8179 | R-12 | 72.1 | 87.56 | 72.86 | 148.343
8180 | R-12 | 72.2 | 87.69 | 72.99 | 148.6076
8181 | R-12 | 72.3 | 87.83 | 73.13 | 148.8927
8182 | R-12 | 72.4 | 87.96 | 73.26 | 149.1574
8183 | R-12 | 72.5 | 88.1 | 73.4 | 149.4424
8184 | R-12 | 72.6 | 88.23 | 73.53 | 149.7071
8185 | R-12 | 72.7 | 88.37 | 73.67 | 149.9921
8186 | R-12 | 72.8 | 88.51 | 73.81 | 150.2772
8187 | R-12 | 72.9 | 88.64 | 73.94 | 150.5418
8188 | R-12 | 73 | 88.78 | 74.08 | 150.8269
8189 | R-12 | 73.1 | 88.91 | 74.21 | 151.0916
8190 | R-12 | 73.2 | 89.05 | 74.35 | 151.3766
8191 | R-12 | 73.3 | 89.19 | 74.49 | 151.6616
8192 | R-12 | 73.4 | 89.32 | 74.62 | 151.9263
8193 | R-12 | 73.5 | 89.46 | 74.76 | 152.2114
8194 | R-12 | 73.6 | 89.6 | 74.9 | 152.4964
8195 | R-12 | 73.7 | 89.74 | 75.04 | 152.7814
8196 | R-12 | 73.8 | 89.87 | 75.17 | 153.0461
8197 | R-12 | 73.9 | 90.01 | 75.31 | 153.3312
8198 | R-12 | 74 | 90.15 | 75.45 | 153.6162
8199 | R-12 | 74.1 | 90.29 | 75.59 | 153.9012
8200 | R-12 | 74.2 | 90.43 | 75.73 | 154.1863
8201 | R-12 | 74.3 | 90.56 | 75.86 | 154.451
8202 | R-12 | 74.4 | 90.7 | 76 | 154.736
8203 | R-12 | 74.5 | 90.84 | 76.14 | 155.021
8204 | R-12 | 74.6 | 90.98 | 76.28 | 155.3061
8205 | R-12 | 74.7 | 91.12 | 76.42 | 155.5911
8206 | R-12 | 74.8 | 91.26 | 76.56 | 155.8762
8207 | R-12 | 74.9 | 91.4 | 76.7 | 156.1612
8208 | R-12 | 75 | 91.54 | 76.84 | 156.4462
8209 | R-12 | 75.1 | 91.68 | 76.98 | 156.7313
8210 | R-12 | 75.2 | 91.82 | 77.12 | 157.0163
8211 | R-12 | 75.3 | 91.96 | 77.26 | 157.3014
8212 | R-12 | 75.4 | 92.1 | 77.4 | 157.5864
8213 | R-12 | 75.5 | 92.24 | 77.54 | 157.8714
8214 | R-12 | 75.6 | 92.38 | 77.68 | 158.1565
8215 | R-12 | 75.7 | 92.52 | 77.82 | 158.4415
8216 | R-12 | 75.8 | 92.66 | 77.96 | 158.7266
8217 | R-12 | 75.9 | 92.8 | 78.1 | 159.0116
8218 | R-12 | 76 | 92.94 | 78.24 | 159.2966
8219 | R-12 | 76.1 | 93.08 | 78.38 | 159.5817
8220 | R-12 | 76.2 | 93.22 | 78.52 | 159.8667
8221 | R-12 | 76.3 | 93.36 | 78.66 | 160.1518
8222 | R-12 | 76.4 | 93.5 | 78.8 | 160.4368
8223 | R-12 | 76.5 | 93.65 | 78.95 | 160.7422
8224 | R-12 | 76.6 | 93.79 | 79.09 | 161.0272
8225 | R-12 | 76.7 | 93.93 | 79.23 | 161.3123
8226 | R-12 | 76.8 | 94.07 | 79.37 | 161.5973
8227 | R-12 | 76.9 | 94.22 | 79.52 | 161.9027
8228 | R-12 | 77 | 94.36 | 79.66 | 162.1878
8229 | R-12 | 77.1 | 94.5 | 79.8 | 162.4728
8230 | R-12 | 77.2 | 94.64 | 79.94 | 162.7578
8231 | R-12 | 77.3 | 94.79 | 80.09 | 163.0632
8232 | R-12 | 77.4 | 94.93 | 80.23 | 163.3483
8233 | R-12 | 77.5 | 95.07 | 80.37 | 163.6333
8234 | R-12 | 77.6 | 95.22 | 80.52 | 163.9387
8235 | R-12 | 77.7 | 95.36 | 80.66 | 164.2238
8236 | R-12 | 77.8 | 95.5 | 80.8 | 164.5088
8237 | R-12 | 77.9 | 95.65 | 80.95 | 164.8142
8238 | R-12 | 78 | 95.79 | 81.09 | 165.0992
8239 | R-12 | 78.1 | 95.94 | 81.24 | 165.4046
8240 | R-12 | 78.2 | 96.08 | 81.38 | 165.6897
8241 | R-12 | 78.3 | 96.23 | 81.53 | 165.9951
8242 | R-12 | 78.4 | 96.37 | 81.67 | 166.2801
8243 | R-12 | 78.5 | 96.52 | 81.82 | 166.5855
8244 | R-12 | 78.6 | 96.66 | 81.96 | 166.8706
8245 | R-12 | 78.7 | 96.81 | 82.11 | 167.176
8246 | R-12 | 78.8 | 96.95 | 82.25 | 167.461
8247 | R-12 | 78.9 | 97.1 | 82.4 | 167.7664
8248 | R-12 | 79 | 97.24 | 82.54 | 168.0514
8249 | R-12 | 79.1 | 97.39 | 82.69 | 168.3568
8250 | R-12 | 79.2 | 97.54 | 82.84 | 168.6622
8251 | R-12 | 79.3 | 97.68 | 82.98 | 168.9473
8252 | R-12 | 79.4 | 97.83 | 83.13 | 169.2527
8253 | R-12 | 79.5 | 97.97 | 83.27 | 169.5377
8254 | R-12 | 79.6 | 98.12 | 83.42 | 169.8431
8255 | R-12 | 79.7 | 98.27 | 83.57 | 170.1485
8256 | R-12 | 79.8 | 98.42 | 83.72 | 170.4539
8257 | R-12 | 79.9 | 98.56 | 83.86 | 170.739
8258 | R-12 | 80 | 98.71 | 84.01 | 171.0444
8259 | R-12 | 80.1 | 98.86 | 84.16 | 171.3498
8260 | R-12 | 80.2 | 99.01 | 84.31 | 171.6552
8261 | R-12 | 80.3 | 99.15 | 84.45 | 171.9402
8262 | R-12 | 80.4 | 99.3 | 84.6 | 172.2456
8263 | R-12 | 80.5 | 99.45 | 84.75 | 172.551
8264 | R-12 | 80.6 | 99.6 | 84.9 | 172.8564
8265 | R-12 | 80.7 | 99.75 | 85.05 | 173.1618
8266 | R-12 | 80.8 | 99.9 | 85.2 | 173.4672
8267 | R-12 | 80.9 | 100 | 85.3 | 173.6708
8268 | R-12 | 81 | 100.2 | 85.5 | 174.078
8269 | R-12 | 81.1 | 100.3 | 85.6 | 174.2816
8270 | R-12 | 81.2 | 100.5 | 85.8 | 174.6888
8271 | R-12 | 81.3 | 100.6 | 85.9 | 174.8924
8272 | R-12 | 81.4 | 100.8 | 86.1 | 175.2996
8273 | R-12 | 81.5 | 100.9 | 86.2 | 175.5032
8274 | R-12 | 81.6 | 101.1 | 86.4 | 175.9104
8275 | R-12 | 81.7 | 101.2 | 86.5 | 176.114
8276 | R-12 | 81.8 | 101.4 | 86.7 | 176.5212
8277 | R-12 | 81.9 | 101.5 | 86.8 | 176.7248
8278 | R-12 | 82 | 101.7 | 87 | 177.132
8279 | R-12 | 82.1 | 101.8 | 87.1 | 177.3356
8280 | R-12 | 82.2 | 102 | 87.3 | 177.7428
8281 | R-12 | 82.3 | 102.1 | 87.4 | 177.9464
8282 | R-12 | 82.4 | 102.3 | 87.6 | 178.3536
8283 | R-12 | 82.5 | 102.4 | 87.7 | 178.5572
8284 | R-12 | 82.6 | 102.6 | 87.9 | 178.9644
8285 | R-12 | 82.7 | 102.8 | 88.1 | 179.3716
8286 | R-12 | 82.8 | 102.9 | 88.2 | 179.5752
8287 | R-12 | 82.9 | 103.1 | 88.4 | 179.9824
8288 | R-12 | 83 | 103.2 | 88.5 | 180.186
8289 | R-12 | 83.1 | 103.4 | 88.7 | 180.5932
8290 | R-12 | 83.2 | 103.5 | 88.8 | 180.7968
8291 | R-12 | 83.3 | 103.7 | 89 | 181.204
8292 | R-12 | 83.4 | 103.8 | 89.1 | 181.4076
8293 | R-12 | 83.5 | 104 | 89.3 | 181.8148
8294 | R-12 | 83.6 | 104.1 | 89.4 | 182.0184
8295 | R-12 | 83.7 | 104.3 | 89.6 | 182.4256
8296 | R-12 | 83.8 | 104.4 | 89.7 | 182.6292
8297 | R-12 | 83.9 | 104.6 | 89.9 | 183.0364
8298 | R-12 | 84 | 104.7 | 90 | 183.24
8299 | R-12 | 84.1 | 104.9 | 90.2 | 183.6472
8300 | R-12 | 84.2 | 105.1 | 90.4 | 184.0544
8301 | R-12 | 84.3 | 105.2 | 90.5 | 184.258
8302 | R-12 | 84.4 | 105.4 | 90.7 | 184.6652
8303 | R-12 | 84.5 | 105.5 | 90.8 | 184.8688
8304 | R-12 | 84.6 | 105.7 | 91 | 185.276
8305 | R-12 | 84.7 | 105.8 | 91.1 | 185.4796
8306 | R-12 | 84.8 | 106 | 91.3 | 185.8868
8307 | R-12 | 84.9 | 106.1 | 91.4 | 186.0904
8308 | R-12 | 85 | 106.3 | 91.6 | 186.4976
8309 | R-12 | 85.1 | 106.4 | 91.7 | 186.7012
8310 | R-12 | 85.2 | 106.6 | 91.9 | 187.1084
8311 | R-12 | 85.3 | 106.8 | 92.1 | 187.5156
8312 | R-12 | 85.4 | 106.9 | 92.2 | 187.7192
8313 | R-12 | 85.5 | 107.1 | 92.4 | 188.1264
8314 | R-12 | 85.6 | 107.2 | 92.5 | 188.33
8315 | R-12 | 85.7 | 107.4 | 92.7 | 188.7372
8316 | R-12 | 85.8 | 107.5 | 92.8 | 188.9408
8317 | R-12 | 85.9 | 107.7 | 93 | 189.348
8318 | R-12 | 86 | 107.9 | 93.2 | 189.7552
8319 | R-12 | 86.1 | 108 | 93.3 | 189.9588
8320 | R-12 | 86.2 | 108.2 | 93.5 | 190.366
8321 | R-12 | 86.3 | 108.3 | 93.6 | 190.5696
8322 | R-12 | 86.4 | 108.5 | 93.8 | 190.9768
8323 | R-12 | 86.5 | 108.6 | 93.9 | 191.1804
8324 | R-12 | 86.6 | 108.8 | 94.1 | 191.5876
8325 | R-12 | 86.7 | 109 | 94.3 | 191.9948
8326 | R-12 | 86.8 | 109.1 | 94.4 | 192.1984
8327 | R-12 | 86.9 | 109.3 | 94.6 | 192.6056
8328 | R-12 | 87 | 109.4 | 94.7 | 192.8092
8329 | R-12 | 87.1 | 109.6 | 94.9 | 193.2164
8330 | R-12 | 87.2 | 109.8 | 95.1 | 193.6236
8331 | R-12 | 87.3 | 109.9 | 95.2 | 193.8272
8332 | R-12 | 87.4 | 110.1 | 95.4 | 194.2344
8333 | R-12 | 87.5 | 110.2 | 95.5 | 194.438
8334 | R-12 | 87.6 | 110.4 | 95.7 | 194.8452
8335 | R-12 | 87.7 | 110.6 | 95.9 | 195.2524
8336 | R-12 | 87.8 | 110.7 | 96 | 195.456
8337 | R-12 | 87.9 | 110.9 | 96.2 | 195.8632
8338 | R-12 | 88 | 111 | 96.3 | 196.0668
8339 | R-12 | 88.1 | 111.2 | 96.5 | 196.474
8340 | R-12 | 88.2 | 111.4 | 96.7 | 196.8812
8341 | R-12 | 88.3 | 111.5 | 96.8 | 197.0848
8342 | R-12 | 88.4 | 111.7 | 97 | 197.492
8343 | R-12 | 88.5 | 111.8 | 97.1 | 197.6956
8344 | R-12 | 88.6 | 112 | 97.3 | 198.1028
8345 | R-12 | 88.7 | 112.2 | 97.5 | 198.51
8346 | R-12 | 88.8 | 112.3 | 97.6 | 198.7136
8347 | R-12 | 88.9 | 112.5 | 97.8 | 199.1208
8348 | R-12 | 89 | 112.7 | 98 | 199.528
8349 | R-12 | 89.1 | 112.8 | 98.1 | 199.7316
8350 | R-12 | 89.2 | 113 | 98.3 | 200.1388
8351 | R-12 | 89.3 | 113.1 | 98.4 | 200.3424
8352 | R-12 | 89.4 | 113.3 | 98.6 | 200.7496
8353 | R-12 | 89.5 | 113.5 | 98.8 | 201.1568
8354 | R-12 | 89.6 | 113.6 | 98.9 | 201.3604
8355 | R-12 | 89.7 | 113.8 | 99.1 | 201.7676
8356 | R-12 | 89.8 | 114 | 99.3 | 202.1748
8357 | R-12 | 89.9 | 114.1 | 99.4 | 202.3784
8358 | R-12 | 90 | 114.3 | 99.6 | 202.7856
8359 | R-12 | 90.1 | 114.5 | 99.8 | 203.1928
8360 | R-12 | 90.2 | 114.6 | 99.9 | 203.3964
8361 | R-12 | 90.3 | 114.8 | 100.1 | 203.8036
8362 | R-12 | 90.4 | 115 | 100.3 | 204.2108
8363 | R-12 | 90.5 | 115.1 | 100.4 | 204.4144
8364 | R-12 | 90.6 | 115.3 | 100.6 | 204.8216
8365 | R-12 | 90.7 | 115.4 | 100.7 | 205.0252
8366 | R-12 | 90.8 | 115.6 | 100.9 | 205.4324
8367 | R-12 | 90.9 | 115.8 | 101.1 | 205.8396
8368 | R-12 | 91 | 115.9 | 101.2 | 206.0432
8369 | R-12 | 91.1 | 116.1 | 101.4 | 206.4504
8370 | R-12 | 91.2 | 116.3 | 101.6 | 206.8576
8371 | R-12 | 91.3 | 116.4 | 101.7 | 207.0612
8372 | R-12 | 91.4 | 116.6 | 101.9 | 207.4684
8373 | R-12 | 91.5 | 116.8 | 102.1 | 207.8756
8374 | R-12 | 91.6 | 116.9 | 102.2 | 208.0792
8375 | R-12 | 91.7 | 117.1 | 102.4 | 208.4864
8376 | R-12 | 91.8 | 117.3 | 102.6 | 208.8936
8377 | R-12 | 91.9 | 117.4 | 102.7 | 209.0972
8378 | R-12 | 92 | 117.6 | 102.9 | 209.5044
8379 | R-12 | 92.1 | 117.8 | 103.1 | 209.9116
8380 | R-12 | 92.2 | 118 | 103.3 | 210.3188
8381 | R-12 | 92.3 | 118.1 | 103.4 | 210.5224
8382 | R-12 | 92.4 | 118.3 | 103.6 | 210.9296
8383 | R-12 | 92.5 | 118.5 | 103.8 | 211.3368
8384 | R-12 | 92.6 | 118.6 | 103.9 | 211.5404
8385 | R-12 | 92.7 | 118.8 | 104.1 | 211.9476
8386 | R-12 | 92.8 | 119 | 104.3 | 212.3548
8387 | R-12 | 92.9 | 119.1 | 104.4 | 212.5584
8388 | R-12 | 93 | 119.3 | 104.6 | 212.9656
8389 | R-12 | 93.1 | 119.5 | 104.8 | 213.3728
8390 | R-12 | 93.2 | 119.6 | 104.9 | 213.5764
8391 | R-12 | 93.3 | 119.8 | 105.1 | 213.9836
8392 | R-12 | 93.4 | 120 | 105.3 | 214.3908
8393 | R-12 | 93.5 | 120.2 | 105.5 | 214.798
8394 | R-12 | 93.6 | 120.3 | 105.6 | 215.0016
8395 | R-12 | 93.7 | 120.5 | 105.8 | 215.4088
8396 | R-12 | 93.8 | 120.7 | 106 | 215.816
8397 | R-12 | 93.9 | 120.8 | 106.1 | 216.0196
8398 | R-12 | 94 | 121 | 106.3 | 216.4268
8399 | R-12 | 94.1 | 121.2 | 106.5 | 216.834
8400 | R-12 | 94.2 | 121.4 | 106.7 | 217.2412
8401 | R-12 | 94.3 | 121.5 | 106.8 | 217.4448
8402 | R-12 | 94.4 | 121.7 | 107 | 217.852
8403 | R-12 | 94.5 | 121.9 | 107.2 | 218.2592
8404 | R-12 | 94.6 | 122 | 107.3 | 218.4628
8405 | R-12 | 94.7 | 122.2 | 107.5 | 218.87
8406 | R-12 | 94.8 | 122.4 | 107.7 | 219.2772
8407 | R-12 | 94.9 | 122.6 | 107.9 | 219.6844
8408 | R-12 | 95 | 122.7 | 108 | 219.888
8409 | R-12 | 95.1 | 122.9 | 108.2 | 220.2952
8410 | R-12 | 95.2 | 123.1 | 108.4 | 220.7024
8411 | R-12 | 95.3 | 123.3 | 108.6 | 221.1096
8412 | R-12 | 95.4 | 123.4 | 108.7 | 221.3132
8413 | R-12 | 95.5 | 123.6 | 108.9 | 221.7204
8414 | R-12 | 95.6 | 123.8 | 109.1 | 222.1276
8415 | R-12 | 95.7 | 123.9 | 109.2 | 222.3312
8416 | R-12 | 95.8 | 124.1 | 109.4 | 222.7384
8417 | R-12 | 95.9 | 124.3 | 109.6 | 223.1456
8418 | R-12 | 96 | 124.5 | 109.8 | 223.5528
8419 | R-12 | 96.1 | 124.6 | 109.9 | 223.7564
8420 | R-12 | 96.2 | 124.8 | 110.1 | 224.1636
8421 | R-12 | 96.3 | 125 | 110.3 | 224.5708
8422 | R-12 | 96.4 | 125.2 | 110.5 | 224.978
8423 | R-12 | 96.5 | 125.4 | 110.7 | 225.3852
8424 | R-12 | 96.6 | 125.5 | 110.8 | 225.5888
8425 | R-12 | 96.7 | 125.7 | 111 | 225.996
8426 | R-12 | 96.8 | 125.9 | 111.2 | 226.4032
8427 | R-12 | 96.9 | 126.1 | 111.4 | 226.8104
8428 | R-12 | 97 | 126.2 | 111.5 | 227.014
8429 | R-12 | 97.1 | 126.4 | 111.7 | 227.4212
8430 | R-12 | 97.2 | 126.6 | 111.9 | 227.8284
8431 | R-12 | 97.3 | 126.8 | 112.1 | 228.2356
8432 | R-12 | 97.4 | 126.9 | 112.2 | 228.4392
8433 | R-12 | 97.5 | 127.1 | 112.4 | 228.8464
8434 | R-12 | 97.6 | 127.3 | 112.6 | 229.2536
8435 | R-12 | 97.7 | 127.5 | 112.8 | 229.6608
8436 | R-12 | 97.8 | 127.7 | 113 | 230.068
8437 | R-12 | 97.9 | 127.8 | 113.1 | 230.2716
8438 | R-12 | 98 | 128 | 113.3 | 230.6788
8439 | R-12 | 98.1 | 128.2 | 113.5 | 231.086
8440 | R-12 | 98.2 | 128.4 | 113.7 | 231.4932
8441 | R-12 | 98.3 | 128.5 | 113.8 | 231.6968
8442 | R-12 | 98.4 | 128.7 | 114 | 232.104
8443 | R-12 | 98.5 | 128.9 | 114.2 | 232.5112
8444 | R-12 | 98.6 | 129.1 | 114.4 | 232.9184
8445 | R-12 | 98.7 | 129.3 | 114.6 | 233.3256
8446 | R-12 | 98.8 | 129.4 | 114.7 | 233.5292
8447 | R-12 | 98.9 | 129.6 | 114.9 | 233.9364
8448 | R-12 | 99 | 129.8 | 115.1 | 234.3436
8449 | R-12 | 99.1 | 130 | 115.3 | 234.7508
8450 | R-12 | 99.2 | 130.2 | 115.5 | 235.158
8451 | R-12 | 99.3 | 130.3 | 115.6 | 235.3616
8452 | R-12 | 99.4 | 130.5 | 115.8 | 235.7688
8453 | R-12 | 99.5 | 130.7 | 116 | 236.176
8454 | R-12 | 99.6 | 130.9 | 116.2 | 236.5832
8455 | R-12 | 99.7 | 131.1 | 116.4 | 236.9904
8456 | R-12 | 99.8 | 131.3 | 116.6 | 237.3976
8457 | R-12 | 99.9 | 131.4 | 116.7 | 237.6012
8458 | R-12 | 100 | 131.6 | 116.9 | 238.0084
8459 | R-12 | 100.1 | 131.8 | 117.1 | 238.4156
8460 | R-12 | 100.2 | 132 | 117.3 | 238.8228
8461 | R-12 | 100.3 | 132.2 | 117.5 | 239.23
8462 | R-12 | 100.4 | 132.4 | 117.7 | 239.6372
8463 | R-12 | 100.5 | 132.5 | 117.8 | 239.8408
8464 | R-12 | 100.6 | 132.7 | 118 | 240.248
8465 | R-12 | 100.7 | 132.9 | 118.2 | 240.6552
8466 | R-12 | 100.8 | 133.1 | 118.4 | 241.0624
8467 | R-12 | 100.9 | 133.3 | 118.6 | 241.4696
8468 | R-12 | 101 | 133.5 | 118.8 | 241.8768
8469 | R-12 | 101.1 | 133.6 | 118.9 | 242.0804
8470 | R-12 | 101.2 | 133.8 | 119.1 | 242.4876
8471 | R-12 | 101.3 | 134 | 119.3 | 242.8948
8472 | R-12 | 101.4 | 134.2 | 119.5 | 243.302
8473 | R-12 | 101.5 | 134.4 | 119.7 | 243.7092
8474 | R-12 | 101.6 | 134.6 | 119.9 | 244.1164
8475 | R-12 | 101.7 | 134.7 | 120 | 244.32
8476 | R-12 | 101.8 | 134.9 | 120.2 | 244.7272
8477 | R-12 | 101.9 | 135.1 | 120.4 | 245.1344
8478 | R-12 | 102 | 135.3 | 120.6 | 245.5416
8479 | R-12 | 102.1 | 135.5 | 120.8 | 245.9488
8480 | R-12 | 102.2 | 135.7 | 121 | 246.356
8481 | R-12 | 102.3 | 135.9 | 121.2 | 246.7632
8482 | R-12 | 102.4 | 136.1 | 121.4 | 247.1704
8483 | R-12 | 102.5 | 136.2 | 121.5 | 247.374
8484 | R-12 | 102.6 | 136.4 | 121.7 | 247.7812
8485 | R-12 | 102.7 | 136.6 | 121.9 | 248.1884
8486 | R-12 | 102.8 | 136.8 | 122.1 | 248.5956
8487 | R-12 | 102.9 | 137 | 122.3 | 249.0028
8488 | R-12 | 103 | 137.2 | 122.5 | 249.41
8489 | R-12 | 103.1 | 137.4 | 122.7 | 249.8172
8490 | R-12 | 103.2 | 137.6 | 122.9 | 250.2244
8491 | R-12 | 103.3 | 137.7 | 123 | 250.428
8492 | R-12 | 103.4 | 137.9 | 123.2 | 250.8352
8493 | R-12 | 103.5 | 138.1 | 123.4 | 251.2424
8494 | R-12 | 103.6 | 138.3 | 123.6 | 251.6496
8495 | R-12 | 103.7 | 138.5 | 123.8 | 252.0568
8496 | R-12 | 103.8 | 138.7 | 124 | 252.464
8497 | R-12 | 103.9 | 138.9 | 124.2 | 252.8712
8498 | R-12 | 104 | 139.1 | 124.4 | 253.2784
8499 | R-12 | 104.1 | 139.3 | 124.6 | 253.6856
8500 | R-12 | 104.2 | 139.4 | 124.7 | 253.8892
8501 | R-12 | 104.3 | 139.6 | 124.9 | 254.2964
8502 | R-12 | 104.4 | 139.8 | 125.1 | 254.7036
8503 | R-12 | 104.5 | 140 | 125.3 | 255.1108
8504 | R-12 | 104.6 | 140.2 | 125.5 | 255.518
8505 | R-12 | 104.7 | 140.4 | 125.7 | 255.9252
8506 | R-12 | 104.8 | 140.6 | 125.9 | 256.3324
8507 | R-12 | 104.9 | 140.8 | 126.1 | 256.7396
8508 | R-12 | 105 | 141 | 126.3 | 257.1468
8509 | R-12 | 105.1 | 141.2 | 126.5 | 257.554
8510 | R-12 | 105.2 | 141.4 | 126.7 | 257.9612
8511 | R-12 | 105.3 | 141.6 | 126.9 | 258.3684
8512 | R-12 | 105.4 | 141.7 | 127 | 258.572
8513 | R-12 | 105.5 | 141.9 | 127.2 | 258.9792
8514 | R-12 | 105.6 | 142.1 | 127.4 | 259.3864
8515 | R-12 | 105.7 | 142.3 | 127.6 | 259.7936
8516 | R-12 | 105.8 | 142.5 | 127.8 | 260.2008
8517 | R-12 | 105.9 | 142.7 | 128 | 260.608
8518 | R-12 | 106 | 142.9 | 128.2 | 261.0152
8519 | R-12 | 106.1 | 143.1 | 128.4 | 261.4224
8520 | R-12 | 106.2 | 143.3 | 128.6 | 261.8296
8521 | R-12 | 106.3 | 143.5 | 128.8 | 262.2368
8522 | R-12 | 106.4 | 143.7 | 129 | 262.644
8523 | R-12 | 106.5 | 143.9 | 129.2 | 263.0512
8524 | R-12 | 106.6 | 144.1 | 129.4 | 263.4584
8525 | R-12 | 106.7 | 144.3 | 129.6 | 263.8656
8526 | R-12 | 106.8 | 144.5 | 129.8 | 264.2728
8527 | R-12 | 106.9 | 144.7 | 130 | 264.68
8528 | R-12 | 107 | 144.8 | 130.1 | 264.8836
8529 | R-12 | 107.1 | 145 | 130.3 | 265.2908
8530 | R-12 | 107.2 | 145.2 | 130.5 | 265.698
8531 | R-12 | 107.3 | 145.4 | 130.7 | 266.1052
8532 | R-12 | 107.4 | 145.6 | 130.9 | 266.5124
8533 | R-12 | 107.5 | 145.8 | 131.1 | 266.9196
8534 | R-12 | 107.6 | 146 | 131.3 | 267.3268
8535 | R-12 | 107.7 | 146.2 | 131.5 | 267.734
8536 | R-12 | 107.8 | 146.4 | 131.7 | 268.1412
8537 | R-12 | 107.9 | 146.6 | 131.9 | 268.5484
8538 | R-12 | 108 | 146.8 | 132.1 | 268.9556
8539 | R-12 | 108.1 | 147 | 132.3 | 269.3628
8540 | R-12 | 108.2 | 147.2 | 132.5 | 269.77
8541 | R-12 | 108.3 | 147.4 | 132.7 | 270.1772
8542 | R-12 | 108.4 | 147.6 | 132.9 | 270.5844
8543 | R-12 | 108.5 | 147.8 | 133.1 | 270.9916
8544 | R-12 | 108.6 | 148 | 133.3 | 271.3988
8545 | R-12 | 108.7 | 148.2 | 133.5 | 271.806
8546 | R-12 | 108.8 | 148.4 | 133.7 | 272.2132
8547 | R-12 | 108.9 | 148.6 | 133.9 | 272.6204
8548 | R-12 | 109 | 148.8 | 134.1 | 273.0276
8549 | R-12 | 109.1 | 149 | 134.3 | 273.4348
8550 | R-12 | 109.2 | 149.2 | 134.5 | 273.842
8551 | R-12 | 109.3 | 149.4 | 134.7 | 274.2492
8552 | R-12 | 109.4 | 149.6 | 134.9 | 274.6564
8553 | R-12 | 109.5 | 149.8 | 135.1 | 275.0636
8554 | R-12 | 109.6 | 150 | 135.3 | 275.4708
8555 | R-12 | 109.7 | 150.2 | 135.5 | 275.878
8556 | R-12 | 109.8 | 150.4 | 135.7 | 276.2852
8557 | R-12 | 109.9 | 150.6 | 135.9 | 276.6924
8558 | R-12 | 110 | 150.8 | 136.1 | 277.0996
8559 | R-12 | 110.1 | 151 | 136.3 | 277.5068
8560 | R-12 | 110.2 | 151.2 | 136.5 | 277.914
8561 | R-12 | 110.3 | 151.4 | 136.7 | 278.3212
8562 | R-12 | 110.4 | 151.6 | 136.9 | 278.7284
8563 | R-12 | 110.5 | 151.8 | 137.1 | 279.1356
8564 | R-12 | 110.6 | 152 | 137.3 | 279.5428
8565 | R-12 | 110.7 | 152.2 | 137.5 | 279.95
8566 | R-12 | 110.8 | 152.4 | 137.7 | 280.3572
8567 | R-12 | 110.9 | 152.6 | 137.9 | 280.7644
8568 | R-12 | 111 | 152.8 | 138.1 | 281.1716
8569 | R-12 | 111.1 | 153 | 138.3 | 281.5788
8570 | R-12 | 111.2 | 153.2 | 138.5 | 281.986
8571 | R-12 | 111.3 | 153.4 | 138.7 | 282.3932
8572 | R-12 | 111.4 | 153.6 | 138.9 | 282.8004
8573 | R-12 | 111.5 | 153.9 | 139.2 | 283.4112
8574 | R-12 | 111.6 | 154.1 | 139.4 | 283.8184
8575 | R-12 | 111.7 | 154.3 | 139.6 | 284.2256
8576 | R-12 | 111.8 | 154.5 | 139.8 | 284.6328
8577 | R-12 | 111.9 | 154.7 | 140 | 285.04
8578 | R-12 | 112 | 154.9 | 140.2 | 285.4472
8579 | R-12 | 112.1 | 155.1 | 140.4 | 285.8544
8580 | R-12 | 112.2 | 155.3 | 140.6 | 286.2616
8581 | R-12 | 112.3 | 155.5 | 140.8 | 286.6688
8582 | R-12 | 112.4 | 155.7 | 141 | 287.076
8583 | R-12 | 112.5 | 155.9 | 141.2 | 287.4832
8584 | R-12 | 112.6 | 156.1 | 141.4 | 287.8904
8585 | R-12 | 112.7 | 156.3 | 141.6 | 288.2976
8586 | R-12 | 112.8 | 156.5 | 141.8 | 288.7048
8587 | R-12 | 112.9 | 156.7 | 142 | 289.112
8588 | R-12 | 113 | 156.9 | 142.2 | 289.5192
8589 | R-12 | 113.1 | 157.2 | 142.5 | 290.13
8590 | R-12 | 113.2 | 157.4 | 142.7 | 290.5372
8591 | R-12 | 113.3 | 157.6 | 142.9 | 290.9444
8592 | R-12 | 113.4 | 157.8 | 143.1 | 291.3516
8593 | R-12 | 113.5 | 158 | 143.3 | 291.7588
8594 | R-12 | 113.6 | 158.2 | 143.5 | 292.166
8595 | R-12 | 113.7 | 158.4 | 143.7 | 292.5732
8596 | R-12 | 113.8 | 158.6 | 143.9 | 292.9804
8597 | R-12 | 113.9 | 158.8 | 144.1 | 293.3876
8598 | R-12 | 114 | 159 | 144.3 | 293.7948
8599 | R-12 | 114.1 | 159.2 | 144.5 | 294.202
8600 | R-12 | 114.2 | 159.4 | 144.7 | 294.6092
8601 | R-12 | 114.3 | 159.7 | 145 | 295.22
8602 | R-12 | 114.4 | 159.9 | 145.2 | 295.6272
8603 | R-12 | 114.5 | 160.1 | 145.4 | 296.0344
8604 | R-12 | 114.6 | 160.3 | 145.6 | 296.4416
8605 | R-12 | 114.7 | 160.5 | 145.8 | 296.8488
8606 | R-12 | 114.8 | 160.7 | 146 | 297.256
8607 | R-12 | 114.9 | 160.9 | 146.2 | 297.6632
8608 | R-12 | 115 | 161.1 | 146.4 | 298.0704
8609 | R-12 | 115.1 | 161.3 | 146.6 | 298.4776
8610 | R-12 | 115.2 | 161.6 | 146.9 | 299.0884
8611 | R-12 | 115.3 | 161.8 | 147.1 | 299.4956
8612 | R-12 | 115.4 | 162 | 147.3 | 299.9028
8613 | R-12 | 115.5 | 162.2 | 147.5 | 300.31
8614 | R-12 | 115.6 | 162.4 | 147.7 | 300.7172
8615 | R-12 | 115.7 | 162.6 | 147.9 | 301.1244
8616 | R-12 | 115.8 | 162.8 | 148.1 | 301.5316
8617 | R-12 | 115.9 | 163 | 148.3 | 301.9388
8618 | R-12 | 116 | 163.3 | 148.6 | 302.5496
8619 | R-12 | 116.1 | 163.5 | 148.8 | 302.9568
8620 | R-12 | 116.2 | 163.7 | 149 | 303.364
8621 | R-12 | 116.3 | 163.9 | 149.2 | 303.7712
8622 | R-12 | 116.4 | 164.1 | 149.4 | 304.1784
8623 | R-12 | 116.5 | 164.3 | 149.6 | 304.5856
8624 | R-12 | 116.6 | 164.5 | 149.8 | 304.9928
8625 | R-12 | 116.7 | 164.8 | 150.1 | 305.6036
8626 | R-12 | 116.8 | 165 | 150.3 | 306.0108
8627 | R-12 | 116.9 | 165.2 | 150.5 | 306.418
8628 | R-12 | 117 | 165.4 | 150.7 | 306.8252
8629 | R-12 | 117.1 | 165.6 | 150.9 | 307.2324
8630 | R-12 | 117.2 | 165.8 | 151.1 | 307.6396
8631 | R-12 | 117.3 | 166.1 | 151.4 | 308.2504
8632 | R-12 | 117.4 | 166.3 | 151.6 | 308.6576
8633 | R-12 | 117.5 | 166.5 | 151.8 | 309.0648
8634 | R-12 | 117.6 | 166.7 | 152 | 309.472
8635 | R-12 | 117.7 | 166.9 | 152.2 | 309.8792
8636 | R-12 | 117.8 | 167.1 | 152.4 | 310.2864
8637 | R-12 | 117.9 | 167.4 | 152.7 | 310.8972
8638 | R-12 | 118 | 167.6 | 152.9 | 311.3044
8639 | R-12 | 118.1 | 167.8 | 153.1 | 311.7116
8640 | R-12 | 118.2 | 168 | 153.3 | 312.1188
8641 | R-12 | 118.3 | 168.2 | 153.5 | 312.526
8642 | R-12 | 118.4 | 168.4 | 153.7 | 312.9332
8643 | R-12 | 118.5 | 168.7 | 154 | 313.544
8644 | R-12 | 118.6 | 168.9 | 154.2 | 313.9512
8645 | R-12 | 118.7 | 169.1 | 154.4 | 314.3584
8646 | R-12 | 118.8 | 169.3 | 154.6 | 314.7656
8647 | R-12 | 118.9 | 169.5 | 154.8 | 315.1728
8648 | R-12 | 119 | 169.8 | 155.1 | 315.7836
8649 | R-12 | 119.1 | 170 | 155.3 | 316.1908
8650 | R-12 | 119.2 | 170.2 | 155.5 | 316.598
8651 | R-12 | 119.3 | 170.4 | 155.7 | 317.0052
8652 | R-12 | 119.4 | 170.6 | 155.9 | 317.4124
8653 | R-12 | 119.5 | 170.9 | 156.2 | 318.0232
8654 | R-12 | 119.6 | 171.1 | 156.4 | 318.4304
8655 | R-12 | 119.7 | 171.3 | 156.6 | 318.8376
8656 | R-12 | 119.8 | 171.5 | 156.8 | 319.2448
8657 | R-12 | 119.9 | 171.7 | 157 | 319.652
8658 | R-12 | 120 | 172 | 157.3 | 320.2628
8659 | R-22 | -40 | 15.26 | 0.56 | NULL
8660 | R-22 | -39.8 | 15.34 | 0.64 | NULL
8661 | R-22 | -39.6 | 15.42 | 0.72 | NULL
8662 | R-22 | -39.4 | 15.5 | 0.8 | NULL
8663 | R-22 | -39.2 | 15.58 | 0.88 | NULL
8664 | R-22 | -39 | 15.66 | 0.96 | NULL
8665 | R-22 | -38.8 | 15.74 | 1.04 | NULL
8666 | R-22 | -38.6 | 15.82 | 1.12 | NULL
8667 | R-22 | -38.4 | 15.9 | 1.2 | NULL
8668 | R-22 | -38.2 | 15.99 | 1.29 | NULL
8669 | R-22 | -38 | 16.07 | 1.37 | NULL
8670 | R-22 | -37.8 | 16.15 | 1.45 | NULL
8671 | R-22 | -37.6 | 16.23 | 1.53 | NULL
8672 | R-22 | -37.4 | 16.31 | 1.61 | NULL
8673 | R-22 | -37.2 | 16.4 | 1.7 | NULL
8674 | R-22 | -37 | 16.48 | 1.78 | NULL
8675 | R-22 | -36.8 | 16.57 | 1.87 | NULL
8676 | R-22 | -36.6 | 16.65 | 1.95 | NULL
8677 | R-22 | -36.4 | 16.73 | 2.03 | NULL
8678 | R-22 | -36.2 | 16.82 | 2.12 | NULL
8679 | R-22 | -36 | 16.9 | 2.2 | NULL
8680 | R-22 | -35.8 | 16.99 | 2.29 | NULL
8681 | R-22 | -35.6 | 17.08 | 2.38 | NULL
8682 | R-22 | -35.4 | 17.16 | 2.46 | NULL
8683 | R-22 | -35.2 | 17.25 | 2.55 | NULL
8684 | R-22 | -35 | 17.34 | 2.64 | NULL
8685 | R-22 | -34.8 | 17.42 | 2.72 | NULL
8686 | R-22 | -34.6 | 17.51 | 2.81 | NULL
8687 | R-22 | -34.4 | 17.6 | 2.9 | NULL
8688 | R-22 | -34.2 | 17.69 | 2.99 | NULL
8689 | R-22 | -34 | 17.78 | 3.08 | NULL
8690 | R-22 | -33.8 | 17.87 | 3.17 | NULL
8691 | R-22 | -33.6 | 17.95 | 3.25 | NULL
8692 | R-22 | -33.4 | 18.04 | 3.34 | NULL
8693 | R-22 | -33.2 | 18.13 | 3.43 | NULL
8694 | R-22 | -33 | 18.22 | 3.52 | NULL
8695 | R-22 | -32.8 | 18.32 | 3.62 | NULL
8696 | R-22 | -32.6 | 18.41 | 3.71 | NULL
8697 | R-22 | -32.4 | 18.5 | 3.8 | NULL
8698 | R-22 | -32.2 | 18.59 | 3.89 | NULL
8699 | R-22 | -32 | 18.68 | 3.98 | NULL
8700 | R-22 | -31.8 | 18.77 | 4.07 | NULL
8701 | R-22 | -31.6 | 18.87 | 4.17 | NULL
8702 | R-22 | -31.4 | 18.96 | 4.26 | NULL
8703 | R-22 | -31.2 | 19.05 | 4.35 | NULL
8704 | R-22 | -31 | 19.15 | 4.45 | NULL
8705 | R-22 | -30.8 | 19.24 | 4.54 | NULL
8706 | R-22 | -30.6 | 19.34 | 4.64 | NULL
8707 | R-22 | -30.4 | 19.43 | 4.73 | NULL
8708 | R-22 | -30.2 | 19.53 | 4.83 | NULL
8709 | R-22 | -30 | 19.62 | 4.92 | NULL
8710 | R-22 | -29.8 | 19.72 | 5.02 | NULL
8711 | R-22 | -29.6 | 19.82 | 5.12 | NULL
8712 | R-22 | -29.4 | 19.91 | 5.21 | NULL
8713 | R-22 | -29.2 | 20.01 | 5.31 | NULL
8714 | R-22 | -29 | 20.11 | 5.41 | NULL
8715 | R-22 | -28.8 | 20.21 | 5.51 | NULL
8716 | R-22 | -28.6 | 20.31 | 5.61 | NULL
8717 | R-22 | -28.4 | 20.4 | 5.7 | NULL
8718 | R-22 | -28.2 | 20.5 | 5.8 | NULL
8719 | R-22 | -28 | 20.6 | 5.9 | NULL
8720 | R-22 | -27.8 | 20.7 | 6 | NULL
8721 | R-22 | -27.6 | 20.8 | 6.1 | NULL
8722 | R-22 | -27.4 | 20.9 | 6.2 | NULL
8723 | R-22 | -27.2 | 21.01 | 6.31 | NULL
8724 | R-22 | -27 | 21.11 | 6.41 | NULL
8725 | R-22 | -26.8 | 21.21 | 6.51 | NULL
8726 | R-22 | -26.6 | 21.31 | 6.61 | NULL
8727 | R-22 | -26.4 | 21.41 | 6.71 | NULL
8728 | R-22 | -26.2 | 21.52 | 6.82 | NULL
8729 | R-22 | -26 | 21.62 | 6.92 | NULL
8730 | R-22 | -25.8 | 21.72 | 7.02 | NULL
8731 | R-22 | -25.6 | 21.83 | 7.13 | NULL
8732 | R-22 | -25.4 | 21.93 | 7.23 | NULL
8733 | R-22 | -25.2 | 22.04 | 7.34 | NULL
8734 | R-22 | -25 | 22.14 | 7.44 | NULL
8735 | R-22 | -24.8 | 22.25 | 7.55 | NULL
8736 | R-22 | -24.6 | 22.35 | 7.65 | NULL
8737 | R-22 | -24.4 | 22.46 | 7.76 | NULL
8738 | R-22 | -24.2 | 22.57 | 7.87 | NULL
8739 | R-22 | -24 | 22.67 | 7.97 | NULL
8740 | R-22 | -23.8 | 22.78 | 8.08 | NULL
8741 | R-22 | -23.6 | 22.89 | 8.19 | NULL
8742 | R-22 | -23.4 | 23 | 8.3 | NULL
8743 | R-22 | -23.2 | 23.11 | 8.41 | NULL
8744 | R-22 | -23 | 23.22 | 8.52 | NULL
8745 | R-22 | -22.8 | 23.33 | 8.63 | NULL
8746 | R-22 | -22.6 | 23.44 | 8.74 | NULL
8747 | R-22 | -22.4 | 23.55 | 8.85 | NULL
8748 | R-22 | -22.2 | 23.66 | 8.96 | NULL
8749 | R-22 | -22 | 23.77 | 9.07 | NULL
8750 | R-22 | -21.8 | 23.88 | 9.18 | NULL
8751 | R-22 | -21.6 | 23.99 | 9.29 | NULL
8752 | R-22 | -21.4 | 24.11 | 9.41 | NULL
8753 | R-22 | -21.2 | 24.22 | 9.52 | NULL
8754 | R-22 | -21 | 24.33 | 9.63 | NULL
8755 | R-22 | -20.8 | 24.45 | 9.75 | NULL
8756 | R-22 | -20.6 | 24.56 | 9.86 | NULL
8757 | R-22 | -20.4 | 24.68 | 9.98 | NULL
8758 | R-22 | -20.2 | 24.79 | 10.09 | NULL
8759 | R-22 | -20 | 24.91 | 10.21 | NULL
8760 | R-22 | -19.8 | 25.02 | 10.32 | NULL
8761 | R-22 | -19.6 | 25.14 | 10.44 | NULL
8762 | R-22 | -19.4 | 25.25 | 10.55 | NULL
8763 | R-22 | -19.2 | 25.37 | 10.67 | NULL
8764 | R-22 | -19 | 25.49 | 10.79 | NULL
8765 | R-22 | -18.8 | 25.61 | 10.91 | NULL
8766 | R-22 | -18.6 | 25.73 | 11.03 | NULL
8767 | R-22 | -18.4 | 25.84 | 11.14 | NULL
8768 | R-22 | -18.2 | 25.96 | 11.26 | NULL
8769 | R-22 | -18 | 26.08 | 11.38 | NULL
8770 | R-22 | -17.8 | 26.2 | 11.5 | NULL
8771 | R-22 | -17.6 | 26.32 | 11.62 | NULL
8772 | R-22 | -17.4 | 26.44 | 11.74 | NULL
8773 | R-22 | -17.2 | 26.57 | 11.87 | NULL
8774 | R-22 | -17 | 26.69 | 11.99 | NULL
8775 | R-22 | -16.8 | 26.81 | 12.11 | NULL
8776 | R-22 | -16.6 | 26.93 | 12.23 | NULL
8777 | R-22 | -16.4 | 27.06 | 12.36 | NULL
8778 | R-22 | -16.2 | 27.18 | 12.48 | NULL
8779 | R-22 | -16 | 27.3 | 12.6 | NULL
8780 | R-22 | -15.8 | 27.43 | 12.73 | NULL
8781 | R-22 | -15.6 | 27.55 | 12.85 | NULL
8782 | R-22 | -15.4 | 27.68 | 12.98 | NULL
8783 | R-22 | -15.2 | 27.8 | 13.1 | NULL
8784 | R-22 | -15 | 27.93 | 13.23 | NULL
8785 | R-22 | -14.8 | 28.06 | 13.36 | NULL
8786 | R-22 | -14.6 | 28.18 | 13.48 | NULL
8787 | R-22 | -14.4 | 28.31 | 13.61 | NULL
8788 | R-22 | -14.2 | 28.44 | 13.74 | NULL
8789 | R-22 | -14 | 28.57 | 13.87 | NULL
8790 | R-22 | -13.8 | 28.7 | 14 | NULL
8791 | R-22 | -13.6 | 28.82 | 14.12 | NULL
8792 | R-22 | -13.4 | 28.95 | 14.25 | NULL
8793 | R-22 | -13.2 | 29.08 | 14.38 | NULL
8794 | R-22 | -13 | 29.22 | 14.52 | NULL
8795 | R-22 | -12.8 | 29.35 | 14.65 | NULL
8796 | R-22 | -12.6 | 29.48 | 14.78 | NULL
8797 | R-22 | -12.4 | 29.61 | 14.91 | NULL
8798 | R-22 | -12.2 | 29.74 | 15.04 | NULL
8799 | R-22 | -12 | 29.88 | 15.18 | NULL
8800 | R-22 | -11.8 | 30.01 | 15.31 | NULL
8801 | R-22 | -11.6 | 30.14 | 15.44 | NULL
8802 | R-22 | -11.4 | 30.28 | 15.58 | NULL
8803 | R-22 | -11.2 | 30.41 | 15.71 | NULL
8804 | R-22 | -11 | 30.55 | 15.85 | NULL
8805 | R-22 | -10.8 | 30.68 | 15.98 | NULL
8806 | R-22 | -10.6 | 30.82 | 16.12 | NULL
8807 | R-22 | -10.4 | 30.96 | 16.26 | NULL
8808 | R-22 | -10.2 | 31.09 | 16.39 | NULL
8809 | R-22 | -10 | 31.23 | 16.53 | NULL
8810 | R-22 | -9.8 | 31.37 | 16.67 | NULL
8811 | R-22 | -9.6 | 31.51 | 16.81 | NULL
8812 | R-22 | -9.4 | 31.65 | 16.95 | NULL
8813 | R-22 | -9.2 | 31.79 | 17.09 | NULL
8814 | R-22 | -9 | 31.92 | 17.22 | NULL
8815 | R-22 | -8.8 | 32.07 | 17.37 | NULL
8816 | R-22 | -8.6 | 32.21 | 17.51 | NULL
8817 | R-22 | -8.4 | 32.35 | 17.65 | NULL
8818 | R-22 | -8.2 | 32.49 | 17.79 | NULL
8819 | R-22 | -8 | 32.63 | 17.93 | NULL
8820 | R-22 | -7.8 | 32.77 | 18.07 | NULL
8821 | R-22 | -7.6 | 32.92 | 18.22 | NULL
8822 | R-22 | -7.4 | 33.06 | 18.36 | NULL
8823 | R-22 | -7.2 | 33.21 | 18.51 | NULL
8824 | R-22 | -7 | 33.35 | 18.65 | NULL
8825 | R-22 | -6.8 | 33.5 | 18.8 | NULL
8826 | R-22 | -6.6 | 33.64 | 18.94 | NULL
8827 | R-22 | -6.4 | 33.79 | 19.09 | NULL
8828 | R-22 | -6.2 | 33.93 | 19.23 | NULL
8829 | R-22 | -6 | 34.08 | 19.38 | NULL
8830 | R-22 | -5.8 | 34.23 | 19.53 | NULL
8831 | R-22 | -5.6 | 34.38 | 19.68 | NULL
8832 | R-22 | -5.4 | 34.53 | 19.83 | NULL
8833 | R-22 | -5.2 | 34.67 | 19.97 | NULL
8834 | R-22 | -5 | 34.82 | 20.12 | NULL
8835 | R-22 | -4.8 | 34.97 | 20.27 | NULL
8836 | R-22 | -4.6 | 35.12 | 20.42 | NULL
8837 | R-22 | -4.4 | 35.28 | 20.58 | NULL
8838 | R-22 | -4.2 | 35.43 | 20.73 | NULL
8839 | R-22 | -4 | 35.58 | 20.88 | NULL
8840 | R-22 | -3.8 | 35.73 | 21.03 | NULL
8841 | R-22 | -3.6 | 35.89 | 21.19 | NULL
8842 | R-22 | -3.4 | 36.04 | 21.34 | NULL
8843 | R-22 | -3.2 | 36.19 | 21.49 | NULL
8844 | R-22 | -3 | 36.35 | 21.65 | NULL
8845 | R-22 | -2.8 | 36.5 | 21.8 | NULL
8846 | R-22 | -2.6 | 36.66 | 21.96 | NULL
8847 | R-22 | -2.4 | 36.81 | 22.11 | NULL
8848 | R-22 | -2.2 | 36.97 | 22.27 | NULL
8849 | R-22 | -2 | 37.13 | 22.43 | NULL
8850 | R-22 | -1.8 | 37.29 | 22.59 | NULL
8851 | R-22 | -1.6 | 37.44 | 22.74 | NULL
8852 | R-22 | -1.4 | 37.6 | 22.9 | NULL
8853 | R-22 | -1.2 | 37.76 | 23.06 | NULL
8854 | R-22 | -1 | 37.92 | 23.22 | NULL
8855 | R-22 | -0.8 | 38.08 | 23.38 | NULL
8856 | R-22 | -0.6 | 38.24 | 23.54 | NULL
8857 | R-22 | -0.4 | 38.4 | 23.7 | NULL
8858 | R-22 | -0.2 | 38.57 | 23.87 | NULL
8859 | R-22 | 0 | 38.73 | 24.03 | NULL
8860 | R-22 | 0.2 | 38.89 | 24.19 | NULL
8861 | R-22 | 0.4 | 39.05 | 24.35 | NULL
8862 | R-22 | 0.6 | 39.22 | 24.52 | NULL
8863 | R-22 | 0.8 | 39.38 | 24.68 | NULL
8864 | R-22 | 1 | 39.55 | 24.85 | NULL
8865 | R-22 | 1.2 | 39.71 | 25.01 | NULL
8866 | R-22 | 1.4 | 39.88 | 25.18 | NULL
8867 | R-22 | 1.6 | 40.05 | 25.35 | NULL
8868 | R-22 | 1.8 | 40.21 | 25.51 | NULL
8869 | R-22 | 2 | 40.38 | 25.68 | NULL
8870 | R-22 | 2.2 | 40.55 | 25.85 | NULL
8871 | R-22 | 2.4 | 40.72 | 26.02 | NULL
8872 | R-22 | 2.6 | 40.89 | 26.19 | NULL
8873 | R-22 | 2.8 | 41.06 | 26.36 | NULL
8874 | R-22 | 3 | 41.23 | 26.53 | NULL
8875 | R-22 | 3.2 | 41.4 | 26.7 | NULL
8876 | R-22 | 3.4 | 41.57 | 26.87 | NULL
8877 | R-22 | 3.6 | 41.74 | 27.04 | NULL
8878 | R-22 | 3.8 | 41.91 | 27.21 | NULL
8879 | R-22 | 4 | 42.09 | 27.39 | NULL
8880 | R-22 | 4.2 | 42.26 | 27.56 | NULL
8881 | R-22 | 4.4 | 42.43 | 27.73 | NULL
8882 | R-22 | 4.6 | 42.61 | 27.91 | NULL
8883 | R-22 | 4.8 | 42.78 | 28.08 | NULL
8884 | R-22 | 5 | 42.96 | 28.26 | NULL
8885 | R-22 | 5.2 | 43.14 | 28.44 | NULL
8886 | R-22 | 5.4 | 43.31 | 28.61 | NULL
8887 | R-22 | 5.6 | 43.49 | 28.79 | NULL
8888 | R-22 | 5.8 | 43.67 | 28.97 | NULL
8889 | R-22 | 6 | 43.85 | 29.15 | NULL
8890 | R-22 | 6.2 | 44.03 | 29.33 | NULL
8891 | R-22 | 6.4 | 44.21 | 29.51 | NULL
8892 | R-22 | 6.6 | 44.39 | 29.69 | NULL
8893 | R-22 | 6.8 | 44.57 | 29.87 | NULL
8894 | R-22 | 7 | 44.75 | 30.05 | NULL
8895 | R-22 | 7.2 | 44.93 | 30.23 | NULL
8896 | R-22 | 7.4 | 45.11 | 30.41 | NULL
8897 | R-22 | 7.6 | 45.3 | 30.6 | NULL
8898 | R-22 | 7.8 | 45.48 | 30.78 | NULL
8899 | R-22 | 8 | 45.66 | 30.96 | NULL
8900 | R-22 | 8.2 | 45.85 | 31.15 | NULL
8901 | R-22 | 8.4 | 46.03 | 31.33 | NULL
8902 | R-22 | 8.6 | 46.22 | 31.52 | NULL
8903 | R-22 | 8.8 | 46.41 | 31.71 | NULL
8904 | R-22 | 9 | 46.59 | 31.89 | NULL
8905 | R-22 | 9.2 | 46.78 | 32.08 | NULL
8906 | R-22 | 9.4 | 46.97 | 32.27 | NULL
8907 | R-22 | 9.6 | 47.16 | 32.46 | NULL
8908 | R-22 | 9.8 | 47.35 | 32.65 | NULL
8909 | R-114 | 38.1 | NULL | -0.05 | NULL
8910 | R-114 | 38.5 | NULL | 0 | NULL
8911 | R-114 | 38.8 | NULL | 0.1 | NULL
8912 | R-114 | 39.1 | NULL | 0.2 | NULL
8913 | R-114 | 39.4 | NULL | 0.3 | NULL
8914 | R-114 | 39.8 | NULL | 0.4 | NULL
8915 | R-114 | 40.1 | NULL | 0.5 | NULL
8916 | R-114 | 40.4 | NULL | 0.6 | NULL
8917 | R-114 | 40.7 | NULL | 0.7 | NULL
8918 | R-114 | 41 | NULL | 0.8 | NULL
8919 | R-114 | 41.3 | NULL | 0.9 | NULL
8920 | R-114 | 41.6 | NULL | 1 | NULL
8921 | R-114 | 41.9 | NULL | 1.1 | NULL
8922 | R-114 | 42.2 | NULL | 1.2 | NULL
8923 | R-114 | 42.5 | NULL | 1.3 | NULL
8924 | R-114 | 42.8 | NULL | 1.4 | NULL
8925 | R-114 | 43.1 | NULL | 1.5 | NULL
8926 | R-114 | 43.4 | NULL | 1.6 | NULL
8927 | R-114 | 43.7 | NULL | 1.7 | NULL
8928 | R-114 | 44 | NULL | 1.8 | NULL
8929 | R-114 | 44.3 | NULL | 1.9 | NULL
8930 | R-114 | 44.6 | NULL | 2 | NULL
8931 | R-114 | 44.9 | NULL | 2.1 | NULL
8932 | R-114 | 45.2 | NULL | 2.2 | NULL
8933 | R-114 | 45.5 | NULL | 2.3 | NULL
8934 | R-114 | 45.7 | NULL | 2.4 | NULL
8935 | R-114 | 46 | NULL | 2.5 | NULL
8936 | R-114 | 46.3 | NULL | 2.6 | NULL
8937 | R-114 | 46.6 | NULL | 2.7 | NULL
8938 | R-114 | 46.9 | NULL | 2.8 | NULL
8939 | R-114 | 47.1 | NULL | 2.9 | NULL
8940 | R-114 | 47.4 | NULL | 3 | NULL
8941 | R-114 | 47.7 | NULL | 3.1 | NULL
8942 | R-114 | 48 | NULL | 3.2 | NULL
8943 | R-114 | 48.3 | NULL | 3.3 | NULL
8944 | R-114 | 48.5 | NULL | 3.4 | NULL
8945 | R-114 | 48.8 | NULL | 3.5 | NULL
8946 | R-114 | 49.1 | NULL | 3.6 | NULL
8947 | R-114 | 49.3 | NULL | 3.7 | NULL
8948 | R-114 | 49.6 | NULL | 3.8 | NULL
8949 | R-114 | 49.9 | NULL | 3.9 | NULL
8950 | R-114 | 50.1 | NULL | 4 | NULL
8951 | R-114 | 50.4 | NULL | 4.1 | NULL
8952 | R-114 | 50.7 | NULL | 4.2 | NULL
8953 | R-114 | 50.9 | NULL | 4.3 | NULL
8954 | R-114 | 51.2 | NULL | 4.4 | NULL
8955 | R-114 | 51.5 | NULL | 4.5 | NULL
8956 | R-114 | 51.7 | NULL | 4.6 | NULL
8957 | R-114 | 52 | NULL | 4.7 | NULL
8958 | R-114 | 52.2 | NULL | 4.8 | NULL
8959 | R-114 | 52.5 | NULL | 4.9 | NULL
8960 | R-114 | 52.8 | NULL | 5 | NULL
8961 | R-114 | 53 | NULL | 5.1 | NULL
8962 | R-114 | 53.3 | NULL | 5.2 | NULL
8963 | R-114 | 53.5 | NULL | 5.3 | NULL
8964 | R-114 | 53.8 | NULL | 5.4 | NULL
8965 | R-114 | 54 | NULL | 5.5 | NULL
8966 | R-114 | 54.3 | NULL | 5.6 | NULL
8967 | R-114 | 54.5 | NULL | 5.7 | NULL
8968 | R-114 | 54.8 | NULL | 5.8 | NULL
8969 | R-114 | 55 | NULL | 5.9 | NULL
8970 | R-114 | 55.3 | NULL | 6 | NULL
8971 | R-114 | 55.5 | NULL | 6.1 | NULL
8972 | R-114 | 55.8 | NULL | 6.2 | NULL
8973 | R-114 | 56 | NULL | 6.3 | NULL
8974 | R-114 | 56.2 | NULL | 6.4 | NULL
8975 | R-114 | 56.5 | NULL | 6.5 | NULL
8976 | R-114 | 56.7 | NULL | 6.6 | NULL
8977 | R-114 | 57 | NULL | 6.7 | NULL
8978 | R-114 | 57.2 | NULL | 6.8 | NULL
8979 | R-114 | 57.4 | NULL | 6.9 | NULL
8980 | R-114 | 57.7 | NULL | 7 | NULL
8981 | R-114 | 57.9 | NULL | 7.1 | NULL
8982 | R-114 | 58.2 | NULL | 7.2 | NULL
8983 | R-114 | 58.4 | NULL | 7.3 | NULL
8984 | R-114 | 58.6 | NULL | 7.4 | NULL
8985 | R-114 | 58.9 | NULL | 7.5 | NULL
8986 | R-114 | 59.1 | NULL | 7.6 | NULL
8987 | R-114 | 59.3 | NULL | 7.7 | NULL
8988 | R-114 | 59.6 | NULL | 7.8 | NULL
8989 | R-114 | 59.8 | NULL | 7.9 | NULL
8990 | R-114 | 60 | NULL | 8 | NULL
8991 | R-114 | 60.2 | NULL | 8.1 | NULL
8992 | R-114 | 60.5 | NULL | 8.2 | NULL
8993 | R-114 | 60.7 | NULL | 8.3 | NULL
8994 | R-114 | 60.9 | NULL | 8.4 | NULL
8995 | R-114 | 61.1 | NULL | 8.5 | NULL
8996 | R-114 | 61.4 | NULL | 8.6 | NULL
8997 | R-114 | 61.6 | NULL | 8.7 | NULL
8998 | R-114 | 61.8 | NULL | 8.8 | NULL
8999 | R-114 | 62 | NULL | 8.9 | NULL
9000 | R-114 | 62.3 | NULL | 9 | NULL
9001 | R-114 | 62.5 | NULL | 9.1 | NULL
9002 | R-114 | 62.7 | NULL | 9.2 | NULL
9003 | R-114 | 62.9 | NULL | 9.3 | NULL
9004 | R-114 | 63.1 | NULL | 9.4 | NULL
9005 | R-114 | 63.4 | NULL | 9.5 | NULL
9006 | R-114 | 63.6 | NULL | 9.6 | NULL
9007 | R-114 | 63.8 | NULL | 9.7 | NULL
9008 | R-114 | 64 | NULL | 9.8 | NULL
9009 | R-114 | 64.2 | NULL | 9.9 | NULL
9010 | R-114 | 64.4 | NULL | 10 | NULL
9011 | R-114 | 64.7 | NULL | 10.1 | NULL
9012 | R-114 | 64.9 | NULL | 10.2 | NULL
9013 | R-114 | 65.1 | NULL | 10.3 | NULL
9014 | R-114 | 65.3 | NULL | 10.4 | NULL
9015 | R-114 | 65.5 | NULL | 10.5 | NULL
9016 | R-114 | 65.7 | NULL | 10.6 | NULL
9017 | R-114 | 65.9 | NULL | 10.7 | NULL
9018 | R-114 | 66.1 | NULL | 10.8 | NULL
9019 | R-114 | 66.4 | NULL | 10.9 | NULL
9020 | R-114 | 66.6 | NULL | 11 | NULL
9021 | R-114 | 66.8 | NULL | 11.1 | NULL
9022 | R-114 | 67 | NULL | 11.2 | NULL
9023 | R-114 | 67.2 | NULL | 11.3 | NULL
9024 | R-114 | 67.4 | NULL | 11.4 | NULL
9025 | R-114 | 67.6 | NULL | 11.5 | NULL
9026 | R-114 | 67.8 | NULL | 11.6 | NULL
9027 | R-114 | 68 | NULL | 11.7 | NULL
9028 | R-114 | 68.2 | NULL | 11.8 | NULL
9029 | R-114 | 68.4 | NULL | 11.9 | NULL
9030 | R-114 | 68.6 | NULL | 12 | NULL
9031 | R-114 | 68.8 | NULL | 12.1 | NULL
9032 | R-114 | 69 | NULL | 12.2 | NULL
9033 | R-114 | 69.2 | NULL | 12.3 | NULL
9034 | R-114 | 69.4 | NULL | 12.4 | NULL
9035 | R-114 | 69.6 | NULL | 12.5 | NULL
9036 | R-114 | 69.8 | NULL | 12.6 | NULL
9037 | R-114 | 70 | NULL | 12.7 | NULL
9038 | R-114 | 70.2 | NULL | 12.8 | NULL
9039 | R-114 | 70.4 | NULL | 12.9 | NULL
9040 | R-114 | 70.6 | NULL | 13 | NULL
9041 | R-114 | 70.8 | NULL | 13.1 | NULL
9042 | R-114 | 71 | NULL | 13.2 | NULL
9043 | R-114 | 71.2 | NULL | 13.3 | NULL
9044 | R-114 | 71.4 | NULL | 13.4 | NULL
9045 | R-114 | 71.6 | NULL | 13.5 | NULL
9046 | R-114 | 71.8 | NULL | 13.6 | NULL
9047 | R-114 | 72 | NULL | 13.7 | NULL
9048 | R-114 | 72.2 | NULL | 13.8 | NULL
9049 | R-114 | 72.4 | NULL | 13.9 | NULL
9050 | R-114 | 72.6 | NULL | 14 | NULL
9051 | R-114 | 72.7 | NULL | 14.1 | NULL
9052 | R-114 | 72.9 | NULL | 14.2 | NULL
9053 | R-114 | 73.1 | NULL | 14.3 | NULL
9054 | R-114 | 73.3 | NULL | 14.4 | NULL
9055 | R-114 | 73.5 | NULL | 14.5 | NULL
9056 | R-114 | 73.7 | NULL | 14.6 | NULL
9057 | R-114 | 73.9 | NULL | 14.7 | NULL
9058 | R-114 | 74.1 | NULL | 14.8 | NULL
9059 | R-114 | 74.3 | NULL | 14.9 | NULL
9060 | R-114 | 74.4 | NULL | 15 | NULL
9061 | R-114 | 74.6 | NULL | 15.1 | NULL
9062 | R-114 | 74.8 | NULL | 15.2 | NULL
9063 | R-114 | 75 | NULL | 15.3 | NULL
9064 | R-114 | 75.2 | NULL | 15.4 | NULL
9065 | R-114 | 75.4 | NULL | 15.5 | NULL
9066 | R-114 | 75.6 | NULL | 15.6 | NULL
9067 | R-114 | 75.7 | NULL | 15.7 | NULL
9068 | R-114 | 75.9 | NULL | 15.8 | NULL
9069 | R-114 | 76.1 | NULL | 15.9 | NULL
9070 | R-114 | 76.3 | NULL | 16 | NULL
9071 | R-114 | 76.5 | NULL | 16.1 | NULL
9072 | R-114 | 76.6 | NULL | 16.2 | NULL
9073 | R-114 | 76.8 | NULL | 16.3 | NULL
9074 | R-114 | 77 | NULL | 16.4 | NULL
9075 | R-114 | 77.2 | NULL | 16.5 | NULL
9076 | R-114 | 77.4 | NULL | 16.6 | NULL
9077 | R-114 | 77.5 | NULL | 16.7 | NULL
9078 | R-114 | 77.7 | NULL | 16.8 | NULL
9079 | R-114 | 77.9 | NULL | 16.9 | NULL
9080 | R-114 | 78.1 | NULL | 17 | NULL
9081 | R-114 | 78.3 | NULL | 17.1 | NULL
9082 | R-114 | 78.4 | NULL | 17.2 | NULL
9083 | R-114 | 78.6 | NULL | 17.3 | NULL
9084 | R-114 | 78.8 | NULL | 17.4 | NULL
9085 | R-114 | 79 | NULL | 17.5 | NULL
9086 | R-114 | 79.1 | NULL | 17.6 | NULL
9087 | R-114 | 79.3 | NULL | 17.7 | NULL
9088 | R-114 | 79.5 | NULL | 17.8 | NULL
9089 | R-114 | 79.7 | NULL | 17.9 | NULL
9090 | R-114 | 79.8 | NULL | 18 | NULL
9091 | R-114 | 80 | NULL | 18.1 | NULL
9092 | R-114 | 80.2 | NULL | 18.2 | NULL
9093 | R-114 | 80.4 | NULL | 18.3 | NULL
9094 | R-114 | 80.5 | NULL | 18.4 | NULL
9095 | R-114 | 80.7 | NULL | 18.5 | NULL
9096 | R-114 | 80.9 | NULL | 18.6 | NULL
9097 | R-114 | 81 | NULL | 18.7 | NULL
9098 | R-114 | 81.2 | NULL | 18.8 | NULL
9099 | R-114 | 81.4 | NULL | 18.9 | NULL
9100 | R-114 | 81.5 | NULL | 19 | NULL
9101 | R-114 | 81.7 | NULL | 19.1 | NULL
9102 | R-114 | 81.9 | NULL | 19.2 | NULL
9103 | R-114 | 82.1 | NULL | 19.3 | NULL
9104 | R-114 | 82.2 | NULL | 19.4 | NULL
9105 | R-114 | 82.4 | NULL | 19.5 | NULL
9106 | R-114 | 82.6 | NULL | 19.6 | NULL
9107 | R-114 | 82.7 | NULL | 19.7 | NULL
9108 | R-114 | 82.9 | NULL | 19.8 | NULL
9109 | R-114 | 83.1 | NULL | 19.9 | NULL
9110 | R-114 | 83.2 | NULL | 20 | NULL
9111 | R-114 | 83.4 | NULL | 20.1 | NULL
9112 | R-114 | 83.6 | NULL | 20.2 | NULL
9113 | R-114 | 83.7 | NULL | 20.3 | NULL
9114 | R-114 | 83.9 | NULL | 20.4 | NULL
9115 | R-114 | 84 | NULL | 20.5 | NULL
9116 | R-114 | 84.2 | NULL | 20.6 | NULL
9117 | R-114 | 84.4 | NULL | 20.7 | NULL
9118 | R-114 | 84.5 | NULL | 20.8 | NULL
9119 | R-114 | 84.7 | NULL | 20.9 | NULL
9120 | R-114 | 84.9 | NULL | 21 | NULL
9121 | R-114 | 85 | NULL | 21.1 | NULL
9122 | R-114 | 85.2 | NULL | 21.2 | NULL
9123 | R-114 | 85.3 | NULL | 21.3 | NULL
9124 | R-114 | 85.5 | NULL | 21.4 | NULL
9125 | R-114 | 85.7 | NULL | 21.5 | NULL
9126 | R-114 | 85.8 | NULL | 21.6 | NULL
9127 | R-114 | 86 | NULL | 21.7 | NULL
9128 | R-114 | 86.1 | NULL | 21.8 | NULL
9129 | R-114 | 86.3 | NULL | 21.9 | NULL
9130 | R-114 | 86.5 | NULL | 22 | NULL
9131 | R-114 | 86.6 | NULL | 22.1 | NULL
9132 | R-114 | 86.8 | NULL | 22.2 | NULL
9133 | R-114 | 86.9 | NULL | 22.3 | NULL
9134 | R-114 | 87.1 | NULL | 22.4 | NULL
9135 | R-114 | 87.3 | NULL | 22.5 | NULL
9136 | R-114 | 87.4 | NULL | 22.6 | NULL
9137 | R-114 | 87.6 | NULL | 22.7 | NULL
9138 | R-114 | 87.7 | NULL | 22.8 | NULL
9139 | R-114 | 87.9 | NULL | 22.9 | NULL
9140 | R-114 | 88 | NULL | 23 | NULL
9141 | R-114 | 88.2 | NULL | 23.1 | NULL
9142 | R-114 | 88.3 | NULL | 23.2 | NULL
9143 | R-114 | 88.5 | NULL | 23.3 | NULL
9144 | R-114 | 88.7 | NULL | 23.4 | NULL
9145 | R-114 | 88.8 | NULL | 23.5 | NULL
9146 | R-114 | 89 | NULL | 23.6 | NULL
9147 | R-114 | 89.1 | NULL | 23.7 | NULL
9148 | R-114 | 89.3 | NULL | 23.8 | NULL
9149 | R-114 | 89.4 | NULL | 23.9 | NULL
9150 | R-114 | 89.6 | NULL | 24 | NULL
9151 | R-114 | 89.7 | NULL | 24.1 | NULL
9152 | R-114 | 89.9 | NULL | 24.2 | NULL
9153 | R-114 | 90 | NULL | 24.3 | NULL
9154 | R-114 | 90.2 | NULL | 24.4 | NULL
9155 | R-114 | 90.3 | NULL | 24.5 | NULL
9156 | R-114 | 90.5 | NULL | 24.6 | NULL
9157 | R-114 | 90.6 | NULL | 24.7 | NULL
9158 | R-114 | 90.8 | NULL | 24.8 | NULL
9159 | R-114 | 90.9 | NULL | 24.9 | NULL
9160 | R-114 | 91.1 | NULL | 25 | NULL
9161 | R-114 | 91.2 | NULL | 25.1 | NULL
9162 | R-114 | 91.4 | NULL | 25.2 | NULL
9163 | R-114 | 91.5 | NULL | 25.3 | NULL
9164 | R-114 | 91.7 | NULL | 25.4 | NULL
9165 | R-114 | 91.8 | NULL | 25.5 | NULL
9166 | R-114 | 92 | NULL | 25.6 | NULL
9167 | R-114 | 92.1 | NULL | 25.7 | NULL
9168 | R-114 | 92.3 | NULL | 25.8 | NULL
9169 | R-114 | 92.4 | NULL | 25.9 | NULL
9170 | R-114 | 92.6 | NULL | 26 | NULL
9171 | R-114 | 92.7 | NULL | 26.1 | NULL
9172 | R-114 | 92.9 | NULL | 26.2 | NULL
9173 | R-114 | 93 | NULL | 26.3 | NULL
9174 | R-114 | 93.2 | NULL | 26.4 | NULL
9175 | R-114 | 93.3 | NULL | 26.5 | NULL
9176 | R-114 | 93.4 | NULL | 26.6 | NULL
9177 | R-114 | 93.6 | NULL | 26.7 | NULL
9178 | R-114 | 93.7 | NULL | 26.8 | NULL
9179 | R-114 | 93.9 | NULL | 26.9 | NULL
9180 | R-114 | 94 | NULL | 27 | NULL
9181 | R-114 | 94.2 | NULL | 27.1 | NULL
9182 | R-114 | 94.3 | NULL | 27.2 | NULL
9183 | R-114 | 94.5 | NULL | 27.3 | NULL
9184 | R-114 | 94.6 | NULL | 27.4 | NULL
9185 | R-114 | 94.7 | NULL | 27.5 | NULL
9186 | R-114 | 94.9 | NULL | 27.6 | NULL
9187 | R-114 | 95 | NULL | 27.7 | NULL
9188 | R-114 | 95.2 | NULL | 27.8 | NULL
9189 | R-114 | 95.3 | NULL | 27.9 | NULL
9190 | R-114 | 95.4 | NULL | 28 | NULL
9191 | R-114 | 95.6 | NULL | 28.1 | NULL
9192 | R-114 | 95.7 | NULL | 28.2 | NULL
9193 | R-114 | 95.9 | NULL | 28.3 | NULL
9194 | R-114 | 96 | NULL | 28.4 | NULL
9195 | R-114 | 96.2 | NULL | 28.5 | NULL
9196 | R-114 | 96.3 | NULL | 28.6 | NULL
9197 | R-114 | 96.4 | NULL | 28.7 | NULL
9198 | R-114 | 96.6 | NULL | 28.8 | NULL
9199 | R-114 | 96.7 | NULL | 28.9 | NULL
9200 | R-114 | 96.9 | NULL | 29 | NULL
9201 | R-114 | 97 | NULL | 29.1 | NULL
9202 | R-114 | 97.1 | NULL | 29.2 | NULL
9203 | R-114 | 97.3 | NULL | 29.3 | NULL
9204 | R-114 | 97.4 | NULL | 29.4 | NULL
9205 | R-114 | 97.5 | NULL | 29.5 | NULL
9206 | R-114 | 97.7 | NULL | 29.6 | NULL
9207 | R-114 | 97.8 | NULL | 29.7 | NULL
9208 | R-114 | 98 | NULL | 29.8 | NULL
9209 | R-114 | 98.1 | NULL | 29.9 | NULL
9210 | R-114 | 98.2 | NULL | 30 | NULL
9211 | R-114 | 98.4 | NULL | 30.1 | NULL
9212 | R-114 | 98.5 | NULL | 30.2 | NULL
9213 | R-114 | 98.6 | NULL | 30.3 | NULL
9214 | R-114 | 98.8 | NULL | 30.4 | NULL
9215 | R-114 | 98.9 | NULL | 30.5 | NULL
9216 | R-114 | 99 | NULL | 30.6 | NULL
9217 | R-114 | 99.2 | NULL | 30.7 | NULL
9218 | R-114 | 99.3 | NULL | 30.8 | NULL
9219 | R-114 | 99.5 | NULL | 30.9 | NULL
9220 | R-114 | 99.6 | NULL | 31 | NULL
9221 | R-114 | 99.7 | NULL | 31.1 | NULL
9222 | R-114 | 99.9 | NULL | 31.2 | NULL
9223 | R-114 | 100 | NULL | 31.3 | NULL
9224 | R-114 | 100.1 | NULL | 31.4 | NULL
9225 | R-114 | 100.3 | NULL | 31.5 | NULL
9226 | R-114 | 100.4 | NULL | 31.6 | NULL
9227 | R-114 | 100.5 | NULL | 31.7 | NULL
9228 | R-114 | 100.6 | NULL | 31.8 | NULL
9229 | R-114 | 100.8 | NULL | 31.9 | NULL
9230 | R-114 | 100.9 | NULL | 32 | NULL
9231 | R-114 | 101 | NULL | 32.1 | NULL
9232 | R-114 | 101.2 | NULL | 32.2 | NULL
9233 | R-114 | 101.3 | NULL | 32.3 | NULL
9234 | R-114 | 101.4 | NULL | 32.4 | NULL
9235 | R-114 | 101.6 | NULL | 32.5 | NULL
9236 | R-114 | 101.7 | NULL | 32.6 | NULL
9237 | R-114 | 101.8 | NULL | 32.7 | NULL
9238 | R-114 | 102 | NULL | 32.8 | NULL
9239 | R-114 | 102.1 | NULL | 32.9 | NULL
9240 | R-114 | 102.2 | NULL | 33 | NULL
9241 | R-114 | 102.4 | NULL | 33.1 | NULL
9242 | R-114 | 102.5 | NULL | 33.2 | NULL
9243 | R-114 | 102.6 | NULL | 33.3 | NULL
9244 | R-114 | 102.7 | NULL | 33.4 | NULL
9245 | R-114 | 102.9 | NULL | 33.5 | NULL
9246 | R-114 | 103 | NULL | 33.6 | NULL
9247 | R-114 | 103.1 | NULL | 33.7 | NULL
9248 | R-114 | 103.3 | NULL | 33.8 | NULL
9249 | R-114 | 103.4 | NULL | 33.9 | NULL
9250 | R-114 | 103.5 | NULL | 34 | NULL
9251 | R-114 | 103.6 | NULL | 34.1 | NULL
9252 | R-114 | 103.8 | NULL | 34.2 | NULL
9253 | R-114 | 103.9 | NULL | 34.3 | NULL
9254 | R-114 | 104 | NULL | 34.4 | NULL
9255 | R-114 | 104.2 | NULL | 34.5 | NULL
9256 | R-114 | 104.3 | NULL | 34.6 | NULL
9257 | R-114 | 104.4 | NULL | 34.7 | NULL
9258 | R-114 | 104.5 | NULL | 34.8 | NULL
9259 | R-114 | 104.7 | NULL | 34.9 | NULL
9260 | R-114 | 104.8 | NULL | 35 | NULL
9261 | R-114 | 104.9 | NULL | 35.1 | NULL
9262 | R-114 | 105 | NULL | 35.2 | NULL
9263 | R-114 | 105.2 | NULL | 35.3 | NULL
9264 | R-114 | 105.3 | NULL | 35.4 | NULL
9265 | R-114 | 105.4 | NULL | 35.5 | NULL
9266 | R-114 | 105.5 | NULL | 35.6 | NULL
9267 | R-114 | 105.7 | NULL | 35.7 | NULL
9268 | R-114 | 105.8 | NULL | 35.8 | NULL
9269 | R-114 | 105.9 | NULL | 35.9 | NULL
9270 | R-114 | 106 | NULL | 36 | NULL
9271 | R-114 | 106.2 | NULL | 36.1 | NULL
9272 | R-114 | 106.3 | NULL | 36.2 | NULL
9273 | R-114 | 106.4 | NULL | 36.3 | NULL
9274 | R-114 | 106.5 | NULL | 36.4 | NULL
9275 | R-114 | 106.7 | NULL | 36.5 | NULL
9276 | R-114 | 106.8 | NULL | 36.6 | NULL
9277 | R-114 | 106.9 | NULL | 36.7 | NULL
9278 | R-114 | 107 | NULL | 36.8 | NULL
9279 | R-114 | 107.2 | NULL | 36.9 | NULL
9280 | R-114 | 107.3 | NULL | 37 | NULL
9281 | R-114 | 107.4 | NULL | 37.1 | NULL
9282 | R-114 | 107.5 | NULL | 37.2 | NULL
9283 | R-114 | 107.6 | NULL | 37.3 | NULL
9284 | R-114 | 107.8 | NULL | 37.4 | NULL
9285 | R-114 | 107.9 | NULL | 37.5 | NULL
9286 | R-114 | 108 | NULL | 37.6 | NULL
9287 | R-114 | 108.1 | NULL | 37.7 | NULL
9288 | R-114 | 108.2 | NULL | 37.8 | NULL
9289 | R-114 | 108.4 | NULL | 37.9 | NULL
9290 | R-114 | 108.5 | NULL | 38 | NULL
9291 | R-114 | 108.6 | NULL | 38.1 | NULL
9292 | R-114 | 108.7 | NULL | 38.2 | NULL
9293 | R-114 | 108.9 | NULL | 38.3 | NULL
9294 | R-114 | 109 | NULL | 38.4 | NULL
9295 | R-114 | 109.1 | NULL | 38.5 | NULL
9296 | R-114 | 109.2 | NULL | 38.6 | NULL
9297 | R-114 | 109.3 | NULL | 38.7 | NULL
9298 | R-114 | 109.5 | NULL | 38.8 | NULL
9299 | R-114 | 109.6 | NULL | 38.9 | NULL
9300 | R-114 | 109.7 | NULL | 39 | NULL
9301 | R-114 | 109.8 | NULL | 39.1 | NULL
9302 | R-114 | 109.9 | NULL | 39.2 | NULL
9303 | R-114 | 110 | NULL | 39.3 | NULL
9304 | R-114 | 110.2 | NULL | 39.4 | NULL
9305 | R-114 | 110.3 | NULL | 39.5 | NULL
9306 | R-114 | 110.4 | NULL | 39.6 | NULL
9307 | R-114 | 110.5 | NULL | 39.7 | NULL
9308 | R-114 | 110.6 | NULL | 39.8 | NULL
9309 | R-114 | 110.8 | NULL | 39.9 | NULL
9310 | R-114 | 110.9 | NULL | 40 | NULL
9311 | R-114 | 111 | NULL | 40.1 | NULL
9312 | R-114 | 111.1 | NULL | 40.2 | NULL
9313 | R-114 | 111.2 | NULL | 40.3 | NULL
9314 | R-114 | 111.3 | NULL | 40.4 | NULL
9315 | R-114 | 111.5 | NULL | 40.5 | NULL
9316 | R-114 | 111.6 | NULL | 40.6 | NULL
9317 | R-114 | 111.7 | NULL | 40.7 | NULL
9318 | R-114 | 111.8 | NULL | 40.8 | NULL
9319 | R-114 | 111.9 | NULL | 40.9 | NULL
9320 | R-114 | 112 | NULL | 41 | NULL
9321 | R-114 | 112.2 | NULL | 41.1 | NULL
9322 | R-114 | 112.3 | NULL | 41.2 | NULL
9323 | R-114 | 112.4 | NULL | 41.3 | NULL
9324 | R-114 | 112.5 | NULL | 41.4 | NULL
9325 | R-114 | 112.6 | NULL | 41.5 | NULL
9326 | R-114 | 112.7 | NULL | 41.6 | NULL
9327 | R-114 | 112.8 | NULL | 41.7 | NULL
9328 | R-114 | 113 | NULL | 41.8 | NULL
9329 | R-114 | 113.1 | NULL | 41.9 | NULL
9330 | R-114 | 113.2 | NULL | 42 | NULL
9331 | R-114 | 113.3 | NULL | 42.1 | NULL
9332 | R-114 | 113.4 | NULL | 42.2 | NULL
9333 | R-114 | 113.5 | NULL | 42.3 | NULL
9334 | R-114 | 113.6 | NULL | 42.4 | NULL
9335 | R-114 | 113.8 | NULL | 42.5 | NULL
9336 | R-114 | 113.9 | NULL | 42.6 | NULL
9337 | R-114 | 114 | NULL | 42.7 | NULL
9338 | R-114 | 114.1 | NULL | 42.8 | NULL
9339 | R-114 | 114.2 | NULL | 42.9 | NULL
9340 | R-114 | 114.3 | NULL | 43 | NULL
9341 | R-114 | 114.4 | NULL | 43.1 | NULL
9342 | R-114 | 114.5 | NULL | 43.2 | NULL
9343 | R-114 | 114.7 | NULL | 43.3 | NULL
9344 | R-114 | 114.8 | NULL | 43.4 | NULL
9345 | R-114 | 114.9 | NULL | 43.5 | NULL
9346 | R-114 | 115 | NULL | 43.6 | NULL
9347 | R-114 | 115.1 | NULL | 43.7 | NULL
9348 | R-114 | 115.2 | NULL | 43.8 | NULL
9349 | R-114 | 115.3 | NULL | 43.9 | NULL
9350 | R-114 | 115.4 | NULL | 44 | NULL
9351 | R-114 | 115.6 | NULL | 44.1 | NULL
9352 | R-114 | 115.7 | NULL | 44.2 | NULL
9353 | R-114 | 115.8 | NULL | 44.3 | NULL
9354 | R-114 | 115.9 | NULL | 44.4 | NULL
9355 | R-114 | 116 | NULL | 44.5 | NULL
9356 | R-114 | 116.1 | NULL | 44.6 | NULL
9357 | R-114 | 116.2 | NULL | 44.7 | NULL
9358 | R-114 | 116.3 | NULL | 44.8 | NULL
9359 | R-114 | 116.4 | NULL | 44.9 | NULL
9360 | R-114 | 116.5 | NULL | 45 | NULL
9361 | R-114 | 116.7 | NULL | 45.1 | NULL
9362 | R-114 | 116.8 | NULL | 45.2 | NULL
9363 | R-114 | 116.9 | NULL | 45.3 | NULL
9364 | R-114 | 117 | NULL | 45.4 | NULL
9365 | R-114 | 117.1 | NULL | 45.5 | NULL
9366 | R-114 | 117.2 | NULL | 45.6 | NULL
9367 | R-114 | 117.3 | NULL | 45.7 | NULL
9368 | R-114 | 117.4 | NULL | 45.8 | NULL
9369 | R-114 | 117.5 | NULL | 45.9 | NULL
9370 | R-114 | 117.6 | NULL | 46 | NULL
9371 | R-114 | 117.8 | NULL | 46.1 | NULL
9372 | R-114 | 117.9 | NULL | 46.2 | NULL
9373 | R-114 | 118 | NULL | 46.3 | NULL
9374 | R-114 | 118.1 | NULL | 46.4 | NULL
9375 | R-114 | 118.2 | NULL | 46.5 | NULL
9376 | R-114 | 118.3 | NULL | 46.6 | NULL
9377 | R-114 | 118.4 | NULL | 46.7 | NULL
9378 | R-114 | 118.5 | NULL | 46.8 | NULL
9379 | R-114 | 118.6 | NULL | 46.9 | NULL
9380 | R-114 | 118.7 | NULL | 47 | NULL
9381 | R-114 | 118.8 | NULL | 47.1 | NULL
9382 | R-114 | 118.9 | NULL | 47.2 | NULL
9383 | R-114 | 119 | NULL | 47.3 | NULL
9384 | R-114 | 119.1 | NULL | 47.4 | NULL
9385 | R-114 | 119.3 | NULL | 47.5 | NULL
9386 | R-114 | 119.4 | NULL | 47.6 | NULL
9387 | R-114 | 119.5 | NULL | 47.7 | NULL
9388 | R-114 | 119.6 | NULL | 47.8 | NULL
9389 | R-114 | 119.7 | NULL | 47.9 | NULL
9390 | R-114 | 119.8 | NULL | 48 | NULL
9391 | R-114 | 119.9 | NULL | 48.1 | NULL
9392 | R-114 | 120 | NULL | 48.2 | NULL
9393 | R-114 | 120.1 | NULL | 48.3 | NULL
9394 | R-114 | 120.2 | NULL | 48.4 | NULL
9395 | R-114 | 120.3 | NULL | 48.5 | NULL
9396 | R-114 | 120.4 | NULL | 48.6 | NULL
9397 | R-114 | 120.5 | NULL | 48.7 | NULL
9398 | R-114 | 120.6 | NULL | 48.8 | NULL
9399 | R-114 | 120.7 | NULL | 48.9 | NULL
9400 | R-114 | 120.8 | NULL | 49 | NULL
9401 | R-114 | 120.9 | NULL | 49.1 | NULL
9402 | R-114 | 121 | NULL | 49.2 | NULL
9403 | R-114 | 121.2 | NULL | 49.3 | NULL
9404 | R-114 | 121.3 | NULL | 49.4 | NULL
9405 | R-114 | 121.4 | NULL | 49.5 | NULL
9406 | R-114 | 121.5 | NULL | 49.6 | NULL
9407 | R-114 | 121.6 | NULL | 49.7 | NULL
9408 | R-114 | 121.7 | NULL | 49.8 | NULL
9409 | R-114 | 121.8 | NULL | 49.9 | NULL
9410 | R-114 | 121.9 | NULL | 50 | NULL
9411 | R-114 | 122 | NULL | 50.1 | NULL
9412 | R-114 | 122.1 | NULL | 50.2 | NULL
9413 | R-114 | 122.2 | NULL | 50.3 | NULL
9414 | R-114 | 122.3 | NULL | 50.4 | NULL
9415 | R-114 | 122.4 | NULL | 50.5 | NULL
9416 | R-114 | 122.5 | NULL | 50.6 | NULL
9417 | R-114 | 122.6 | NULL | 50.7 | NULL
9418 | R-114 | 122.7 | NULL | 50.8 | NULL
9419 | R-114 | 122.8 | NULL | 50.9 | NULL
9420 | R-114 | 122.9 | NULL | 51 | NULL
9421 | R-114 | 123 | NULL | 51.1 | NULL
9422 | R-114 | 123.1 | NULL | 51.2 | NULL
9423 | R-114 | 123.2 | NULL | 51.3 | NULL
9424 | R-114 | 123.3 | NULL | 51.4 | NULL
9425 | R-114 | 123.4 | NULL | 51.5 | NULL
9426 | R-114 | 123.5 | NULL | 51.6 | NULL
9427 | R-114 | 123.6 | NULL | 51.7 | NULL
9428 | R-114 | 123.7 | NULL | 51.8 | NULL
9429 | R-114 | 123.8 | NULL | 51.9 | NULL
9430 | R-114 | 123.9 | NULL | 52 | NULL
9431 | R-114 | 124 | NULL | 52.1 | NULL
9432 | R-114 | 124.1 | NULL | 52.2 | NULL
9433 | R-114 | 124.2 | NULL | 52.3 | NULL
9434 | R-114 | 124.3 | NULL | 52.4 | NULL
9435 | R-114 | 124.4 | NULL | 52.5 | NULL
9436 | R-114 | 124.5 | NULL | 52.6 | NULL
9437 | R-114 | 124.6 | NULL | 52.7 | NULL
9438 | R-114 | 124.7 | NULL | 52.8 | NULL
9439 | R-114 | 124.8 | NULL | 52.9 | NULL
9440 | R-114 | 124.9 | NULL | 53 | NULL
9441 | R-114 | 125 | NULL | 53.1 | NULL
9442 | R-114 | 125.1 | NULL | 53.2 | NULL
9443 | R-114 | 125.2 | NULL | 53.3 | NULL
9444 | R-114 | 125.3 | NULL | 53.4 | NULL
9445 | R-114 | 125.4 | NULL | 53.5 | NULL
9446 | R-114 | 125.5 | NULL | 53.6 | NULL
9447 | R-114 | 125.6 | NULL | 53.7 | NULL
9448 | R-114 | 125.7 | NULL | 53.8 | NULL
9449 | R-114 | 125.8 | NULL | 53.9 | NULL
9450 | R-114 | 125.9 | NULL | 54 | NULL
9451 | R-114 | 126 | NULL | 54.1 | NULL
9452 | R-114 | 126.1 | NULL | 54.2 | NULL
9453 | R-114 | 126.2 | NULL | 54.3 | NULL
9454 | R-114 | 126.3 | NULL | 54.4 | NULL
9455 | R-114 | 126.4 | NULL | 54.5 | NULL
9456 | R-114 | 126.5 | NULL | 54.6 | NULL
9457 | R-114 | 126.6 | NULL | 54.7 | NULL
9458 | R-114 | 126.7 | NULL | 54.8 | NULL
9459 | R-114 | 126.8 | NULL | 54.9 | NULL
9460 | R-114 | 126.9 | NULL | 55 | NULL
9461 | R-114 | 127 | NULL | 55.1 | NULL
9462 | R-114 | 127.1 | NULL | 55.2 | NULL
9463 | R-114 | 127.2 | NULL | 55.3 | NULL
9464 | R-114 | 127.3 | NULL | 55.4 | NULL
9465 | R-114 | 127.4 | NULL | 55.5 | NULL
9466 | R-114 | 127.5 | NULL | 55.6 | NULL
9467 | R-114 | 127.6 | NULL | 55.7 | NULL
9468 | R-114 | 127.7 | NULL | 55.8 | NULL
9469 | R-114 | 127.8 | NULL | 55.9 | NULL
9470 | R-114 | 127.9 | NULL | 56 | NULL
9471 | R-114 | 128 | NULL | 56.1 | NULL
9472 | R-114 | 128.1 | NULL | 56.2 | NULL
9473 | R-114 | 128.2 | NULL | 56.3 | NULL
9474 | R-114 | 128.3 | NULL | 56.4 | NULL
9475 | R-114 | 128.4 | NULL | 56.5 | NULL
9476 | R-114 | 128.5 | NULL | 56.6 | NULL
9477 | R-114 | 128.6 | NULL | 56.7 | NULL
9478 | R-114 | 128.7 | NULL | 56.8 | NULL
9479 | R-114 | 128.8 | NULL | 56.9 | NULL
9480 | R-114 | 128.8 | NULL | 57 | NULL
9481 | R-114 | 128.9 | NULL | 57.1 | NULL
9482 | R-114 | 129 | NULL | 57.2 | NULL
9483 | R-114 | 129.1 | NULL | 57.3 | NULL
9484 | R-114 | 129.2 | NULL | 57.4 | NULL
9485 | R-114 | 129.3 | NULL | 57.5 | NULL
9486 | R-114 | 129.4 | NULL | 57.6 | NULL
9487 | R-114 | 129.5 | NULL | 57.7 | NULL
9488 | R-114 | 129.6 | NULL | 57.8 | NULL
9489 | R-114 | 129.7 | NULL | 57.9 | NULL
9490 | R-114 | 129.8 | NULL | 58 | NULL
9491 | R-114 | 129.9 | NULL | 58.1 | NULL
9492 | R-114 | 130 | NULL | 58.2 | NULL
9493 | R-114 | 130.1 | NULL | 58.3 | NULL
9494 | R-114 | 130.2 | NULL | 58.4 | NULL
9495 | R-114 | 130.3 | NULL | 58.5 | NULL
9496 | R-114 | 130.4 | NULL | 58.6 | NULL
9497 | R-114 | 130.5 | NULL | 58.7 | NULL
9498 | R-114 | 130.6 | NULL | 58.8 | NULL
9499 | R-114 | 130.6 | NULL | 58.9 | NULL
9500 | R-114 | 130.7 | NULL | 59 | NULL
9501 | R-114 | 130.8 | NULL | 59.1 | NULL
9502 | R-114 | 130.9 | NULL | 59.2 | NULL
9503 | R-114 | 131 | NULL | 59.3 | NULL
9504 | R-114 | 131.1 | NULL | 59.4 | NULL
9505 | R-114 | 131.2 | NULL | 59.5 | NULL
9506 | R-114 | 131.3 | NULL | 59.6 | NULL
9507 | R-114 | 131.4 | NULL | 59.7 | NULL
9508 | R-114 | 131.5 | NULL | 59.8 | NULL
9509 | R-114 | 131.6 | NULL | 59.9 | NULL
9510 | R-114 | 131.7 | NULL | 60 | NULL
9511 | R-114 | 131.8 | NULL | 60.1 | NULL
9512 | R-114 | 131.9 | NULL | 60.2 | NULL
9513 | R-114 | 132 | NULL | 60.3 | NULL
9518 | R-114 | 25 | NULL | -3.83 | -7.8
9519 | R-114 | 25.2 | NULL | -3.78 | -7.7
9520 | R-114 | 25.4 | NULL | -3.73 | -7.6
9521 | R-114 | 25.6 | NULL | -3.68 | -7.5
9522 | R-114 | 25.8 | NULL | -3.63 | -7.4
9523 | R-114 | 26 | NULL | -3.58 | -7.3
9524 | R-114 | 26.2 | NULL | -3.54 | -7.2
9525 | R-114 | 26.3 | NULL | -3.49 | -7.1
9526 | R-114 | 26.5 | NULL | -3.44 | -7
9527 | R-114 | 26.7 | NULL | -3.39 | -6.9
9528 | R-114 | 26.9 | NULL | -3.34 | -6.8
9529 | R-114 | 27.1 | NULL | -3.29 | -6.7
9530 | R-114 | 27.3 | NULL | -3.24 | -6.6
9531 | R-114 | 27.5 | NULL | -3.19 | -6.5
9532 | R-114 | 27.7 | NULL | -3.14 | -6.4
9533 | R-114 | 27.9 | NULL | -3.09 | -6.3
9534 | R-114 | 28.1 | NULL | -3.04 | -6.2
9535 | R-114 | 28.3 | NULL | -3 | -6.1
9536 | R-114 | 28.5 | NULL | -2.95 | -6
9537 | R-114 | 28.7 | NULL | -2.9 | -5.9
9538 | R-114 | 28.8 | NULL | -2.85 | -5.8
9539 | R-114 | 29 | NULL | -2.8 | -5.7
9540 | R-114 | 29.2 | NULL | -2.75 | -5.6
9541 | R-114 | 29.4 | NULL | -2.7 | -5.5
9542 | R-114 | 29.6 | NULL | -2.65 | -5.4
9543 | R-114 | 29.8 | NULL | -2.6 | -5.3
9544 | R-114 | 30 | NULL | -2.55 | -5.2
9545 | R-114 | 30.2 | NULL | -2.5 | -5.1
9546 | R-114 | 30.3 | NULL | -2.46 | -5
9547 | R-114 | 30.5 | NULL | -2.41 | -4.9
9548 | R-114 | 30.7 | NULL | -2.36 | -4.8
9549 | R-114 | 30.9 | NULL | -2.31 | -4.7
9550 | R-114 | 31 | NULL | -2.26 | -4.6
9551 | R-114 | 31.2 | NULL | -2.21 | -4.5
9552 | R-114 | 31.4 | NULL | -2.16 | -4.4
9553 | R-114 | 31.6 | NULL | -2.11 | -4.3
9554 | R-114 | 31.7 | NULL | -2.06 | -4.2
9555 | R-114 | 31.9 | NULL | -2.01 | -4.1
9556 | R-114 | 32.1 | NULL | -1.96 | -4
9557 | R-114 | 32.2 | NULL | -1.91 | -3.9
9558 | R-114 | 32.4 | NULL | -1.87 | -3.8
9559 | R-114 | 32.6 | NULL | -1.82 | -3.7
9560 | R-114 | 32.8 | NULL | -1.77 | -3.6
9561 | R-114 | 32.9 | NULL | -1.72 | -3.5
9562 | R-114 | 33.1 | NULL | -1.67 | -3.4
9563 | R-114 | 33.3 | NULL | -1.62 | -3.3
9564 | R-114 | 33.4 | NULL | -1.57 | -3.2
9565 | R-114 | 33.6 | NULL | -1.52 | -3.1
9566 | R-114 | 33.8 | NULL | -1.47 | -3
9567 | R-114 | 34 | NULL | -1.42 | -2.9
9568 | R-114 | 34.1 | NULL | -1.37 | -2.8
9569 | R-114 | 34.3 | NULL | -1.33 | -2.7
9570 | R-114 | 34.5 | NULL | -1.28 | -2.6
9571 | R-114 | 34.7 | NULL | -1.23 | -2.5
9572 | R-114 | 34.8 | NULL | -1.18 | -2.4
9573 | R-114 | 35 | NULL | -1.13 | -2.3
9574 | R-114 | 35.1 | NULL | -1.08 | -2.2
9575 | R-114 | 35.3 | NULL | -1.03 | -2.1
9576 | R-114 | 35.4 | NULL | -0.98 | -2
9577 | R-114 | 35.6 | NULL | -0.93 | -1.9
9578 | R-114 | 35.7 | NULL | -0.88 | -1.8
9579 | R-114 | 35.8 | NULL | -0.83 | -1.7
9580 | R-114 | 36 | NULL | -0.79 | -1.6
9581 | R-114 | 36.1 | NULL | -0.74 | -1.5
9582 | R-114 | 36.3 | NULL | -0.69 | -1.4
9583 | R-114 | 36.4 | NULL | -0.64 | -1.3
9584 | R-114 | 36.5 | NULL | -0.59 | -1.2
9585 | R-114 | 36.7 | NULL | -0.54 | -1.1
9586 | R-114 | 36.8 | NULL | -0.49 | -1
9587 | R-114 | 37 | NULL | -0.44 | -0.9
9588 | R-114 | 37.1 | NULL | -0.39 | -0.8
9589 | R-114 | 37.3 | NULL | -0.34 | -0.7
9590 | R-114 | 37.4 | NULL | -0.29 | -0.6
9591 | R-114 | 37.5 | NULL | -0.25 | -0.5
9592 | R-114 | 37.7 | NULL | -0.2 | -0.4
9593 | R-114 | 37.8 | NULL | -0.15 | -0.3
9594 | R-114 | 38 | NULL | -0.1 | -0.2
9595 | R-514A | -40 | 0.47 | -14.23 | -6.9891
9596 | R-514A | -39.9 | 0.47 | -14.23 | -6.9891
9597 | R-514A | -39.8 | 0.47 | -14.23 | -6.9891
9598 | R-514A | -39.7 | 0.48 | -14.22 | -6.9842
9599 | R-514A | -39.6 | 0.48 | -14.22 | -6.9842
9600 | R-514A | -39.5 | 0.48 | -14.22 | -6.9842
9601 | R-514A | -39.4 | 0.48 | -14.22 | -6.9842
9602 | R-514A | -39.3 | 0.48 | -14.22 | -6.9842
9603 | R-514A | -39.2 | 0.49 | -14.21 | -6.9793
9604 | R-514A | -39.1 | 0.49 | -14.21 | -6.9793
9605 | R-514A | -39 | 0.49 | -14.21 | -6.9793
9606 | R-514A | -38.9 | 0.49 | -14.21 | -6.9793
9607 | R-514A | -38.8 | 0.49 | -14.21 | -6.9793
9608 | R-514A | -38.7 | 0.5 | -14.2 | -6.9744
9609 | R-514A | -38.6 | 0.5 | -14.2 | -6.9744
9610 | R-514A | -38.5 | 0.5 | -14.2 | -6.9744
9611 | R-514A | -38.4 | 0.5 | -14.2 | -6.9744
9612 | R-514A | -38.3 | 0.5 | -14.2 | -6.9744
9613 | R-514A | -38.2 | 0.5 | -14.2 | -6.9744
9614 | R-514A | -38.1 | 0.51 | -14.19 | -6.9695
9615 | R-514A | -38 | 0.51 | -14.19 | -6.9695
9616 | R-514A | -37.9 | 0.51 | -14.19 | -6.9695
9617 | R-514A | -37.8 | 0.51 | -14.19 | -6.9695
9618 | R-514A | -37.7 | 0.51 | -14.19 | -6.9695
9619 | R-514A | -37.6 | 0.52 | -14.18 | -6.9646
9620 | R-514A | -37.5 | 0.52 | -14.18 | -6.9646
9621 | R-514A | -37.4 | 0.52 | -14.18 | -6.9646
9622 | R-514A | -37.3 | 0.52 | -14.18 | -6.9646
9623 | R-514A | -37.2 | 0.52 | -14.18 | -6.9646
9624 | R-514A | -37.1 | 0.53 | -14.17 | -6.9597
9625 | R-514A | -37 | 0.53 | -14.17 | -6.9597
9626 | R-514A | -36.9 | 0.53 | -14.17 | -6.9597
9627 | R-514A | -36.8 | 0.53 | -14.17 | -6.9597
9628 | R-514A | -36.7 | 0.53 | -14.17 | -6.9597
9629 | R-514A | -36.6 | 0.54 | -14.16 | -6.9547
9630 | R-514A | -36.5 | 0.54 | -14.16 | -6.9547
9631 | R-514A | -36.4 | 0.54 | -14.16 | -6.9547
9632 | R-514A | -36.3 | 0.54 | -14.16 | -6.9547
9633 | R-514A | -36.2 | 0.54 | -14.16 | -6.9547
9634 | R-514A | -36.1 | 0.55 | -14.15 | -6.9498
9635 | R-514A | -36 | 0.55 | -14.15 | -6.9498
9636 | R-514A | -35.9 | 0.55 | -14.15 | -6.9498
9637 | R-514A | -35.8 | 0.55 | -14.15 | -6.9498
9638 | R-514A | -35.7 | 0.55 | -14.15 | -6.9498
9639 | R-514A | -35.6 | 0.56 | -14.14 | -6.9449
9640 | R-514A | -35.5 | 0.56 | -14.14 | -6.9449
9641 | R-514A | -35.4 | 0.56 | -14.14 | -6.9449
9642 | R-514A | -35.3 | 0.56 | -14.14 | -6.9449
9643 | R-514A | -35.2 | 0.56 | -14.14 | -6.9449
9644 | R-514A | -35.1 | 0.57 | -14.13 | -6.94
9645 | R-514A | -35 | 0.57 | -14.13 | -6.94
9646 | R-514A | -34.9 | 0.57 | -14.13 | -6.94
9647 | R-514A | -34.8 | 0.57 | -14.13 | -6.94
9648 | R-514A | -34.7 | 0.57 | -14.13 | -6.94
9649 | R-514A | -34.6 | 0.58 | -14.12 | -6.9351
9650 | R-514A | -34.5 | 0.58 | -14.12 | -6.9351
9651 | R-514A | -34.4 | 0.58 | -14.12 | -6.9351
9652 | R-514A | -34.3 | 0.58 | -14.12 | -6.9351
9653 | R-514A | -34.2 | 0.58 | -14.12 | -6.9351
9654 | R-514A | -34.1 | 0.59 | -14.11 | -6.9302
9655 | R-514A | -34 | 0.59 | -14.11 | -6.9302
9656 | R-514A | -33.9 | 0.59 | -14.11 | -6.9302
9657 | R-514A | -33.8 | 0.59 | -14.11 | -6.9302
9658 | R-514A | -33.7 | 0.6 | -14.1 | -6.9253
9659 | R-514A | -33.6 | 0.6 | -14.1 | -6.9253
9660 | R-514A | -33.5 | 0.6 | -14.1 | -6.9253
9661 | R-514A | -33.4 | 0.6 | -14.1 | -6.9253
9662 | R-514A | -33.3 | 0.6 | -14.1 | -6.9253
9663 | R-514A | -33.2 | 0.61 | -14.09 | -6.9204
9664 | R-514A | -33.1 | 0.61 | -14.09 | -6.9204
9665 | R-514A | -33 | 0.61 | -14.09 | -6.9204
9666 | R-514A | -32.9 | 0.61 | -14.09 | -6.9204
9667 | R-514A | -32.8 | 0.62 | -14.08 | -6.9154
9668 | R-514A | -32.7 | 0.62 | -14.08 | -6.9154
9669 | R-514A | -32.6 | 0.62 | -14.08 | -6.9154
9670 | R-514A | -32.5 | 0.62 | -14.08 | -6.9154
9671 | R-514A | -32.4 | 0.62 | -14.08 | -6.9154
9672 | R-514A | -32.3 | 0.63 | -14.07 | -6.9105
9673 | R-514A | -32.2 | 0.63 | -14.07 | -6.9105
9674 | R-514A | -32.1 | 0.63 | -14.07 | -6.9105
9675 | R-514A | -32 | 0.63 | -14.07 | -6.9105
9676 | R-514A | -31.9 | 0.64 | -14.06 | -6.9056
9677 | R-514A | -31.8 | 0.64 | -14.06 | -6.9056
9678 | R-514A | -31.7 | 0.64 | -14.06 | -6.9056
9679 | R-514A | -31.6 | 0.64 | -14.06 | -6.9056
9680 | R-514A | -31.5 | 0.64 | -14.06 | -6.9056
9681 | R-514A | -31.4 | 0.65 | -14.05 | -6.9007
9682 | R-514A | -31.3 | 0.65 | -14.05 | -6.9007
9683 | R-514A | -31.2 | 0.65 | -14.05 | -6.9007
9684 | R-514A | -31.1 | 0.65 | -14.05 | -6.9007
9685 | R-514A | -31 | 0.66 | -14.04 | -6.8958
9686 | R-514A | -30.9 | 0.66 | -14.04 | -6.8958
9687 | R-514A | -30.8 | 0.66 | -14.04 | -6.8958
9688 | R-514A | -30.7 | 0.66 | -14.04 | -6.8958
9689 | R-514A | -30.6 | 0.67 | -14.03 | -6.8909
9690 | R-514A | -30.5 | 0.67 | -14.03 | -6.8909
9691 | R-514A | -30.4 | 0.67 | -14.03 | -6.8909
9692 | R-514A | -30.3 | 0.67 | -14.03 | -6.8909
9693 | R-514A | -30.2 | 0.68 | -14.02 | -6.886
9694 | R-514A | -30.1 | 0.68 | -14.02 | -6.886
9695 | R-514A | -30 | 0.68 | -14.02 | -6.886
9696 | R-514A | -29.9 | 0.68 | -14.02 | -6.886
9697 | R-514A | -29.8 | 0.69 | -14.01 | -6.8811
9698 | R-514A | -29.7 | 0.69 | -14.01 | -6.8811
9699 | R-514A | -29.6 | 0.69 | -14.01 | -6.8811
9700 | R-514A | -29.5 | 0.69 | -14.01 | -6.8811
9701 | R-514A | -29.4 | 0.7 | -14 | -6.8762
9702 | R-514A | -29.3 | 0.7 | -14 | -6.8762
9703 | R-514A | -29.2 | 0.7 | -14 | -6.8762
9704 | R-514A | -29.1 | 0.7 | -14 | -6.8762
9705 | R-514A | -29 | 0.71 | -13.99 | -6.8712
9706 | R-514A | -28.9 | 0.71 | -13.99 | -6.8712
9707 | R-514A | -28.8 | 0.71 | -13.99 | -6.8712
9708 | R-514A | -28.7 | 0.71 | -13.99 | -6.8712
9709 | R-514A | -28.6 | 0.72 | -13.98 | -6.8663
9710 | R-514A | -28.5 | 0.72 | -13.98 | -6.8663
9711 | R-514A | -28.4 | 0.72 | -13.98 | -6.8663
9712 | R-514A | -28.3 | 0.72 | -13.98 | -6.8663
9713 | R-514A | -28.2 | 0.73 | -13.97 | -6.8614
9714 | R-514A | -28.1 | 0.73 | -13.97 | -6.8614
9715 | R-514A | -28 | 0.73 | -13.97 | -6.8614
9716 | R-514A | -27.9 | 0.73 | -13.97 | -6.8614
9717 | R-514A | -27.8 | 0.74 | -13.96 | -6.8565
9718 | R-514A | -27.7 | 0.74 | -13.96 | -6.8565
9719 | R-514A | -27.6 | 0.74 | -13.96 | -6.8565
9720 | R-514A | -27.5 | 0.74 | -13.96 | -6.8565
9721 | R-514A | -27.4 | 0.75 | -13.95 | -6.8516
9722 | R-514A | -27.3 | 0.75 | -13.95 | -6.8516
9723 | R-514A | -27.2 | 0.75 | -13.95 | -6.8516
9724 | R-514A | -27.1 | 0.75 | -13.95 | -6.8516
9725 | R-514A | -27 | 0.76 | -13.94 | -6.8467
9726 | R-514A | -26.9 | 0.76 | -13.94 | -6.8467
9727 | R-514A | -26.8 | 0.76 | -13.94 | -6.8467
9728 | R-514A | -26.7 | 0.76 | -13.94 | -6.8467
9729 | R-514A | -26.6 | 0.77 | -13.93 | -6.8418
9730 | R-514A | -26.5 | 0.77 | -13.93 | -6.8418
9731 | R-514A | -26.4 | 0.77 | -13.93 | -6.8418
9732 | R-514A | -26.3 | 0.78 | -13.92 | -6.8369
9733 | R-514A | -26.2 | 0.78 | -13.92 | -6.8369
9734 | R-514A | -26.1 | 0.78 | -13.92 | -6.8369
9735 | R-514A | -26 | 0.78 | -13.92 | -6.8369
9736 | R-514A | -25.9 | 0.79 | -13.91 | -6.832
9737 | R-514A | -25.8 | 0.79 | -13.91 | -6.832
9738 | R-514A | -25.7 | 0.79 | -13.91 | -6.832
9739 | R-514A | -25.6 | 0.79 | -13.91 | -6.832
9740 | R-514A | -25.5 | 0.8 | -13.9 | -6.827
9741 | R-514A | -25.4 | 0.8 | -13.9 | -6.827
9742 | R-514A | -25.3 | 0.8 | -13.9 | -6.827
9743 | R-514A | -25.2 | 0.81 | -13.89 | -6.8221
9744 | R-514A | -25.1 | 0.81 | -13.89 | -6.8221
9745 | R-514A | -25 | 0.81 | -13.89 | -6.8221
9746 | R-514A | -24.9 | 0.81 | -13.89 | -6.8221
9747 | R-514A | -24.8 | 0.82 | -13.88 | -6.8172
9748 | R-514A | -24.7 | 0.82 | -13.88 | -6.8172
9749 | R-514A | -24.6 | 0.82 | -13.88 | -6.8172
9750 | R-514A | -24.5 | 0.83 | -13.87 | -6.8123
9751 | R-514A | -24.4 | 0.83 | -13.87 | -6.8123
9752 | R-514A | -24.3 | 0.83 | -13.87 | -6.8123
9753 | R-514A | -24.2 | 0.83 | -13.87 | -6.8123
9754 | R-514A | -24.1 | 0.84 | -13.86 | -6.8074
9755 | R-514A | -24 | 0.84 | -13.86 | -6.8074
9756 | R-514A | -23.9 | 0.84 | -13.86 | -6.8074
9757 | R-514A | -23.8 | 0.85 | -13.85 | -6.8025
9758 | R-514A | -23.7 | 0.85 | -13.85 | -6.8025
9759 | R-514A | -23.6 | 0.85 | -13.85 | -6.8025
9760 | R-514A | -23.5 | 0.85 | -13.85 | -6.8025
9761 | R-514A | -23.4 | 0.86 | -13.84 | -6.7976
9762 | R-514A | -23.3 | 0.86 | -13.84 | -6.7976
9763 | R-514A | -23.2 | 0.86 | -13.84 | -6.7976
9764 | R-514A | -23.1 | 0.87 | -13.83 | -6.7927
9765 | R-514A | -23 | 0.87 | -13.83 | -6.7927
9766 | R-514A | -22.9 | 0.87 | -13.83 | -6.7927
9767 | R-514A | -22.8 | 0.88 | -13.82 | -6.7877
9768 | R-514A | -22.7 | 0.88 | -13.82 | -6.7877
9769 | R-514A | -22.6 | 0.88 | -13.82 | -6.7877
9770 | R-514A | -22.5 | 0.88 | -13.82 | -6.7877
9771 | R-514A | -22.4 | 0.89 | -13.81 | -6.7828
9772 | R-514A | -22.3 | 0.89 | -13.81 | -6.7828
9773 | R-514A | -22.2 | 0.89 | -13.81 | -6.7828
9774 | R-514A | -22.1 | 0.9 | -13.8 | -6.7779
9775 | R-514A | -22 | 0.9 | -13.8 | -6.7779
9776 | R-514A | -21.9 | 0.9 | -13.8 | -6.7779
9777 | R-514A | -21.8 | 0.91 | -13.79 | -6.773
9778 | R-514A | -21.7 | 0.91 | -13.79 | -6.773
9779 | R-514A | -21.6 | 0.91 | -13.79 | -6.773
9780 | R-514A | -21.5 | 0.92 | -13.78 | -6.7681
9781 | R-514A | -21.4 | 0.92 | -13.78 | -6.7681
9782 | R-514A | -21.3 | 0.92 | -13.78 | -6.7681
9783 | R-514A | -21.2 | 0.92 | -13.78 | -6.7681
9784 | R-514A | -21.1 | 0.93 | -13.77 | -6.7632
9785 | R-514A | -21 | 0.93 | -13.77 | -6.7632
9786 | R-514A | -20.9 | 0.93 | -13.77 | -6.7632
9787 | R-514A | -20.8 | 0.94 | -13.76 | -6.7583
9788 | R-514A | -20.7 | 0.94 | -13.76 | -6.7583
9789 | R-514A | -20.6 | 0.94 | -13.76 | -6.7583
9790 | R-514A | -20.5 | 0.95 | -13.75 | -6.7534
9791 | R-514A | -20.4 | 0.95 | -13.75 | -6.7534
9792 | R-514A | -20.3 | 0.95 | -13.75 | -6.7534
9793 | R-514A | -20.2 | 0.96 | -13.74 | -6.7485
9794 | R-514A | -20.1 | 0.96 | -13.74 | -6.7485
9795 | R-514A | -20 | 0.96 | -13.74 | -6.7485
9796 | R-514A | -19.9 | 0.97 | -13.73 | -6.7435
9797 | R-514A | -19.8 | 0.97 | -13.73 | -6.7435
9798 | R-514A | -19.7 | 0.97 | -13.73 | -6.7435
9799 | R-514A | -19.6 | 0.98 | -13.72 | -6.7386
9800 | R-514A | -19.5 | 0.98 | -13.72 | -6.7386
9801 | R-514A | -19.4 | 0.98 | -13.72 | -6.7386
9802 | R-514A | -19.3 | 0.99 | -13.71 | -6.7337
9803 | R-514A | -19.2 | 0.99 | -13.71 | -6.7337
9804 | R-514A | -19.1 | 0.99 | -13.71 | -6.7337
9805 | R-514A | -19 | 1 | -13.7 | -6.7288
9806 | R-514A | -18.9 | 1 | -13.7 | -6.7288
9807 | R-514A | -18.8 | 1 | -13.7 | -6.7288
9808 | R-514A | -18.7 | 1.01 | -13.69 | -6.7239
9809 | R-514A | -18.6 | 1.01 | -13.69 | -6.7239
9810 | R-514A | -18.5 | 1.01 | -13.69 | -6.7239
9811 | R-514A | -18.4 | 1.02 | -13.68 | -6.719
9812 | R-514A | -18.3 | 1.02 | -13.68 | -6.719
9813 | R-514A | -18.2 | 1.02 | -13.68 | -6.719
9814 | R-514A | -18.1 | 1.03 | -13.67 | -6.7141
9815 | R-514A | -18 | 1.03 | -13.67 | -6.7141
9816 | R-514A | -17.9 | 1.03 | -13.67 | -6.7141
9817 | R-514A | -17.8 | 1.04 | -13.66 | -6.7092
9818 | R-514A | -17.7 | 1.04 | -13.66 | -6.7092
9819 | R-514A | -17.6 | 1.04 | -13.66 | -6.7092
9820 | R-514A | -17.5 | 1.05 | -13.65 | -6.7043
9821 | R-514A | -17.4 | 1.05 | -13.65 | -6.7043
9822 | R-514A | -17.3 | 1.05 | -13.65 | -6.7043
9823 | R-514A | -17.2 | 1.06 | -13.64 | -6.6993
9824 | R-514A | -17.1 | 1.06 | -13.64 | -6.6993
9825 | R-514A | -17 | 1.06 | -13.64 | -6.6993
9826 | R-514A | -16.9 | 1.07 | -13.63 | -6.6944
9827 | R-514A | -16.8 | 1.07 | -13.63 | -6.6944
9828 | R-514A | -16.7 | 1.08 | -13.62 | -6.6895
9829 | R-514A | -16.6 | 1.08 | -13.62 | -6.6895
9830 | R-514A | -16.5 | 1.08 | -13.62 | -6.6895
9831 | R-514A | -16.4 | 1.09 | -13.61 | -6.6846
9832 | R-514A | -16.3 | 1.09 | -13.61 | -6.6846
9833 | R-514A | -16.2 | 1.09 | -13.61 | -6.6846
9834 | R-514A | -16.1 | 1.1 | -13.6 | -6.6797
9835 | R-514A | -16 | 1.1 | -13.6 | -6.6797
9836 | R-514A | -15.9 | 1.1 | -13.6 | -6.6797
9837 | R-514A | -15.8 | 1.11 | -13.59 | -6.6748
9838 | R-514A | -15.7 | 1.11 | -13.59 | -6.6748
9839 | R-514A | -15.6 | 1.12 | -13.58 | -6.6699
9840 | R-514A | -15.5 | 1.12 | -13.58 | -6.6699
9841 | R-514A | -15.4 | 1.12 | -13.58 | -6.6699
9842 | R-514A | -15.3 | 1.13 | -13.57 | -6.665
9843 | R-514A | -15.2 | 1.13 | -13.57 | -6.665
9844 | R-514A | -15.1 | 1.13 | -13.57 | -6.665
9845 | R-514A | -15 | 1.14 | -13.56 | -6.6601
9846 | R-514A | -14.9 | 1.14 | -13.56 | -6.6601
9847 | R-514A | -14.8 | 1.15 | -13.55 | -6.6551
9848 | R-514A | -14.7 | 1.15 | -13.55 | -6.6551
9849 | R-514A | -14.6 | 1.15 | -13.55 | -6.6551
9850 | R-514A | -14.5 | 1.16 | -13.54 | -6.6502
9851 | R-514A | -14.4 | 1.16 | -13.54 | -6.6502
9852 | R-514A | -14.3 | 1.16 | -13.54 | -6.6502
9853 | R-514A | -14.2 | 1.17 | -13.53 | -6.6453
9854 | R-514A | -14.1 | 1.17 | -13.53 | -6.6453
9855 | R-514A | -14 | 1.18 | -13.52 | -6.6404
9856 | R-514A | -13.9 | 1.18 | -13.52 | -6.6404
9857 | R-514A | -13.8 | 1.18 | -13.52 | -6.6404
9858 | R-514A | -13.7 | 1.19 | -13.51 | -6.6355
9859 | R-514A | -13.6 | 1.19 | -13.51 | -6.6355
9860 | R-514A | -13.5 | 1.19 | -13.51 | -6.6355
9861 | R-514A | -13.4 | 1.2 | -13.5 | -6.6306
9862 | R-514A | -13.3 | 1.2 | -13.5 | -6.6306
9863 | R-514A | -13.2 | 1.21 | -13.49 | -6.6257
9864 | R-514A | -13.1 | 1.21 | -13.49 | -6.6257
9865 | R-514A | -13 | 1.21 | -13.49 | -6.6257
9866 | R-514A | -12.9 | 1.22 | -13.48 | -6.6208
9867 | R-514A | -12.8 | 1.22 | -13.48 | -6.6208
9868 | R-514A | -12.7 | 1.23 | -13.47 | -6.6159
9869 | R-514A | -12.6 | 1.23 | -13.47 | -6.6159
9870 | R-514A | -12.5 | 1.23 | -13.47 | -6.6159
9871 | R-514A | -12.4 | 1.24 | -13.46 | -6.6109
9872 | R-514A | -12.3 | 1.24 | -13.46 | -6.6109
9873 | R-514A | -12.2 | 1.25 | -13.45 | -6.606
9874 | R-514A | -12.1 | 1.25 | -13.45 | -6.606
9875 | R-514A | -12 | 1.25 | -13.45 | -6.606
9876 | R-514A | -11.9 | 1.26 | -13.44 | -6.6011
9877 | R-514A | -11.8 | 1.26 | -13.44 | -6.6011
9878 | R-514A | -11.7 | 1.27 | -13.43 | -6.5962
9879 | R-514A | -11.6 | 1.27 | -13.43 | -6.5962
9880 | R-514A | -11.5 | 1.27 | -13.43 | -6.5962
9881 | R-514A | -11.4 | 1.28 | -13.42 | -6.5913
9882 | R-514A | -11.3 | 1.28 | -13.42 | -6.5913
9883 | R-514A | -11.2 | 1.29 | -13.41 | -6.5864
9884 | R-514A | -11.1 | 1.29 | -13.41 | -6.5864
9885 | R-514A | -11 | 1.3 | -13.4 | -6.5815
9886 | R-514A | -10.9 | 1.3 | -13.4 | -6.5815
9887 | R-514A | -10.8 | 1.3 | -13.4 | -6.5815
9888 | R-514A | -10.7 | 1.31 | -13.39 | -6.5766
9889 | R-514A | -10.6 | 1.31 | -13.39 | -6.5766
9890 | R-514A | -10.5 | 1.32 | -13.38 | -6.5716
9891 | R-514A | -10.4 | 1.32 | -13.38 | -6.5716
9892 | R-514A | -10.3 | 1.33 | -13.37 | -6.5667
9893 | R-514A | -10.2 | 1.33 | -13.37 | -6.5667
9894 | R-514A | -10.1 | 1.33 | -13.37 | -6.5667
9895 | R-514A | -10 | 1.34 | -13.36 | -6.5618
9896 | R-514A | -9.9 | 1.34 | -13.36 | -6.5618
9897 | R-514A | -9.8 | 1.35 | -13.35 | -6.5569
9898 | R-514A | -9.7 | 1.35 | -13.35 | -6.5569
9899 | R-514A | -9.6 | 1.36 | -13.34 | -6.552
9900 | R-514A | -9.5 | 1.36 | -13.34 | -6.552
9901 | R-514A | -9.4 | 1.36 | -13.34 | -6.552
9902 | R-514A | -9.3 | 1.37 | -13.33 | -6.5471
9903 | R-514A | -9.2 | 1.37 | -13.33 | -6.5471
9904 | R-514A | -9.1 | 1.38 | -13.32 | -6.5422
9905 | R-514A | -9 | 1.38 | -13.32 | -6.5422
9906 | R-514A | -8.9 | 1.39 | -13.31 | -6.5373
9907 | R-514A | -8.8 | 1.39 | -13.31 | -6.5373
9908 | R-514A | -8.7 | 1.39 | -13.31 | -6.5373
9909 | R-514A | -8.6 | 1.4 | -13.3 | -6.5324
9910 | R-514A | -8.5 | 1.4 | -13.3 | -6.5324
9911 | R-514A | -8.4 | 1.41 | -13.29 | -6.5274
9912 | R-514A | -8.3 | 1.41 | -13.29 | -6.5274
9913 | R-514A | -8.2 | 1.42 | -13.28 | -6.5225
9914 | R-514A | -8.1 | 1.42 | -13.28 | -6.5225
9915 | R-514A | -8 | 1.43 | -13.27 | -6.5176
9916 | R-514A | -7.9 | 1.43 | -13.27 | -6.5176
9917 | R-514A | -7.8 | 1.43 | -13.27 | -6.5176
9918 | R-514A | -7.7 | 1.44 | -13.26 | -6.5127
9919 | R-514A | -7.6 | 1.44 | -13.26 | -6.5127
9920 | R-514A | -7.5 | 1.45 | -13.25 | -6.5078
9921 | R-514A | -7.4 | 1.45 | -13.25 | -6.5078
9922 | R-514A | -7.3 | 1.46 | -13.24 | -6.5029
9923 | R-514A | -7.2 | 1.46 | -13.24 | -6.5029
9924 | R-514A | -7.1 | 1.47 | -13.23 | -6.498
9925 | R-514A | -7 | 1.47 | -13.23 | -6.498
9926 | R-514A | -6.9 | 1.48 | -13.22 | -6.4931
9927 | R-514A | -6.8 | 1.48 | -13.22 | -6.4931
9928 | R-514A | -6.7 | 1.49 | -13.21 | -6.4882
9929 | R-514A | -6.6 | 1.49 | -13.21 | -6.4882
9930 | R-514A | -6.5 | 1.49 | -13.21 | -6.4882
9931 | R-514A | -6.4 | 1.5 | -13.2 | -6.4832
9932 | R-514A | -6.3 | 1.5 | -13.2 | -6.4832
9933 | R-514A | -6.2 | 1.51 | -13.19 | -6.4783
9934 | R-514A | -6.1 | 1.51 | -13.19 | -6.4783
9935 | R-514A | -6 | 1.52 | -13.18 | -6.4734
9936 | R-514A | -5.9 | 1.52 | -13.18 | -6.4734
9937 | R-514A | -5.8 | 1.53 | -13.17 | -6.4685
9938 | R-514A | -5.7 | 1.53 | -13.17 | -6.4685
9939 | R-514A | -5.6 | 1.54 | -13.16 | -6.4636
9940 | R-514A | -5.5 | 1.54 | -13.16 | -6.4636
9941 | R-514A | -5.4 | 1.55 | -13.15 | -6.4587
9942 | R-514A | -5.3 | 1.55 | -13.15 | -6.4587
9943 | R-514A | -5.2 | 1.56 | -13.14 | -6.4538
9944 | R-514A | -5.1 | 1.56 | -13.14 | -6.4538
9945 | R-514A | -5 | 1.57 | -13.13 | -6.4489
9946 | R-514A | -4.9 | 1.57 | -13.13 | -6.4489
9947 | R-514A | -4.8 | 1.58 | -13.12 | -6.4439
9948 | R-514A | -4.7 | 1.58 | -13.12 | -6.4439
9949 | R-514A | -4.6 | 1.59 | -13.11 | -6.439
9950 | R-514A | -4.5 | 1.59 | -13.11 | -6.439
9951 | R-514A | -4.4 | 1.6 | -13.1 | -6.4341
9952 | R-514A | -4.3 | 1.6 | -13.1 | -6.4341
9953 | R-514A | -4.2 | 1.61 | -13.09 | -6.4292
9954 | R-514A | -4.1 | 1.61 | -13.09 | -6.4292
9955 | R-514A | -4 | 1.62 | -13.08 | -6.4243
9956 | R-514A | -3.9 | 1.62 | -13.08 | -6.4243
9957 | R-514A | -3.8 | 1.63 | -13.07 | -6.4194
9958 | R-514A | -3.7 | 1.63 | -13.07 | -6.4194
9959 | R-514A | -3.6 | 1.64 | -13.06 | -6.4145
9960 | R-514A | -3.5 | 1.64 | -13.06 | -6.4145
9961 | R-514A | -3.4 | 1.65 | -13.05 | -6.4096
9962 | R-514A | -3.3 | 1.65 | -13.05 | -6.4096
9963 | R-514A | -3.2 | 1.66 | -13.04 | -6.4047
9964 | R-514A | -3.1 | 1.66 | -13.04 | -6.4047
9965 | R-514A | -3 | 1.67 | -13.03 | -6.3997
9966 | R-514A | -2.9 | 1.67 | -13.03 | -6.3997
9967 | R-514A | -2.8 | 1.68 | -13.02 | -6.3948
9968 | R-514A | -2.7 | 1.68 | -13.02 | -6.3948
9969 | R-514A | -2.6 | 1.69 | -13.01 | -6.3899
9970 | R-514A | -2.5 | 1.69 | -13.01 | -6.3899
9971 | R-514A | -2.4 | 1.7 | -13 | -6.385
9972 | R-514A | -2.3 | 1.7 | -13 | -6.385
9973 | R-514A | -2.2 | 1.71 | -12.99 | -6.3801
9974 | R-514A | -2.1 | 1.71 | -12.99 | -6.3801
9975 | R-514A | -2 | 1.72 | -12.98 | -6.3752
9976 | R-514A | -1.9 | 1.72 | -12.98 | -6.3752
9977 | R-514A | -1.8 | 1.73 | -12.97 | -6.3703
9978 | R-514A | -1.7 | 1.73 | -12.97 | -6.3703
9979 | R-514A | -1.6 | 1.74 | -12.96 | -6.3654
9980 | R-514A | -1.5 | 1.75 | -12.95 | -6.3605
9981 | R-514A | -1.4 | 1.75 | -12.95 | -6.3605
9982 | R-514A | -1.3 | 1.76 | -12.94 | -6.3555
9983 | R-514A | -1.2 | 1.76 | -12.94 | -6.3555
9984 | R-514A | -1.1 | 1.77 | -12.93 | -6.3506
9985 | R-514A | -1 | 1.77 | -12.93 | -6.3506
9986 | R-514A | -0.9 | 1.78 | -12.92 | -6.3457
9987 | R-514A | -0.8 | 1.78 | -12.92 | -6.3457
9988 | R-514A | -0.7 | 1.79 | -12.91 | -6.3408
9989 | R-514A | -0.6 | 1.79 | -12.91 | -6.3408
9990 | R-514A | -0.5 | 1.8 | -12.9 | -6.3359
9991 | R-514A | -0.4 | 1.81 | -12.89 | -6.331
9992 | R-514A | -0.3 | 1.81 | -12.89 | -6.331
9993 | R-514A | -0.2 | 1.82 | -12.88 | -6.3261
9994 | R-514A | -0.1 | 1.82 | -12.88 | -6.3261
9995 | R-514A | 0 | 1.83 | -12.87 | -6.3212
9996 | R-514A | 0.1 | 1.83 | -12.87 | -6.3212
9997 | R-514A | 0.2 | 1.84 | -12.86 | -6.3162
9998 | R-514A | 0.3 | 1.84 | -12.86 | -6.3162
9999 | R-514A | 0.4 | 1.85 | -12.85 | -6.3113
10000 | R-514A | 0.5 | 1.86 | -12.84 | -6.3064
10001 | R-514A | 0.6 | 1.86 | -12.84 | -6.3064
10002 | R-514A | 0.7 | 1.87 | -12.83 | -6.3015
10003 | R-514A | 0.8 | 1.87 | -12.83 | -6.3015
10004 | R-514A | 0.9 | 1.88 | -12.82 | -6.2966
10005 | R-514A | 1 | 1.88 | -12.82 | -6.2966
10006 | R-514A | 1.1 | 1.89 | -12.81 | -6.2917
10007 | R-514A | 1.2 | 1.89 | -12.81 | -6.2917
10008 | R-514A | 1.3 | 1.9 | -12.8 | -6.2868
10009 | R-514A | 1.4 | 1.91 | -12.79 | -6.2819
10010 | R-514A | 1.5 | 1.91 | -12.79 | -6.2819
10011 | R-514A | 1.6 | 1.92 | -12.78 | -6.277
10012 | R-514A | 1.7 | 1.92 | -12.78 | -6.277
10013 | R-514A | 1.8 | 1.93 | -12.77 | -6.272
10014 | R-514A | 1.9 | 1.94 | -12.76 | -6.2671
10015 | R-514A | 2 | 1.94 | -12.76 | -6.2671
10016 | R-514A | 2.1 | 1.95 | -12.75 | -6.2622
10017 | R-514A | 2.2 | 1.95 | -12.75 | -6.2622
10018 | R-514A | 2.3 | 1.96 | -12.74 | -6.2573
10019 | R-514A | 2.4 | 1.96 | -12.74 | -6.2573
10020 | R-514A | 2.5 | 1.97 | -12.73 | -6.2524
10021 | R-514A | 2.6 | 1.98 | -12.72 | -6.2475
10022 | R-514A | 2.7 | 1.98 | -12.72 | -6.2475
10023 | R-514A | 2.8 | 1.99 | -12.71 | -6.2426
10024 | R-514A | 2.9 | 1.99 | -12.71 | -6.2426
10025 | R-514A | 3 | 2 | -12.7 | -6.2377
10026 | R-514A | 3.1 | 2.01 | -12.69 | -6.2328
10027 | R-514A | 3.2 | 2.01 | -12.69 | -6.2328
10028 | R-514A | 3.3 | 2.02 | -12.68 | -6.2278
10029 | R-514A | 3.4 | 2.02 | -12.68 | -6.2278
10030 | R-514A | 3.5 | 2.03 | -12.67 | -6.2229
10031 | R-514A | 3.6 | 2.04 | -12.66 | -6.218
10032 | R-514A | 3.7 | 2.04 | -12.66 | -6.218
10033 | R-514A | 3.8 | 2.05 | -12.65 | -6.2131
10034 | R-514A | 3.9 | 2.05 | -12.65 | -6.2131
10035 | R-514A | 4 | 2.06 | -12.64 | -6.2082
10036 | R-514A | 4.1 | 2.07 | -12.63 | -6.2033
10037 | R-514A | 4.2 | 2.07 | -12.63 | -6.2033
10038 | R-514A | 4.3 | 2.08 | -12.62 | -6.1984
10039 | R-514A | 4.4 | 2.09 | -12.61 | -6.1935
10040 | R-514A | 4.5 | 2.09 | -12.61 | -6.1935
10041 | R-514A | 4.6 | 2.1 | -12.6 | -6.1885
10042 | R-514A | 4.7 | 2.1 | -12.6 | -6.1885
10043 | R-514A | 4.8 | 2.11 | -12.59 | -6.1836
10044 | R-514A | 4.9 | 2.12 | -12.58 | -6.1787
10045 | R-514A | 5 | 2.12 | -12.58 | -6.1787
10046 | R-514A | 5.1 | 2.13 | -12.57 | -6.1738
10047 | R-514A | 5.2 | 2.14 | -12.56 | -6.1689
10048 | R-514A | 5.3 | 2.14 | -12.56 | -6.1689
10049 | R-514A | 5.4 | 2.15 | -12.55 | -6.164
10050 | R-514A | 5.5 | 2.15 | -12.55 | -6.164
10051 | R-514A | 5.6 | 2.16 | -12.54 | -6.1591
10052 | R-514A | 5.7 | 2.17 | -12.53 | -6.1542
10053 | R-514A | 5.8 | 2.17 | -12.53 | -6.1542
10054 | R-514A | 5.9 | 2.18 | -12.52 | -6.1493
10055 | R-514A | 6 | 2.19 | -12.51 | -6.1443
10056 | R-514A | 6.1 | 2.19 | -12.51 | -6.1443
10057 | R-514A | 6.2 | 2.2 | -12.5 | -6.1394
10058 | R-514A | 6.3 | 2.21 | -12.49 | -6.1345
10059 | R-514A | 6.4 | 2.21 | -12.49 | -6.1345
10060 | R-514A | 6.5 | 2.22 | -12.48 | -6.1296
10061 | R-514A | 6.6 | 2.22 | -12.48 | -6.1296
10062 | R-514A | 6.7 | 2.23 | -12.47 | -6.1247
10063 | R-514A | 6.8 | 2.24 | -12.46 | -6.1198
10064 | R-514A | 6.9 | 2.24 | -12.46 | -6.1198
10065 | R-514A | 7 | 2.25 | -12.45 | -6.1149
10066 | R-514A | 7.1 | 2.26 | -12.44 | -6.11
10067 | R-514A | 7.2 | 2.26 | -12.44 | -6.11
10068 | R-514A | 7.3 | 2.27 | -12.43 | -6.1051
10069 | R-514A | 7.4 | 2.28 | -12.42 | -6.1001
10070 | R-514A | 7.5 | 2.28 | -12.42 | -6.1001
10071 | R-514A | 7.6 | 2.29 | -12.41 | -6.0952
10072 | R-514A | 7.7 | 2.3 | -12.4 | -6.0903
10073 | R-514A | 7.8 | 2.3 | -12.4 | -6.0903
10074 | R-514A | 7.9 | 2.31 | -12.39 | -6.0854
10075 | R-514A | 8 | 2.32 | -12.38 | -6.0805
10076 | R-514A | 8.1 | 2.32 | -12.38 | -6.0805
10077 | R-514A | 8.2 | 2.33 | -12.37 | -6.0756
10078 | R-514A | 8.3 | 2.34 | -12.36 | -6.0707
10079 | R-514A | 8.4 | 2.35 | -12.35 | -6.0658
10080 | R-514A | 8.5 | 2.35 | -12.35 | -6.0658
10081 | R-514A | 8.6 | 2.36 | -12.34 | -6.0608
10082 | R-514A | 8.7 | 2.37 | -12.33 | -6.0559
10083 | R-514A | 8.8 | 2.37 | -12.33 | -6.0559
10084 | R-514A | 8.9 | 2.38 | -12.32 | -6.051
10085 | R-514A | 9 | 2.39 | -12.31 | -6.0461
10086 | R-514A | 9.1 | 2.39 | -12.31 | -6.0461
10087 | R-514A | 9.2 | 2.4 | -12.3 | -6.0412
10088 | R-514A | 9.3 | 2.41 | -12.29 | -6.0363
10089 | R-514A | 9.4 | 2.41 | -12.29 | -6.0363
10090 | R-514A | 9.5 | 2.42 | -12.28 | -6.0314
10091 | R-514A | 9.6 | 2.43 | -12.27 | -6.0265
10092 | R-514A | 9.7 | 2.44 | -12.26 | -6.0216
10093 | R-514A | 9.8 | 2.44 | -12.26 | -6.0216
10094 | R-514A | 9.9 | 2.45 | -12.25 | -6.0166
10095 | R-514A | 10 | 2.46 | -12.24 | -6.0117
10096 | R-514A | 10.1 | 2.46 | -12.24 | -6.0117
10097 | R-514A | 10.2 | 2.47 | -12.23 | -6.0068
10098 | R-514A | 10.3 | 2.48 | -12.22 | -6.0019
10099 | R-514A | 10.4 | 2.48 | -12.22 | -6.0019
10100 | R-514A | 10.5 | 2.49 | -12.21 | -5.997
10101 | R-514A | 10.6 | 2.5 | -12.2 | -5.9921
10102 | R-514A | 10.7 | 2.51 | -12.19 | -5.9872
10103 | R-514A | 10.8 | 2.51 | -12.19 | -5.9872
10104 | R-514A | 10.9 | 2.52 | -12.18 | -5.9823
10105 | R-514A | 11 | 2.53 | -12.17 | -5.9774
10106 | R-514A | 11.1 | 2.53 | -12.17 | -5.9774
10107 | R-514A | 11.2 | 2.54 | -12.16 | -5.9724
10108 | R-514A | 11.3 | 2.55 | -12.15 | -5.9675
10109 | R-514A | 11.4 | 2.56 | -12.14 | -5.9626
10110 | R-514A | 11.5 | 2.56 | -12.14 | -5.9626
10111 | R-514A | 11.6 | 2.57 | -12.13 | -5.9577
10112 | R-514A | 11.7 | 2.58 | -12.12 | -5.9528
10113 | R-514A | 11.8 | 2.59 | -12.11 | -5.9479
10114 | R-514A | 11.9 | 2.59 | -12.11 | -5.9479
10115 | R-514A | 12 | 2.6 | -12.1 | -5.943
10116 | R-514A | 12.1 | 2.61 | -12.09 | -5.9381
10117 | R-514A | 12.2 | 2.62 | -12.08 | -5.9331
10118 | R-514A | 12.3 | 2.62 | -12.08 | -5.9331
10119 | R-514A | 12.4 | 2.63 | -12.07 | -5.9282
10120 | R-514A | 12.5 | 2.64 | -12.06 | -5.9233
10121 | R-514A | 12.6 | 2.65 | -12.05 | -5.9184
10122 | R-514A | 12.7 | 2.65 | -12.05 | -5.9184
10123 | R-514A | 12.8 | 2.66 | -12.04 | -5.9135
10124 | R-514A | 12.9 | 2.67 | -12.03 | -5.9086
10125 | R-514A | 13 | 2.68 | -12.02 | -5.9037
10126 | R-514A | 13.1 | 2.68 | -12.02 | -5.9037
10127 | R-514A | 13.2 | 2.69 | -12.01 | -5.8988
10128 | R-514A | 13.3 | 2.7 | -12 | -5.8938
10129 | R-514A | 13.4 | 2.71 | -11.99 | -5.8889
10130 | R-514A | 13.5 | 2.71 | -11.99 | -5.8889
10131 | R-514A | 13.6 | 2.72 | -11.98 | -5.884
10132 | R-514A | 13.7 | 2.73 | -11.97 | -5.8791
10133 | R-514A | 13.8 | 2.74 | -11.96 | -5.8742
10134 | R-514A | 13.9 | 2.75 | -11.95 | -5.8693
10135 | R-514A | 14 | 2.75 | -11.95 | -5.8693
10136 | R-514A | 14.1 | 2.76 | -11.94 | -5.8644
10137 | R-514A | 14.2 | 2.77 | -11.93 | -5.8595
10138 | R-514A | 14.3 | 2.78 | -11.92 | -5.8546
10139 | R-514A | 14.4 | 2.78 | -11.92 | -5.8546
10140 | R-514A | 14.5 | 2.79 | -11.91 | -5.8496
10141 | R-514A | 14.6 | 2.8 | -11.9 | -5.8447
10142 | R-514A | 14.7 | 2.81 | -11.89 | -5.8398
10143 | R-514A | 14.8 | 2.82 | -11.88 | -5.8349
10144 | R-514A | 14.9 | 2.82 | -11.88 | -5.8349
10145 | R-514A | 15 | 2.83 | -11.87 | -5.83
10146 | R-514A | 15.1 | 2.84 | -11.86 | -5.8251
10147 | R-514A | 15.2 | 2.85 | -11.85 | -5.8202
10148 | R-514A | 15.3 | 2.86 | -11.84 | -5.8153
10149 | R-514A | 15.4 | 2.86 | -11.84 | -5.8153
10150 | R-514A | 15.5 | 2.87 | -11.83 | -5.8104
10151 | R-514A | 15.6 | 2.88 | -11.82 | -5.8054
10152 | R-514A | 15.7 | 2.89 | -11.81 | -5.8005
10153 | R-514A | 15.8 | 2.9 | -11.8 | -5.7956
10154 | R-514A | 15.9 | 2.9 | -11.8 | -5.7956
10155 | R-514A | 16 | 2.91 | -11.79 | -5.7907
10156 | R-514A | 16.1 | 2.92 | -11.78 | -5.7858
10157 | R-514A | 16.2 | 2.93 | -11.77 | -5.7809
10158 | R-514A | 16.3 | 2.94 | -11.76 | -5.776
10159 | R-514A | 16.4 | 2.95 | -11.75 | -5.7711
10160 | R-514A | 16.5 | 2.95 | -11.75 | -5.7711
10161 | R-514A | 16.6 | 2.96 | -11.74 | -5.7661
10162 | R-514A | 16.7 | 2.97 | -11.73 | -5.7612
10163 | R-514A | 16.8 | 2.98 | -11.72 | -5.7563
10164 | R-514A | 16.9 | 2.99 | -11.71 | -5.7514
10165 | R-514A | 17 | 2.99 | -11.71 | -5.7514
10166 | R-514A | 17.1 | 3 | -11.7 | -5.7465
10167 | R-514A | 17.2 | 3.01 | -11.69 | -5.7416
10168 | R-514A | 17.3 | 3.02 | -11.68 | -5.7367
10169 | R-514A | 17.4 | 3.03 | -11.67 | -5.7318
10170 | R-514A | 17.5 | 3.04 | -11.66 | -5.7269
10171 | R-514A | 17.6 | 3.05 | -11.65 | -5.7219
10172 | R-514A | 17.7 | 3.05 | -11.65 | -5.7219
10173 | R-514A | 17.8 | 3.06 | -11.64 | -5.717
10174 | R-514A | 17.9 | 3.07 | -11.63 | -5.7121
10175 | R-514A | 18 | 3.08 | -11.62 | -5.7072
10176 | R-514A | 18.1 | 3.09 | -11.61 | -5.7023
10177 | R-514A | 18.2 | 3.1 | -11.6 | -5.6974
10178 | R-514A | 18.3 | 3.1 | -11.6 | -5.6974
10179 | R-514A | 18.4 | 3.11 | -11.59 | -5.6925
10180 | R-514A | 18.5 | 3.12 | -11.58 | -5.6876
10181 | R-514A | 18.6 | 3.13 | -11.57 | -5.6827
10182 | R-514A | 18.7 | 3.14 | -11.56 | -5.6777
10183 | R-514A | 18.8 | 3.15 | -11.55 | -5.6728
10184 | R-514A | 18.9 | 3.16 | -11.54 | -5.6679
10185 | R-514A | 19 | 3.16 | -11.54 | -5.6679
10186 | R-514A | 19.1 | 3.17 | -11.53 | -5.663
10187 | R-514A | 19.2 | 3.18 | -11.52 | -5.6581
10188 | R-514A | 19.3 | 3.19 | -11.51 | -5.6532
10189 | R-514A | 19.4 | 3.2 | -11.5 | -5.6483
10190 | R-514A | 19.5 | 3.21 | -11.49 | -5.6434
10191 | R-514A | 19.6 | 3.22 | -11.48 | -5.6384
10192 | R-514A | 19.7 | 3.23 | -11.47 | -5.6335
10193 | R-514A | 19.8 | 3.24 | -11.46 | -5.6286
10194 | R-514A | 19.9 | 3.24 | -11.46 | -5.6286
10195 | R-514A | 20 | 3.25 | -11.45 | -5.6237
10196 | R-514A | 20.1 | 3.26 | -11.44 | -5.6188
10197 | R-514A | 20.2 | 3.27 | -11.43 | -5.6139
10198 | R-514A | 20.3 | 3.28 | -11.42 | -5.609
10199 | R-514A | 20.4 | 3.29 | -11.41 | -5.6041
10200 | R-514A | 20.5 | 3.3 | -11.4 | -5.5992
10201 | R-514A | 20.6 | 3.31 | -11.39 | -5.5942
10202 | R-514A | 20.7 | 3.32 | -11.38 | -5.5893
10203 | R-514A | 20.8 | 3.33 | -11.37 | -5.5844
10204 | R-514A | 20.9 | 3.33 | -11.37 | -5.5844
10205 | R-514A | 21 | 3.34 | -11.36 | -5.5795
10206 | R-514A | 21.1 | 3.35 | -11.35 | -5.5746
10207 | R-514A | 21.2 | 3.36 | -11.34 | -5.5697
10208 | R-514A | 21.3 | 3.37 | -11.33 | -5.5648
10209 | R-514A | 21.4 | 3.38 | -11.32 | -5.5599
10210 | R-514A | 21.5 | 3.39 | -11.31 | -5.555
10211 | R-514A | 21.6 | 3.4 | -11.3 | -5.55
10212 | R-514A | 21.7 | 3.41 | -11.29 | -5.5451
10213 | R-514A | 21.8 | 3.42 | -11.28 | -5.5402
10214 | R-514A | 21.9 | 3.43 | -11.27 | -5.5353
10215 | R-514A | 22 | 3.44 | -11.26 | -5.5304
10216 | R-514A | 22.1 | 3.44 | -11.26 | -5.5304
10217 | R-514A | 22.2 | 3.45 | -11.25 | -5.5255
10218 | R-514A | 22.3 | 3.46 | -11.24 | -5.5206
10219 | R-514A | 22.4 | 3.47 | -11.23 | -5.5157
10220 | R-514A | 22.5 | 3.48 | -11.22 | -5.5107
10221 | R-514A | 22.6 | 3.49 | -11.21 | -5.5058
10222 | R-514A | 22.7 | 3.5 | -11.2 | -5.5009
10223 | R-514A | 22.8 | 3.51 | -11.19 | -5.496
10224 | R-514A | 22.9 | 3.52 | -11.18 | -5.4911
10225 | R-514A | 23 | 3.53 | -11.17 | -5.4862
10226 | R-514A | 23.1 | 3.54 | -11.16 | -5.4813
10227 | R-514A | 23.2 | 3.55 | -11.15 | -5.4764
10228 | R-514A | 23.3 | 3.56 | -11.14 | -5.4715
10229 | R-514A | 23.4 | 3.57 | -11.13 | -5.4665
10230 | R-514A | 23.5 | 3.58 | -11.12 | -5.4616
10231 | R-514A | 23.6 | 3.59 | -11.11 | -5.4567
10232 | R-514A | 23.7 | 3.6 | -11.1 | -5.4518
10233 | R-514A | 23.8 | 3.61 | -11.09 | -5.4469
10234 | R-514A | 23.9 | 3.62 | -11.08 | -5.442
10235 | R-514A | 24 | 3.63 | -11.07 | -5.4371
10236 | R-514A | 24.1 | 3.64 | -11.06 | -5.4322
10237 | R-514A | 24.2 | 3.65 | -11.05 | -5.4273
10238 | R-514A | 24.3 | 3.66 | -11.04 | -5.4223
10239 | R-514A | 24.4 | 3.67 | -11.03 | -5.4174
10240 | R-514A | 24.5 | 3.68 | -11.02 | -5.4125
10241 | R-514A | 24.6 | 3.69 | -11.01 | -5.4076
10242 | R-514A | 24.7 | 3.7 | -11 | -5.4027
10243 | R-514A | 24.8 | 3.7 | -11 | -5.4027
10244 | R-514A | 24.9 | 3.71 | -10.99 | -5.3978
10245 | R-514A | 25 | 3.72 | -10.98 | -5.3929
10246 | R-514A | 25.1 | 3.73 | -10.97 | -5.388
10247 | R-514A | 25.2 | 3.74 | -10.96 | -5.383
10248 | R-514A | 25.3 | 3.75 | -10.95 | -5.3781
10249 | R-514A | 25.4 | 3.76 | -10.94 | -5.3732
10250 | R-514A | 25.5 | 3.77 | -10.93 | -5.3683
10251 | R-514A | 25.6 | 3.78 | -10.92 | -5.3634
10252 | R-514A | 25.7 | 3.8 | -10.9 | -5.3536
10253 | R-514A | 25.8 | 3.81 | -10.89 | -5.3487
10254 | R-514A | 25.9 | 3.82 | -10.88 | -5.3438
10255 | R-514A | 26 | 3.83 | -10.87 | -5.3388
10256 | R-514A | 26.1 | 3.84 | -10.86 | -5.3339
10257 | R-514A | 26.2 | 3.85 | -10.85 | -5.329
10258 | R-514A | 26.3 | 3.86 | -10.84 | -5.3241
10259 | R-514A | 26.4 | 3.87 | -10.83 | -5.3192
10260 | R-514A | 26.5 | 3.88 | -10.82 | -5.3143
10261 | R-514A | 26.6 | 3.89 | -10.81 | -5.3094
10262 | R-514A | 26.7 | 3.9 | -10.8 | -5.3045
10263 | R-514A | 26.8 | 3.91 | -10.79 | -5.2996
10264 | R-514A | 26.9 | 3.92 | -10.78 | -5.2946
10265 | R-514A | 27 | 3.93 | -10.77 | -5.2897
10266 | R-514A | 27.1 | 3.94 | -10.76 | -5.2848
10267 | R-514A | 27.2 | 3.95 | -10.75 | -5.2799
10268 | R-514A | 27.3 | 3.96 | -10.74 | -5.275
10269 | R-514A | 27.4 | 3.97 | -10.73 | -5.2701
10270 | R-514A | 27.5 | 3.98 | -10.72 | -5.2652
10271 | R-514A | 27.6 | 3.99 | -10.71 | -5.2603
10272 | R-514A | 27.7 | 4 | -10.7 | -5.2553
10273 | R-514A | 27.8 | 4.01 | -10.69 | -5.2504
10274 | R-514A | 27.9 | 4.02 | -10.68 | -5.2455
10275 | R-514A | 28 | 4.03 | -10.67 | -5.2406
10276 | R-514A | 28.1 | 4.04 | -10.66 | -5.2357
10277 | R-514A | 28.2 | 4.05 | -10.65 | -5.2308
10278 | R-514A | 28.3 | 4.07 | -10.63 | -5.221
10279 | R-514A | 28.4 | 4.08 | -10.62 | -5.2161
10280 | R-514A | 28.5 | 4.09 | -10.61 | -5.2111
10281 | R-514A | 28.6 | 4.1 | -10.6 | -5.2062
10282 | R-514A | 28.7 | 4.11 | -10.59 | -5.2013
10283 | R-514A | 28.8 | 4.12 | -10.58 | -5.1964
10284 | R-514A | 28.9 | 4.13 | -10.57 | -5.1915
10285 | R-514A | 29 | 4.14 | -10.56 | -5.1866
10286 | R-514A | 29.1 | 4.15 | -10.55 | -5.1817
10287 | R-514A | 29.2 | 4.16 | -10.54 | -5.1768
10288 | R-514A | 29.3 | 4.17 | -10.53 | -5.1719
10289 | R-514A | 29.4 | 4.18 | -10.52 | -5.1669
10290 | R-514A | 29.5 | 4.2 | -10.5 | -5.1571
10291 | R-514A | 29.6 | 4.21 | -10.49 | -5.1522
10292 | R-514A | 29.7 | 4.22 | -10.48 | -5.1473
10293 | R-514A | 29.8 | 4.23 | -10.47 | -5.1424
10294 | R-514A | 29.9 | 4.24 | -10.46 | -5.1375
10295 | R-514A | 30 | 4.25 | -10.45 | -5.1326
10296 | R-514A | 30.1 | 4.26 | -10.44 | -5.1277
10297 | R-514A | 30.2 | 4.27 | -10.43 | -5.1227
10298 | R-514A | 30.3 | 4.28 | -10.42 | -5.1178
10299 | R-514A | 30.4 | 4.3 | -10.4 | -5.108
10300 | R-514A | 30.5 | 4.31 | -10.39 | -5.1031
10301 | R-514A | 30.6 | 4.32 | -10.38 | -5.0982
10302 | R-514A | 30.7 | 4.33 | -10.37 | -5.0933
10303 | R-514A | 30.8 | 4.34 | -10.36 | -5.0884
10304 | R-514A | 30.9 | 4.35 | -10.35 | -5.0835
10305 | R-514A | 31 | 4.36 | -10.34 | -5.0785
10306 | R-514A | 31.1 | 4.37 | -10.33 | -5.0736
10307 | R-514A | 31.2 | 4.39 | -10.31 | -5.0638
10308 | R-514A | 31.3 | 4.4 | -10.3 | -5.0589
10309 | R-514A | 31.4 | 4.41 | -10.29 | -5.054
10310 | R-514A | 31.5 | 4.42 | -10.28 | -5.0491
10311 | R-514A | 31.6 | 4.43 | -10.27 | -5.0442
10312 | R-514A | 31.7 | 4.44 | -10.26 | -5.0392
10313 | R-514A | 31.8 | 4.45 | -10.25 | -5.0343
10314 | R-514A | 31.9 | 4.47 | -10.23 | -5.0245
10315 | R-514A | 32 | 4.48 | -10.22 | -5.0196
10316 | R-514A | 32.1 | 4.49 | -10.21 | -5.0147
10317 | R-514A | 32.2 | 4.5 | -10.2 | -5.0098
10318 | R-514A | 32.3 | 4.51 | -10.19 | -5.0049
10319 | R-514A | 32.4 | 4.52 | -10.18 | -5
10320 | R-514A | 32.5 | 4.54 | -10.16 | -4.9901
10321 | R-514A | 32.6 | 4.55 | -10.15 | -4.9852
10322 | R-514A | 32.7 | 4.56 | -10.14 | -4.9803
10323 | R-514A | 32.8 | 4.57 | -10.13 | -4.9754
10324 | R-514A | 32.9 | 4.58 | -10.12 | -4.9705
10325 | R-514A | 33 | 4.59 | -10.11 | -4.9656
10326 | R-514A | 33.1 | 4.61 | -10.09 | -4.9558
10327 | R-514A | 33.2 | 4.62 | -10.08 | -4.9508
10328 | R-514A | 33.3 | 4.63 | -10.07 | -4.9459
10329 | R-514A | 33.4 | 4.64 | -10.06 | -4.941
10330 | R-514A | 33.5 | 4.65 | -10.05 | -4.9361
10331 | R-514A | 33.6 | 4.67 | -10.03 | -4.9263
10332 | R-514A | 33.7 | 4.68 | -10.02 | -4.9214
10333 | R-514A | 33.8 | 4.69 | -10.01 | -4.9165
10334 | R-514A | 33.9 | 4.7 | -10 | -4.9115
10335 | R-514A | 34 | 4.71 | -9.99 | -4.9066
10336 | R-514A | 34.1 | 4.73 | -9.97 | -4.8968
10337 | R-514A | 34.2 | 4.74 | -9.96 | -4.8919
10338 | R-514A | 34.3 | 4.75 | -9.95 | -4.887
10339 | R-514A | 34.4 | 4.76 | -9.94 | -4.8821
10340 | R-514A | 34.5 | 4.77 | -9.93 | -4.8772
10341 | R-514A | 34.6 | 4.79 | -9.91 | -4.8673
10342 | R-514A | 34.7 | 4.8 | -9.9 | -4.8624
10343 | R-514A | 34.8 | 4.81 | -9.89 | -4.8575
10344 | R-514A | 34.9 | 4.82 | -9.88 | -4.8526
10345 | R-514A | 35 | 4.83 | -9.87 | -4.8477
10346 | R-514A | 35.1 | 4.85 | -9.85 | -4.8379
10347 | R-514A | 35.2 | 4.86 | -9.84 | -4.833
10348 | R-514A | 35.3 | 4.87 | -9.83 | -4.8281
10349 | R-514A | 35.4 | 4.88 | -9.82 | -4.8231
10350 | R-514A | 35.5 | 4.9 | -9.8 | -4.8133
10351 | R-514A | 35.6 | 4.91 | -9.79 | -4.8084
10352 | R-514A | 35.7 | 4.92 | -9.78 | -4.8035
10353 | R-514A | 35.8 | 4.93 | -9.77 | -4.7986
10354 | R-514A | 35.9 | 4.95 | -9.75 | -4.7888
10355 | R-514A | 36 | 4.96 | -9.74 | -4.7838
10356 | R-514A | 36.1 | 4.97 | -9.73 | -4.7789
10357 | R-514A | 36.2 | 4.98 | -9.72 | -4.774
10358 | R-514A | 36.3 | 5 | -9.7 | -4.7642
10359 | R-514A | 36.4 | 5.01 | -9.69 | -4.7593
10360 | R-514A | 36.5 | 5.02 | -9.68 | -4.7544
10361 | R-514A | 36.6 | 5.04 | -9.66 | -4.7446
10362 | R-514A | 36.7 | 5.05 | -9.65 | -4.7396
10363 | R-514A | 36.8 | 5.06 | -9.64 | -4.7347
10364 | R-514A | 36.9 | 5.07 | -9.63 | -4.7298
10365 | R-514A | 37 | 5.09 | -9.61 | -4.72
10366 | R-514A | 37.1 | 5.1 | -9.6 | -4.7151
10367 | R-514A | 37.2 | 5.11 | -9.59 | -4.7102
10368 | R-514A | 37.3 | 5.12 | -9.58 | -4.7053
10369 | R-514A | 37.4 | 5.14 | -9.56 | -4.6954
10370 | R-514A | 37.5 | 5.15 | -9.55 | -4.6905
10371 | R-514A | 37.6 | 5.16 | -9.54 | -4.6856
10372 | R-514A | 37.7 | 5.18 | -9.52 | -4.6758
10373 | R-514A | 37.8 | 5.19 | -9.51 | -4.6709
10374 | R-514A | 37.9 | 5.2 | -9.5 | -4.666
10375 | R-514A | 38 | 5.22 | -9.48 | -4.6561
10376 | R-514A | 38.1 | 5.23 | -9.47 | -4.6512
10377 | R-514A | 38.2 | 5.24 | -9.46 | -4.6463
10378 | R-514A | 38.3 | 5.26 | -9.44 | -4.6365
10379 | R-514A | 38.4 | 5.27 | -9.43 | -4.6316
10380 | R-514A | 38.5 | 5.28 | -9.42 | -4.6267
10381 | R-514A | 38.6 | 5.29 | -9.41 | -4.6218
10382 | R-514A | 38.7 | 5.31 | -9.39 | -4.6119
10383 | R-514A | 38.8 | 5.32 | -9.38 | -4.607
10384 | R-514A | 38.9 | 5.33 | -9.37 | -4.6021
10385 | R-514A | 39 | 5.35 | -9.35 | -4.5923
10386 | R-514A | 39.1 | 5.36 | -9.34 | -4.5874
10387 | R-514A | 39.2 | 5.37 | -9.33 | -4.5825
10388 | R-514A | 39.3 | 5.39 | -9.31 | -4.5727
10389 | R-514A | 39.4 | 5.4 | -9.3 | -4.5677
10390 | R-514A | 39.5 | 5.42 | -9.28 | -4.5579
10391 | R-514A | 39.6 | 5.43 | -9.27 | -4.553
10392 | R-514A | 39.7 | 5.44 | -9.26 | -4.5481
10393 | R-514A | 39.8 | 5.46 | -9.24 | -4.5383
10394 | R-514A | 39.9 | 5.47 | -9.23 | -4.5334
10395 | R-514A | 40 | 5.48 | -9.22 | -4.5284
10396 | R-514A | 40.1 | 5.5 | -9.2 | -4.5186
10397 | R-514A | 40.2 | 5.51 | -9.19 | -4.5137
10398 | R-514A | 40.3 | 5.52 | -9.18 | -4.5088
10399 | R-514A | 40.4 | 5.54 | -9.16 | -4.499
10400 | R-514A | 40.5 | 5.55 | -9.15 | -4.4941
10401 | R-514A | 40.6 | 5.57 | -9.13 | -4.4842
10402 | R-514A | 40.7 | 5.58 | -9.12 | -4.4793
10403 | R-514A | 40.8 | 5.59 | -9.11 | -4.4744
10404 | R-514A | 40.9 | 5.61 | -9.09 | -4.4646
10405 | R-514A | 41 | 5.62 | -9.08 | -4.4597
10406 | R-514A | 41.1 | 5.63 | -9.07 | -4.4548
10407 | R-514A | 41.2 | 5.65 | -9.05 | -4.445
10408 | R-514A | 41.3 | 5.66 | -9.04 | -4.44
10409 | R-514A | 41.4 | 5.68 | -9.02 | -4.4302
10410 | R-514A | 41.5 | 5.69 | -9.01 | -4.4253
10411 | R-514A | 41.6 | 5.7 | -9 | -4.4204
10412 | R-514A | 41.7 | 5.72 | -8.98 | -4.4106
10413 | R-514A | 41.8 | 5.73 | -8.97 | -4.4056
10414 | R-514A | 41.9 | 5.75 | -8.95 | -4.3958
10415 | R-514A | 42 | 5.76 | -8.94 | -4.3909
10416 | R-514A | 42.1 | 5.77 | -8.93 | -4.386
10417 | R-514A | 42.2 | 5.79 | -8.91 | -4.3762
10418 | R-514A | 42.3 | 5.8 | -8.9 | -4.3713
10419 | R-514A | 42.4 | 5.82 | -8.88 | -4.3614
10420 | R-514A | 42.5 | 5.83 | -8.87 | -4.3565
10421 | R-514A | 42.6 | 5.85 | -8.85 | -4.3467
10422 | R-514A | 42.7 | 5.86 | -8.84 | -4.3418
10423 | R-514A | 42.8 | 5.88 | -8.82 | -4.332
10424 | R-514A | 42.9 | 5.89 | -8.81 | -4.3271
10425 | R-514A | 43 | 5.9 | -8.8 | -4.3222
10426 | R-514A | 43.1 | 5.92 | -8.78 | -4.3123
10427 | R-514A | 43.2 | 5.93 | -8.77 | -4.3074
10428 | R-514A | 43.3 | 5.95 | -8.75 | -4.2976
10429 | R-514A | 43.4 | 5.96 | -8.74 | -4.2927
10430 | R-514A | 43.5 | 5.98 | -8.72 | -4.2829
10431 | R-514A | 43.6 | 5.99 | -8.71 | -4.2779
10432 | R-514A | 43.7 | 6.01 | -8.69 | -4.2681
10433 | R-514A | 43.8 | 6.02 | -8.68 | -4.2632
10434 | R-514A | 43.9 | 6.04 | -8.66 | -4.2534
10435 | R-514A | 44 | 6.05 | -8.65 | -4.2485
10436 | R-514A | 44.1 | 6.06 | -8.64 | -4.2436
10437 | R-514A | 44.2 | 6.08 | -8.62 | -4.2337
10438 | R-514A | 44.3 | 6.09 | -8.61 | -4.2288
10439 | R-514A | 44.4 | 6.11 | -8.59 | -4.219
10440 | R-514A | 44.5 | 6.12 | -8.58 | -4.2141
10441 | R-514A | 44.6 | 6.14 | -8.56 | -4.2043
10442 | R-514A | 44.7 | 6.15 | -8.55 | -4.1994
10443 | R-514A | 44.8 | 6.17 | -8.53 | -4.1895
10444 | R-514A | 44.9 | 6.18 | -8.52 | -4.1846
10445 | R-514A | 45 | 6.2 | -8.5 | -4.1748
10446 | R-514A | 45.1 | 6.21 | -8.49 | -4.1699
10447 | R-514A | 45.2 | 6.23 | -8.47 | -4.1601
10448 | R-514A | 45.3 | 6.24 | -8.46 | -4.1552
10449 | R-514A | 45.4 | 6.26 | -8.44 | -4.1453
10450 | R-514A | 45.5 | 6.27 | -8.43 | -4.1404
10451 | R-514A | 45.6 | 6.29 | -8.41 | -4.1306
10452 | R-514A | 45.7 | 6.31 | -8.39 | -4.1208
10453 | R-514A | 45.8 | 6.32 | -8.38 | -4.1159
10454 | R-514A | 45.9 | 6.34 | -8.36 | -4.106
10455 | R-514A | 46 | 6.35 | -8.35 | -4.1011
10456 | R-514A | 46.1 | 6.37 | -8.33 | -4.0913
10457 | R-514A | 46.2 | 6.38 | -8.32 | -4.0864
10458 | R-514A | 46.3 | 6.4 | -8.3 | -4.0766
10459 | R-514A | 46.4 | 6.41 | -8.29 | -4.0717
10460 | R-514A | 46.5 | 6.43 | -8.27 | -4.0618
10461 | R-514A | 46.6 | 6.44 | -8.26 | -4.0569
10462 | R-514A | 46.7 | 6.46 | -8.24 | -4.0471
10463 | R-514A | 46.8 | 6.47 | -8.23 | -4.0422
10464 | R-514A | 46.9 | 6.49 | -8.21 | -4.0324
10465 | R-514A | 47 | 6.51 | -8.19 | -4.0225
10466 | R-514A | 47.1 | 6.52 | -8.18 | -4.0176
10467 | R-514A | 47.2 | 6.54 | -8.16 | -4.0078
10468 | R-514A | 47.3 | 6.55 | -8.15 | -4.0029
10469 | R-514A | 47.4 | 6.57 | -8.13 | -3.9931
10470 | R-514A | 47.5 | 6.58 | -8.12 | -3.9882
10471 | R-514A | 47.6 | 6.6 | -8.1 | -3.9783
10472 | R-514A | 47.7 | 6.62 | -8.08 | -3.9685
10473 | R-514A | 47.8 | 6.63 | -8.07 | -3.9636
10474 | R-514A | 47.9 | 6.65 | -8.05 | -3.9538
10475 | R-514A | 48 | 6.66 | -8.04 | -3.9489
10476 | R-514A | 48.1 | 6.68 | -8.02 | -3.9391
10477 | R-514A | 48.2 | 6.7 | -8 | -3.9292
10478 | R-514A | 48.3 | 6.71 | -7.99 | -3.9243
10479 | R-514A | 48.4 | 6.73 | -7.97 | -3.9145
10480 | R-514A | 48.5 | 6.74 | -7.96 | -3.9096
10481 | R-514A | 48.6 | 6.76 | -7.94 | -3.8998
10482 | R-514A | 48.7 | 6.78 | -7.92 | -3.8899
10483 | R-514A | 48.8 | 6.79 | -7.91 | -3.885
10484 | R-514A | 48.9 | 6.81 | -7.89 | -3.8752
10485 | R-514A | 49 | 6.82 | -7.88 | -3.8703
10486 | R-514A | 49.1 | 6.84 | -7.86 | -3.8605
10487 | R-514A | 49.2 | 6.86 | -7.84 | -3.8506
10488 | R-514A | 49.3 | 6.87 | -7.83 | -3.8457
10489 | R-514A | 49.4 | 6.89 | -7.81 | -3.8359
10490 | R-514A | 49.5 | 6.91 | -7.79 | -3.8261
10491 | R-514A | 49.6 | 6.92 | -7.78 | -3.8212
10492 | R-514A | 49.7 | 6.94 | -7.76 | -3.8114
10493 | R-514A | 49.8 | 6.96 | -7.74 | -3.8015
10494 | R-514A | 49.9 | 6.97 | -7.73 | -3.7966
10495 | R-514A | 50 | 6.99 | -7.71 | -3.7868
10496 | R-514A | 50.1 | 7.01 | -7.69 | -3.777
10497 | R-514A | 50.2 | 7.02 | -7.68 | -3.7721
10498 | R-514A | 50.3 | 7.04 | -7.66 | -3.7622
10499 | R-514A | 50.4 | 7.06 | -7.64 | -3.7524
10500 | R-514A | 50.5 | 7.07 | -7.63 | -3.7475
10501 | R-514A | 50.6 | 7.09 | -7.61 | -3.7377
10502 | R-514A | 50.7 | 7.11 | -7.59 | -3.7279
10503 | R-514A | 50.8 | 7.12 | -7.58 | -3.7229
10504 | R-514A | 50.9 | 7.14 | -7.56 | -3.7131
10505 | R-514A | 51 | 7.16 | -7.54 | -3.7033
10506 | R-514A | 51.1 | 7.17 | -7.53 | -3.6984
10507 | R-514A | 51.2 | 7.19 | -7.51 | -3.6886
10508 | R-514A | 51.3 | 7.21 | -7.49 | -3.6787
10509 | R-514A | 51.4 | 7.22 | -7.48 | -3.6738
10510 | R-514A | 51.5 | 7.24 | -7.46 | -3.664
10511 | R-514A | 51.6 | 7.26 | -7.44 | -3.6542
10512 | R-514A | 51.7 | 7.28 | -7.42 | -3.6444
10513 | R-514A | 51.8 | 7.29 | -7.41 | -3.6395
10514 | R-514A | 51.9 | 7.31 | -7.39 | -3.6296
10515 | R-514A | 52 | 7.33 | -7.37 | -3.6198
10516 | R-514A | 52.1 | 7.34 | -7.36 | -3.6149
10517 | R-514A | 52.2 | 7.36 | -7.34 | -3.6051
10518 | R-514A | 52.3 | 7.38 | -7.32 | -3.5953
10519 | R-514A | 52.4 | 7.4 | -7.3 | -3.5854
10520 | R-514A | 52.5 | 7.41 | -7.29 | -3.5805
10521 | R-514A | 52.6 | 7.43 | -7.27 | -3.5707
10522 | R-514A | 52.7 | 7.45 | -7.25 | -3.5609
10523 | R-514A | 52.8 | 7.47 | -7.23 | -3.5511
10524 | R-514A | 52.9 | 7.48 | -7.22 | -3.5461
10525 | R-514A | 53 | 7.5 | -7.2 | -3.5363
10526 | R-514A | 53.1 | 7.52 | -7.18 | -3.5265
10527 | R-514A | 53.2 | 7.54 | -7.16 | -3.5167
10528 | R-514A | 53.3 | 7.55 | -7.15 | -3.5118
10529 | R-514A | 53.4 | 7.57 | -7.13 | -3.5019
10530 | R-514A | 53.5 | 7.59 | -7.11 | -3.4921
10531 | R-514A | 53.6 | 7.61 | -7.09 | -3.4823
10532 | R-514A | 53.7 | 7.62 | -7.08 | -3.4774
10533 | R-514A | 53.8 | 7.64 | -7.06 | -3.4676
10534 | R-514A | 53.9 | 7.66 | -7.04 | -3.4577
10535 | R-514A | 54 | 7.68 | -7.02 | -3.4479
10536 | R-514A | 54.1 | 7.7 | -7 | -3.4381
10537 | R-514A | 54.2 | 7.71 | -6.99 | -3.4332
10538 | R-514A | 54.3 | 7.73 | -6.97 | -3.4234
10539 | R-514A | 54.4 | 7.75 | -6.95 | -3.4135
10540 | R-514A | 54.5 | 7.77 | -6.93 | -3.4037
10541 | R-514A | 54.6 | 7.79 | -6.91 | -3.3939
10542 | R-514A | 54.7 | 7.8 | -6.9 | -3.389
10543 | R-514A | 54.8 | 7.82 | -6.88 | -3.3791
10544 | R-514A | 54.9 | 7.84 | -6.86 | -3.3693
10545 | R-514A | 55 | 7.86 | -6.84 | -3.3595
10546 | R-514A | 55.1 | 7.88 | -6.82 | -3.3497
10547 | R-514A | 55.2 | 7.89 | -6.81 | -3.3448
10548 | R-514A | 55.3 | 7.91 | -6.79 | -3.3349
10549 | R-514A | 55.4 | 7.93 | -6.77 | -3.3251
10550 | R-514A | 55.5 | 7.95 | -6.75 | -3.3153
10551 | R-514A | 55.6 | 7.97 | -6.73 | -3.3055
10552 | R-514A | 55.7 | 7.99 | -6.71 | -3.2957
10553 | R-514A | 55.8 | 8 | -6.7 | -3.2907
10554 | R-514A | 55.9 | 8.02 | -6.68 | -3.2809
10555 | R-514A | 56 | 8.04 | -6.66 | -3.2711
10556 | R-514A | 56.1 | 8.06 | -6.64 | -3.2613
10557 | R-514A | 56.2 | 8.08 | -6.62 | -3.2514
10558 | R-514A | 56.3 | 8.1 | -6.6 | -3.2416
10559 | R-514A | 56.4 | 8.12 | -6.58 | -3.2318
10560 | R-514A | 56.5 | 8.13 | -6.57 | -3.2269
10561 | R-514A | 56.6 | 8.15 | -6.55 | -3.2171
10562 | R-514A | 56.7 | 8.17 | -6.53 | -3.2072
10563 | R-514A | 56.8 | 8.19 | -6.51 | -3.1974
10564 | R-514A | 56.9 | 8.21 | -6.49 | -3.1876
10565 | R-514A | 57 | 8.23 | -6.47 | -3.1778
10566 | R-514A | 57.1 | 8.25 | -6.45 | -3.1679
10567 | R-514A | 57.2 | 8.27 | -6.43 | -3.1581
10568 | R-514A | 57.3 | 8.29 | -6.41 | -3.1483
10569 | R-514A | 57.4 | 8.3 | -6.4 | -3.1434
10570 | R-514A | 57.5 | 8.32 | -6.38 | -3.1336
10571 | R-514A | 57.6 | 8.34 | -6.36 | -3.1237
10572 | R-514A | 57.7 | 8.36 | -6.34 | -3.1139
10573 | R-514A | 57.8 | 8.38 | -6.32 | -3.1041
10574 | R-514A | 57.9 | 8.4 | -6.3 | -3.0943
10575 | R-514A | 58 | 8.42 | -6.28 | -3.0844
10576 | R-514A | 58.1 | 8.44 | -6.26 | -3.0746
10577 | R-514A | 58.2 | 8.46 | -6.24 | -3.0648
10578 | R-514A | 58.3 | 8.48 | -6.22 | -3.055
10579 | R-514A | 58.4 | 8.5 | -6.2 | -3.0452
10580 | R-514A | 58.5 | 8.52 | -6.18 | -3.0353
10581 | R-514A | 58.6 | 8.53 | -6.17 | -3.0304
10582 | R-514A | 58.7 | 8.55 | -6.15 | -3.0206
10583 | R-514A | 58.8 | 8.57 | -6.13 | -3.0108
10584 | R-514A | 58.9 | 8.59 | -6.11 | -3.001
10585 | R-514A | 59 | 8.61 | -6.09 | -2.9911
10586 | R-514A | 59.1 | 8.63 | -6.07 | -2.9813
10587 | R-514A | 59.2 | 8.65 | -6.05 | -2.9715
10588 | R-514A | 59.3 | 8.67 | -6.03 | -2.9617
10589 | R-514A | 59.4 | 8.69 | -6.01 | -2.9518
10590 | R-514A | 59.5 | 8.71 | -5.99 | -2.942
10591 | R-514A | 59.6 | 8.73 | -5.97 | -2.9322
10592 | R-514A | 59.7 | 8.75 | -5.95 | -2.9224
10593 | R-514A | 59.8 | 8.77 | -5.93 | -2.9125
10594 | R-514A | 59.9 | 8.79 | -5.91 | -2.9027
10595 | R-514A | 60 | 8.81 | -5.89 | -2.8929
10596 | R-514A | 60.1 | 8.83 | -5.87 | -2.8831
10597 | R-514A | 60.2 | 8.85 | -5.85 | -2.8733
10598 | R-514A | 60.3 | 8.87 | -5.83 | -2.8634
10599 | R-514A | 60.4 | 8.89 | -5.81 | -2.8536
10600 | R-514A | 60.5 | 8.91 | -5.79 | -2.8438
10601 | R-514A | 60.6 | 8.93 | -5.77 | -2.834
10602 | R-514A | 60.7 | 8.95 | -5.75 | -2.8241
10603 | R-514A | 60.8 | 8.97 | -5.73 | -2.8143
10604 | R-514A | 60.9 | 8.99 | -5.71 | -2.8045
10605 | R-514A | 61 | 9.01 | -5.69 | -2.7947
10606 | R-514A | 61.1 | 9.03 | -5.67 | -2.7848
10607 | R-514A | 61.2 | 9.05 | -5.65 | -2.775
10608 | R-514A | 61.3 | 9.07 | -5.63 | -2.7652
10609 | R-514A | 61.4 | 9.09 | -5.61 | -2.7554
10610 | R-514A | 61.5 | 9.11 | -5.59 | -2.7456
10611 | R-514A | 61.6 | 9.13 | -5.57 | -2.7357
10612 | R-514A | 61.7 | 9.15 | -5.55 | -2.7259
10613 | R-514A | 61.8 | 9.18 | -5.52 | -2.7112
10614 | R-514A | 61.9 | 9.2 | -5.5 | -2.7014
10615 | R-514A | 62 | 9.22 | -5.48 | -2.6915
10616 | R-514A | 62.1 | 9.24 | -5.46 | -2.6817
10617 | R-514A | 62.2 | 9.26 | -5.44 | -2.6719
10618 | R-514A | 62.3 | 9.28 | -5.42 | -2.6621
10619 | R-514A | 62.4 | 9.3 | -5.4 | -2.6522
10620 | R-514A | 62.5 | 9.32 | -5.38 | -2.6424
10621 | R-514A | 62.6 | 9.34 | -5.36 | -2.6326
10622 | R-514A | 62.7 | 9.36 | -5.34 | -2.6228
10623 | R-514A | 62.8 | 9.38 | -5.32 | -2.6129
10624 | R-514A | 62.9 | 9.4 | -5.3 | -2.6031
10625 | R-514A | 63 | 9.42 | -5.28 | -2.5933
10626 | R-514A | 63.1 | 9.45 | -5.25 | -2.5786
10627 | R-514A | 63.2 | 9.47 | -5.23 | -2.5687
10628 | R-514A | 63.3 | 9.49 | -5.21 | -2.5589
10629 | R-514A | 63.4 | 9.51 | -5.19 | -2.5491
10630 | R-514A | 63.5 | 9.53 | -5.17 | -2.5393
10631 | R-514A | 63.6 | 9.55 | -5.15 | -2.5294
10632 | R-514A | 63.7 | 9.57 | -5.13 | -2.5196
10633 | R-514A | 63.8 | 9.59 | -5.11 | -2.5098
10634 | R-514A | 63.9 | 9.62 | -5.08 | -2.4951
10635 | R-514A | 64 | 9.64 | -5.06 | -2.4852
10636 | R-514A | 64.1 | 9.66 | -5.04 | -2.4754
10637 | R-514A | 64.2 | 9.68 | -5.02 | -2.4656
10638 | R-514A | 64.3 | 9.7 | -5 | -2.4558
10639 | R-514A | 64.4 | 9.72 | -4.98 | -2.4459
10640 | R-514A | 64.5 | 9.75 | -4.95 | -2.4312
10641 | R-514A | 64.6 | 9.77 | -4.93 | -2.4214
10642 | R-514A | 64.7 | 9.79 | -4.91 | -2.4116
10643 | R-514A | 64.8 | 9.81 | -4.89 | -2.4017
10644 | R-514A | 64.9 | 9.83 | -4.87 | -2.3919
10645 | R-514A | 65 | 9.85 | -4.85 | -2.3821
10646 | R-514A | 65.1 | 9.88 | -4.82 | -2.3674
10647 | R-514A | 65.2 | 9.9 | -4.8 | -2.3575
10648 | R-514A | 65.3 | 9.92 | -4.78 | -2.3477
10649 | R-514A | 65.4 | 9.94 | -4.76 | -2.3379
10650 | R-514A | 65.5 | 9.96 | -4.74 | -2.3281
10651 | R-514A | 65.6 | 9.99 | -4.71 | -2.3133
10652 | R-514A | 65.7 | 10.01 | -4.69 | -2.3035
10653 | R-514A | 65.8 | 10.03 | -4.67 | -2.2937
10654 | R-514A | 65.9 | 10.05 | -4.65 | -2.2839
10655 | R-514A | 66 | 10.07 | -4.63 | -2.274
10656 | R-514A | 66.1 | 10.1 | -4.6 | -2.2593
10657 | R-514A | 66.2 | 10.12 | -4.58 | -2.2495
10658 | R-514A | 66.3 | 10.14 | -4.56 | -2.2397
10659 | R-514A | 66.4 | 10.16 | -4.54 | -2.2298
10660 | R-514A | 66.5 | 10.18 | -4.52 | -2.22
10661 | R-514A | 66.6 | 10.21 | -4.49 | -2.2053
10662 | R-514A | 66.7 | 10.23 | -4.47 | -2.1955
10663 | R-514A | 66.8 | 10.25 | -4.45 | -2.1856
10664 | R-514A | 66.9 | 10.27 | -4.43 | -2.1758
10665 | R-514A | 67 | 10.3 | -4.4 | -2.1611
10666 | R-514A | 67.1 | 10.32 | -4.38 | -2.1513
10667 | R-514A | 67.2 | 10.34 | -4.36 | -2.1414
10668 | R-514A | 67.3 | 10.37 | -4.33 | -2.1267
10669 | R-514A | 67.4 | 10.39 | -4.31 | -2.1169
10670 | R-514A | 67.5 | 10.41 | -4.29 | -2.1071
10671 | R-514A | 67.6 | 10.43 | -4.27 | -2.0972
10672 | R-514A | 67.7 | 10.46 | -4.24 | -2.0825
10673 | R-514A | 67.8 | 10.48 | -4.22 | -2.0727
10674 | R-514A | 67.9 | 10.5 | -4.2 | -2.0629
10675 | R-514A | 68 | 10.52 | -4.18 | -2.053
10676 | R-514A | 68.1 | 10.55 | -4.15 | -2.0383
10677 | R-514A | 68.2 | 10.57 | -4.13 | -2.0285
10678 | R-514A | 68.3 | 10.59 | -4.11 | -2.0186
10679 | R-514A | 68.4 | 10.62 | -4.08 | -2.0039
10680 | R-514A | 68.5 | 10.64 | -4.06 | -1.9941
10681 | R-514A | 68.6 | 10.66 | -4.04 | -1.9843
10682 | R-514A | 68.7 | 10.69 | -4.01 | -1.9695
10683 | R-514A | 68.8 | 10.71 | -3.99 | -1.9597
10684 | R-514A | 68.9 | 10.73 | -3.97 | -1.9499
10685 | R-514A | 69 | 10.76 | -3.94 | -1.9351
10686 | R-514A | 69.1 | 10.78 | -3.92 | -1.9253
10687 | R-514A | 69.2 | 10.8 | -3.9 | -1.9155
10688 | R-514A | 69.3 | 10.83 | -3.87 | -1.9008
10689 | R-514A | 69.4 | 10.85 | -3.85 | -1.8909
10690 | R-514A | 69.5 | 10.87 | -3.83 | -1.8811
10691 | R-514A | 69.6 | 10.9 | -3.8 | -1.8664
10692 | R-514A | 69.7 | 10.92 | -3.78 | -1.8566
10693 | R-514A | 69.8 | 10.94 | -3.76 | -1.8467
10694 | R-514A | 69.9 | 10.97 | -3.73 | -1.832
10695 | R-514A | 70 | 10.99 | -3.71 | -1.8222
10696 | R-514A | 70.1 | 11.02 | -3.68 | -1.8075
10697 | R-514A | 70.2 | 11.04 | -3.66 | -1.7976
10698 | R-514A | 70.3 | 11.06 | -3.64 | -1.7878
10699 | R-514A | 70.4 | 11.09 | -3.61 | -1.7731
10700 | R-514A | 70.5 | 11.11 | -3.59 | -1.7632
10701 | R-514A | 70.6 | 11.14 | -3.56 | -1.7485
10702 | R-514A | 70.7 | 11.16 | -3.54 | -1.7387
10703 | R-514A | 70.8 | 11.18 | -3.52 | -1.7289
10704 | R-514A | 70.9 | 11.21 | -3.49 | -1.7141
10705 | R-514A | 71 | 11.23 | -3.47 | -1.7043
10706 | R-514A | 71.1 | 11.26 | -3.44 | -1.6896
10707 | R-514A | 71.2 | 11.28 | -3.42 | -1.6798
10708 | R-514A | 71.3 | 11.31 | -3.39 | -1.665
10709 | R-514A | 71.4 | 11.33 | -3.37 | -1.6552
10710 | R-514A | 71.5 | 11.35 | -3.35 | -1.6454
10711 | R-514A | 71.6 | 11.38 | -3.32 | -1.6306
10712 | R-514A | 71.7 | 11.4 | -3.3 | -1.6208
10713 | R-514A | 71.8 | 11.43 | -3.27 | -1.6061
10714 | R-514A | 71.9 | 11.45 | -3.25 | -1.5962
10715 | R-514A | 72 | 11.48 | -3.22 | -1.5815
10716 | R-514A | 72.1 | 11.5 | -3.2 | -1.5717
10717 | R-514A | 72.2 | 11.53 | -3.17 | -1.557
10718 | R-514A | 72.3 | 11.55 | -3.15 | -1.5471
10719 | R-514A | 72.4 | 11.58 | -3.12 | -1.5324
10720 | R-514A | 72.5 | 11.6 | -3.1 | -1.5226
10721 | R-514A | 72.6 | 11.62 | -3.08 | -1.5128
10722 | R-514A | 72.7 | 11.65 | -3.05 | -1.498
10723 | R-514A | 72.8 | 11.67 | -3.03 | -1.4882
10724 | R-514A | 72.9 | 11.7 | -3 | -1.4735
10725 | R-514A | 73 | 11.72 | -2.98 | -1.4636
10726 | R-514A | 73.1 | 11.75 | -2.95 | -1.4489
10727 | R-514A | 73.2 | 11.77 | -2.93 | -1.4391
10728 | R-514A | 73.3 | 11.8 | -2.9 | -1.4244
10729 | R-514A | 73.4 | 11.82 | -2.88 | -1.4145
10730 | R-514A | 73.5 | 11.85 | -2.85 | -1.3998
10731 | R-514A | 73.6 | 11.88 | -2.82 | -1.3851
10732 | R-514A | 73.7 | 11.9 | -2.8 | -1.3752
10733 | R-514A | 73.8 | 11.93 | -2.77 | -1.3605
10734 | R-514A | 73.9 | 11.95 | -2.75 | -1.3507
10735 | R-514A | 74 | 11.98 | -2.72 | -1.3359
10736 | R-514A | 74.1 | 12 | -2.7 | -1.3261
10737 | R-514A | 74.2 | 12.03 | -2.67 | -1.3114
10738 | R-514A | 74.3 | 12.05 | -2.65 | -1.3016
10739 | R-514A | 74.4 | 12.08 | -2.62 | -1.2868
10740 | R-514A | 74.5 | 12.1 | -2.6 | -1.277
10741 | R-514A | 74.6 | 12.13 | -2.57 | -1.2623
10742 | R-514A | 74.7 | 12.16 | -2.54 | -1.2475
10743 | R-514A | 74.8 | 12.18 | -2.52 | -1.2377
10744 | R-514A | 74.9 | 12.21 | -2.49 | -1.223
10745 | R-514A | 75 | 12.23 | -2.47 | -1.2131
10746 | R-514A | 75.1 | 12.26 | -2.44 | -1.1984
10747 | R-514A | 75.2 | 12.29 | -2.41 | -1.1837
10748 | R-514A | 75.3 | 12.31 | -2.39 | -1.1739
10749 | R-514A | 75.4 | 12.34 | -2.36 | -1.1591
10750 | R-514A | 75.5 | 12.36 | -2.34 | -1.1493
10751 | R-514A | 75.6 | 12.39 | -2.31 | -1.1346
10752 | R-514A | 75.7 | 12.42 | -2.28 | -1.1198
10753 | R-514A | 75.8 | 12.44 | -2.26 | -1.11
10754 | R-514A | 75.9 | 12.47 | -2.23 | -1.0953
10755 | R-514A | 76 | 12.49 | -2.21 | -1.0855
10756 | R-514A | 76.1 | 12.52 | -2.18 | -1.0707
10757 | R-514A | 76.2 | 12.55 | -2.15 | -1.056
10758 | R-514A | 76.3 | 12.57 | -2.13 | -1.0462
10759 | R-514A | 76.4 | 12.6 | -2.1 | -1.0314
10760 | R-514A | 76.5 | 12.63 | -2.07 | -1.0167
10761 | R-514A | 76.6 | 12.65 | -2.05 | -1.0069
10762 | R-514A | 76.7 | 12.68 | -2.02 | -0.99213
10763 | R-514A | 76.8 | 12.71 | -1.99 | -0.9774
10764 | R-514A | 76.9 | 12.73 | -1.97 | -0.96757
10765 | R-514A | 77 | 12.76 | -1.94 | -0.95284
10766 | R-514A | 77.1 | 12.79 | -1.91 | -0.9381
10767 | R-514A | 77.2 | 12.81 | -1.89 | -0.92828
10768 | R-514A | 77.3 | 12.84 | -1.86 | -0.91355
10769 | R-514A | 77.4 | 12.87 | -1.83 | -0.89881
10770 | R-514A | 77.5 | 12.89 | -1.81 | -0.88899
10771 | R-514A | 77.6 | 12.92 | -1.78 | -0.87425
10772 | R-514A | 77.7 | 12.95 | -1.75 | -0.85952
10773 | R-514A | 77.8 | 12.98 | -1.72 | -0.84479
10774 | R-514A | 77.9 | 13 | -1.7 | -0.83496
10775 | R-514A | 78 | 13.03 | -1.67 | -0.82023
10776 | R-514A | 78.1 | 13.06 | -1.64 | -0.80549
10777 | R-514A | 78.2 | 13.08 | -1.62 | -0.79567
10778 | R-514A | 78.3 | 13.11 | -1.59 | -0.78094
10779 | R-514A | 78.4 | 13.14 | -1.56 | -0.7662
10780 | R-514A | 78.5 | 13.17 | -1.53 | -0.75147
10781 | R-514A | 78.6 | 13.19 | -1.51 | -0.74164
10782 | R-514A | 78.7 | 13.22 | -1.48 | -0.72691
10783 | R-514A | 78.8 | 13.25 | -1.45 | -0.71217
10784 | R-514A | 78.9 | 13.28 | -1.42 | -0.69744
10785 | R-514A | 79 | 13.3 | -1.4 | -0.68762
10786 | R-514A | 79.1 | 13.33 | -1.37 | -0.67288
10787 | R-514A | 79.2 | 13.36 | -1.34 | -0.65815
10788 | R-514A | 79.3 | 13.39 | -1.31 | -0.64341
10789 | R-514A | 79.4 | 13.41 | -1.29 | -0.63359
10790 | R-514A | 79.5 | 13.44 | -1.26 | -0.61885
10791 | R-514A | 79.6 | 13.47 | -1.23 | -0.60412
10792 | R-514A | 79.7 | 13.5 | -1.2 | -0.58939
10793 | R-514A | 79.8 | 13.53 | -1.17 | -0.57465
10794 | R-514A | 79.9 | 13.55 | -1.15 | -0.56483
10795 | R-514A | 80 | 13.58 | -1.12 | -0.55009
10796 | R-514A | 80.1 | 13.61 | -1.09 | -0.53536
10797 | R-514A | 80.2 | 13.64 | -1.06 | -0.52062
10798 | R-514A | 80.3 | 13.67 | -1.03 | -0.50589
10799 | R-514A | 80.4 | 13.7 | -1 | -0.49115
10800 | R-514A | 80.5 | 13.72 | -0.98 | -0.48133
10801 | R-514A | 80.6 | 13.75 | -0.95 | -0.4666
10802 | R-514A | 80.7 | 13.78 | -0.92 | -0.45186
10803 | R-514A | 80.8 | 13.81 | -0.89 | -0.43713
10804 | R-514A | 80.9 | 13.84 | -0.86 | -0.42239
10805 | R-514A | 81 | 13.87 | -0.83 | -0.40766
10806 | R-514A | 81.1 | 13.89 | -0.81 | -0.39783
10807 | R-514A | 81.2 | 13.92 | -0.78 | -0.3831
10808 | R-514A | 81.3 | 13.95 | -0.75 | -0.36837
10809 | R-514A | 81.4 | 13.98 | -0.72 | -0.35363
10810 | R-514A | 81.5 | 14.01 | -0.69 | -0.3389
10811 | R-514A | 81.6 | 14.04 | -0.66 | -0.32416
10812 | R-514A | 81.7 | 14.07 | -0.63 | -0.30943
10813 | R-514A | 81.8 | 14.1 | -0.6 | -0.29469
10814 | R-514A | 81.9 | 14.12 | -0.58 | -0.28487
10815 | R-514A | 82 | 14.15 | -0.55 | -0.27013
10816 | R-514A | 82.1 | 14.18 | -0.52 | -0.2554
10817 | R-514A | 82.2 | 14.21 | -0.49 | -0.24067
10818 | R-514A | 82.3 | 14.24 | -0.46 | -0.22593
10819 | R-514A | 82.4 | 14.27 | -0.43 | -0.2112
10820 | R-514A | 82.5 | 14.3 | -0.4 | -0.19646
10821 | R-514A | 82.6 | 14.33 | -0.37 | -0.18173
10822 | R-514A | 82.7 | 14.36 | -0.34 | -0.16699
10823 | R-514A | 82.8 | 14.39 | -0.31 | -0.15226
10824 | R-514A | 82.9 | 14.42 | -0.28 | -0.13752
10825 | R-514A | 83 | 14.45 | -0.25 | -0.12279
10826 | R-514A | 83.1 | 14.48 | -0.22 | -0.10805
10827 | R-514A | 83.2 | 14.51 | -0.19 | -0.09332
10828 | R-514A | 83.3 | 14.54 | -0.16 | -0.07858
10829 | R-514A | 83.4 | 14.57 | -0.13 | -0.06385
10830 | R-514A | 83.5 | 14.6 | -0.1 | -0.04912
10831 | R-514A | 83.6 | 14.62 | -0.08 | -0.03929
10832 | R-514A | 83.7 | 14.65 | -0.05 | -0.02456
10833 | R-514A | 83.8 | 14.68 | -0.02 | -0.00982
10834 | R-514A | 83.9 | 14.71 | 0.01 | 0.00491
10835 | R-514A | 84 | 14.74 | 0.04 | 0.01965
10836 | R-514A | 84.1 | 14.77 | 0.07 | 0.03438
10837 | R-514A | 84.2 | 14.8 | 0.1 | 0.04912
10838 | R-514A | 84.3 | 14.83 | 0.13 | 0.06385
10839 | R-514A | 84.4 | 14.86 | 0.16 | 0.07858
10840 | R-514A | 84.5 | 14.9 | 0.2 | 0.09823
10841 | R-514A | 84.6 | 14.93 | 0.23 | 0.11297
10842 | R-514A | 84.7 | 14.96 | 0.26 | 0.1277
10843 | R-514A | 84.8 | 14.99 | 0.29 | 0.14243
10844 | R-514A | 84.9 | 15.02 | 0.32 | 0.15717
10845 | R-514A | 85 | 15.05 | 0.35 | 0.1719
10846 | R-514A | 85.1 | 15.08 | 0.38 | 0.18664
10847 | R-514A | 85.2 | 15.11 | 0.41 | 0.20137
10848 | R-514A | 85.3 | 15.14 | 0.44 | 0.21611
10849 | R-514A | 85.4 | 15.17 | 0.47 | 0.23084
10850 | R-514A | 85.5 | 15.2 | 0.5 | 0.24558
10851 | R-514A | 85.6 | 15.23 | 0.53 | 0.26031
10852 | R-514A | 85.7 | 15.26 | 0.56 | 0.27505
10853 | R-514A | 85.8 | 15.29 | 0.59 | 0.28978
10854 | R-514A | 85.9 | 15.32 | 0.62 | 0.30452
10855 | R-514A | 86 | 15.35 | 0.65 | 0.31925
10856 | R-514A | 86.1 | 15.38 | 0.68 | 0.33398
10857 | R-514A | 86.2 | 15.42 | 0.72 | 0.35363
10858 | R-514A | 86.3 | 15.45 | 0.75 | 0.36837
10859 | R-514A | 86.4 | 15.48 | 0.78 | 0.3831
10860 | R-514A | 86.5 | 15.51 | 0.81 | 0.39783
10861 | R-514A | 86.6 | 15.54 | 0.84 | 0.41257
10862 | R-514A | 86.7 | 15.57 | 0.87 | 0.4273
10863 | R-514A | 86.8 | 15.6 | 0.9 | 0.44204
10864 | R-514A | 86.9 | 15.63 | 0.93 | 0.45677
10865 | R-514A | 87 | 15.67 | 0.97 | 0.47642
10866 | R-514A | 87.1 | 15.7 | 1 | 0.49115
10867 | R-514A | 87.2 | 15.73 | 1.03 | 0.50589
10868 | R-514A | 87.3 | 15.76 | 1.06 | 0.52062
10869 | R-514A | 87.4 | 15.79 | 1.09 | 0.53536
10870 | R-514A | 87.5 | 15.82 | 1.12 | 0.55009
10871 | R-514A | 87.6 | 15.86 | 1.16 | 0.56974
10872 | R-514A | 87.7 | 15.89 | 1.19 | 0.58447
10873 | R-514A | 87.8 | 15.92 | 1.22 | 0.59921
10874 | R-514A | 87.9 | 15.95 | 1.25 | 0.61394
10875 | R-514A | 88 | 15.98 | 1.28 | 0.62868
10876 | R-514A | 88.1 | 16.01 | 1.31 | 0.64341
10877 | R-514A | 88.2 | 16.05 | 1.35 | 0.66306
10878 | R-514A | 88.3 | 16.08 | 1.38 | 0.67779
10879 | R-514A | 88.4 | 16.11 | 1.41 | 0.69253
10880 | R-514A | 88.5 | 16.14 | 1.44 | 0.70726
10881 | R-514A | 88.6 | 16.18 | 1.48 | 0.72691
10882 | R-514A | 88.7 | 16.21 | 1.51 | 0.74164
10883 | R-514A | 88.8 | 16.24 | 1.54 | 0.75638
10884 | R-514A | 88.9 | 16.27 | 1.57 | 0.77111
10885 | R-514A | 89 | 16.3 | 1.6 | 0.78585
10886 | R-514A | 89.1 | 16.34 | 1.64 | 0.80549
10887 | R-514A | 89.2 | 16.37 | 1.67 | 0.82023
10888 | R-514A | 89.3 | 16.4 | 1.7 | 0.83496
10889 | R-514A | 89.4 | 16.44 | 1.74 | 0.85461
10890 | R-514A | 89.5 | 16.47 | 1.77 | 0.86934
10891 | R-514A | 89.6 | 16.5 | 1.8 | 0.88408
10892 | R-514A | 89.7 | 16.53 | 1.83 | 0.89881
10893 | R-514A | 89.8 | 16.57 | 1.87 | 0.91846
10894 | R-514A | 89.9 | 16.6 | 1.9 | 0.93319
10895 | R-514A | 90 | 16.63 | 1.93 | 0.94793
10896 | R-514A | 90.1 | 16.66 | 1.96 | 0.96266
10897 | R-514A | 90.2 | 16.7 | 2 | 0.98231
10898 | R-514A | 90.3 | 16.73 | 2.03 | 0.99704
10899 | R-514A | 90.4 | 16.76 | 2.06 | 1.0118
10900 | R-514A | 90.5 | 16.8 | 2.1 | 1.0314
10901 | R-514A | 90.6 | 16.83 | 2.13 | 1.0462
10902 | R-514A | 90.7 | 16.86 | 2.16 | 1.0609
10903 | R-514A | 90.8 | 16.9 | 2.2 | 1.0805
10904 | R-514A | 90.9 | 16.93 | 2.23 | 1.0953
10905 | R-514A | 91 | 16.96 | 2.26 | 1.11
10906 | R-514A | 91.1 | 17 | 2.3 | 1.1297
10907 | R-514A | 91.2 | 17.03 | 2.33 | 1.1444
10908 | R-514A | 91.3 | 17.07 | 2.37 | 1.164
10909 | R-514A | 91.4 | 17.1 | 2.4 | 1.1788
10910 | R-514A | 91.5 | 17.13 | 2.43 | 1.1935
10911 | R-514A | 91.6 | 17.17 | 2.47 | 1.2131
10912 | R-514A | 91.7 | 17.2 | 2.5 | 1.2279
10913 | R-514A | 91.8 | 17.23 | 2.53 | 1.2426
10914 | R-514A | 91.9 | 17.27 | 2.57 | 1.2623
10915 | R-514A | 92 | 17.3 | 2.6 | 1.277
10916 | R-514A | 92.1 | 17.34 | 2.64 | 1.2967
10917 | R-514A | 92.2 | 17.37 | 2.67 | 1.3114
10918 | R-514A | 92.3 | 17.4 | 2.7 | 1.3261
10919 | R-514A | 92.4 | 17.44 | 2.74 | 1.3458
10920 | R-514A | 92.5 | 17.47 | 2.77 | 1.3605
10921 | R-514A | 92.6 | 17.51 | 2.81 | 1.3801
10922 | R-514A | 92.7 | 17.54 | 2.84 | 1.3949
10923 | R-514A | 92.8 | 17.58 | 2.88 | 1.4145
10924 | R-514A | 92.9 | 17.61 | 2.91 | 1.4293
10925 | R-514A | 93 | 17.64 | 2.94 | 1.444
10926 | R-514A | 93.1 | 17.68 | 2.98 | 1.4636
10927 | R-514A | 93.2 | 17.71 | 3.01 | 1.4784
10928 | R-514A | 93.3 | 17.75 | 3.05 | 1.498
10929 | R-514A | 93.4 | 17.78 | 3.08 | 1.5128
10930 | R-514A | 93.5 | 17.82 | 3.12 | 1.5324
10931 | R-514A | 93.6 | 17.85 | 3.15 | 1.5471
10932 | R-514A | 93.7 | 17.89 | 3.19 | 1.5668
10933 | R-514A | 93.8 | 17.92 | 3.22 | 1.5815
10934 | R-514A | 93.9 | 17.96 | 3.26 | 1.6012
10935 | R-514A | 94 | 17.99 | 3.29 | 1.6159
10936 | R-514A | 94.1 | 18.03 | 3.33 | 1.6355
10937 | R-514A | 94.2 | 18.06 | 3.36 | 1.6503
10938 | R-514A | 94.3 | 18.1 | 3.4 | 1.6699
10939 | R-514A | 94.4 | 18.13 | 3.43 | 1.6847
10940 | R-514A | 94.5 | 18.17 | 3.47 | 1.7043
10941 | R-514A | 94.6 | 18.2 | 3.5 | 1.719
10942 | R-514A | 94.7 | 18.24 | 3.54 | 1.7387
10943 | R-514A | 94.8 | 18.27 | 3.57 | 1.7534
10944 | R-514A | 94.9 | 18.31 | 3.61 | 1.7731
10945 | R-514A | 95 | 18.35 | 3.65 | 1.7927
10946 | R-514A | 95.1 | 18.38 | 3.68 | 1.8075
10947 | R-514A | 95.2 | 18.42 | 3.72 | 1.8271
10948 | R-514A | 95.3 | 18.45 | 3.75 | 1.8418
10949 | R-514A | 95.4 | 18.49 | 3.79 | 1.8615
10950 | R-514A | 95.5 | 18.52 | 3.82 | 1.8762
10951 | R-514A | 95.6 | 18.56 | 3.86 | 1.8959
10952 | R-514A | 95.7 | 18.6 | 3.9 | 1.9155
10953 | R-514A | 95.8 | 18.63 | 3.93 | 1.9302
10954 | R-514A | 95.9 | 18.67 | 3.97 | 1.9499
10955 | R-514A | 96 | 18.7 | 4 | 1.9646
10956 | R-514A | 96.1 | 18.74 | 4.04 | 1.9843
10957 | R-514A | 96.2 | 18.78 | 4.08 | 2.0039
10958 | R-514A | 96.3 | 18.81 | 4.11 | 2.0186
10959 | R-514A | 96.4 | 18.85 | 4.15 | 2.0383
10960 | R-514A | 96.5 | 18.89 | 4.19 | 2.0579
10961 | R-514A | 96.6 | 18.92 | 4.22 | 2.0727
10962 | R-514A | 96.7 | 18.96 | 4.26 | 2.0923
10963 | R-514A | 96.8 | 19 | 4.3 | 2.112
10964 | R-514A | 96.9 | 19.03 | 4.33 | 2.1267
10965 | R-514A | 97 | 19.07 | 4.37 | 2.1463
10966 | R-514A | 97.1 | 19.11 | 4.41 | 2.166
10967 | R-514A | 97.2 | 19.14 | 4.44 | 2.1807
10968 | R-514A | 97.3 | 19.18 | 4.48 | 2.2004
10969 | R-514A | 97.4 | 19.22 | 4.52 | 2.22
10970 | R-514A | 97.5 | 19.25 | 4.55 | 2.2348
10971 | R-514A | 97.6 | 19.29 | 4.59 | 2.2544
10972 | R-514A | 97.7 | 19.33 | 4.63 | 2.274
10973 | R-514A | 97.8 | 19.36 | 4.66 | 2.2888
10974 | R-514A | 97.9 | 19.4 | 4.7 | 2.3084
10975 | R-514A | 98 | 19.44 | 4.74 | 2.3281
10976 | R-514A | 98.1 | 19.48 | 4.78 | 2.3477
10977 | R-514A | 98.2 | 19.51 | 4.81 | 2.3624
10978 | R-514A | 98.3 | 19.55 | 4.85 | 2.3821
10979 | R-514A | 98.4 | 19.59 | 4.89 | 2.4017
10980 | R-514A | 98.5 | 19.63 | 4.93 | 2.4214
10981 | R-514A | 98.6 | 19.66 | 4.96 | 2.4361
10982 | R-514A | 98.7 | 19.7 | 5 | 2.4558
10983 | R-514A | 98.8 | 19.74 | 5.04 | 2.4754
10984 | R-514A | 98.9 | 19.78 | 5.08 | 2.4951
10985 | R-514A | 99 | 19.81 | 5.11 | 2.5098
10986 | R-514A | 99.1 | 19.85 | 5.15 | 2.5294
10987 | R-514A | 99.2 | 19.89 | 5.19 | 2.5491
10988 | R-514A | 99.3 | 19.93 | 5.23 | 2.5687
10989 | R-514A | 99.4 | 19.97 | 5.27 | 2.5884
10990 | R-514A | 99.5 | 20 | 5.3 | 2.6031
10991 | R-514A | 99.6 | 20.04 | 5.34 | 2.6228
10992 | R-514A | 99.7 | 20.08 | 5.38 | 2.6424
10993 | R-514A | 99.8 | 20.12 | 5.42 | 2.6621
10994 | R-514A | 99.9 | 20.16 | 5.46 | 2.6817
10995 | R-514A | 100 | 20.19 | 5.49 | 2.6964
10996 | R-514A | 100.1 | 20.23 | 5.53 | 2.7161
10997 | R-514A | 100.2 | 20.27 | 5.57 | 2.7357
10998 | R-514A | 100.3 | 20.31 | 5.61 | 2.7554
10999 | R-514A | 100.4 | 20.35 | 5.65 | 2.775
11000 | R-514A | 100.5 | 20.39 | 5.69 | 2.7947
11001 | R-514A | 100.6 | 20.43 | 5.73 | 2.8143
11002 | R-514A | 100.7 | 20.46 | 5.76 | 2.8291
11003 | R-514A | 100.8 | 20.5 | 5.8 | 2.8487
11004 | R-514A | 100.9 | 20.54 | 5.84 | 2.8683
11005 | R-514A | 101 | 20.58 | 5.88 | 2.888
11006 | R-514A | 101.1 | 20.62 | 5.92 | 2.9076
11007 | R-514A | 101.2 | 20.66 | 5.96 | 2.9273
11008 | R-514A | 101.3 | 20.7 | 6 | 2.9469
11009 | R-514A | 101.4 | 20.74 | 6.04 | 2.9666
11010 | R-514A | 101.5 | 20.78 | 6.08 | 2.9862
11011 | R-514A | 101.6 | 20.82 | 6.12 | 3.0059
11012 | R-514A | 101.7 | 20.86 | 6.16 | 3.0255
11013 | R-514A | 101.8 | 20.89 | 6.19 | 3.0402
11014 | R-514A | 101.9 | 20.93 | 6.23 | 3.0599
11015 | R-514A | 102 | 20.97 | 6.27 | 3.0795
11016 | R-514A | 102.1 | 21.01 | 6.31 | 3.0992
11017 | R-514A | 102.2 | 21.05 | 6.35 | 3.1188
11018 | R-514A | 102.3 | 21.09 | 6.39 | 3.1385
11019 | R-514A | 102.4 | 21.13 | 6.43 | 3.1581
11020 | R-514A | 102.5 | 21.17 | 6.47 | 3.1778
11021 | R-514A | 102.6 | 21.21 | 6.51 | 3.1974
11022 | R-514A | 102.7 | 21.25 | 6.55 | 3.2171
11023 | R-514A | 102.8 | 21.29 | 6.59 | 3.2367
11024 | R-514A | 102.9 | 21.33 | 6.63 | 3.2563
11025 | R-514A | 103 | 21.37 | 6.67 | 3.276
11026 | R-514A | 103.1 | 21.41 | 6.71 | 3.2957
11027 | R-514A | 103.2 | 21.45 | 6.75 | 3.3153
11028 | R-514A | 103.3 | 21.49 | 6.79 | 3.3349
11029 | R-514A | 103.4 | 21.53 | 6.83 | 3.3546
11030 | R-514A | 103.5 | 21.57 | 6.87 | 3.3742
11031 | R-514A | 103.6 | 21.61 | 6.91 | 3.3939
11032 | R-514A | 103.7 | 21.65 | 6.95 | 3.4135
11033 | R-514A | 103.8 | 21.69 | 6.99 | 3.4332
11034 | R-514A | 103.9 | 21.73 | 7.03 | 3.4528
11035 | R-514A | 104 | 21.78 | 7.08 | 3.4774
11036 | R-514A | 104.1 | 21.82 | 7.12 | 3.497
11037 | R-514A | 104.2 | 21.86 | 7.16 | 3.5167
11038 | R-514A | 104.3 | 21.9 | 7.2 | 3.5363
11039 | R-514A | 104.4 | 21.94 | 7.24 | 3.556
11040 | R-514A | 104.5 | 21.98 | 7.28 | 3.5756
11041 | R-514A | 104.6 | 22.02 | 7.32 | 3.5953
11042 | R-514A | 104.7 | 22.06 | 7.36 | 3.6149
11043 | R-514A | 104.8 | 22.1 | 7.4 | 3.6345
11044 | R-514A | 104.9 | 22.14 | 7.44 | 3.6542
11045 | R-514A | 105 | 22.19 | 7.49 | 3.6787
11046 | R-514A | 105.1 | 22.23 | 7.53 | 3.6984
11047 | R-514A | 105.2 | 22.27 | 7.57 | 3.718
11048 | R-514A | 105.3 | 22.31 | 7.61 | 3.7377
11049 | R-514A | 105.4 | 22.35 | 7.65 | 3.7573
11050 | R-514A | 105.5 | 22.39 | 7.69 | 3.777
11051 | R-514A | 105.6 | 22.43 | 7.73 | 3.7966
11052 | R-514A | 105.7 | 22.48 | 7.78 | 3.8212
11053 | R-514A | 105.8 | 22.52 | 7.82 | 3.8408
11054 | R-514A | 105.9 | 22.56 | 7.86 | 3.8605
11055 | R-514A | 106 | 22.6 | 7.9 | 3.8801
11056 | R-514A | 106.1 | 22.64 | 7.94 | 3.8998
11057 | R-514A | 106.2 | 22.69 | 7.99 | 3.9243
11058 | R-514A | 106.3 | 22.73 | 8.03 | 3.944
11059 | R-514A | 106.4 | 22.77 | 8.07 | 3.9636
11060 | R-514A | 106.5 | 22.81 | 8.11 | 3.9833
11061 | R-514A | 106.6 | 22.85 | 8.15 | 4.0029
11062 | R-514A | 106.7 | 22.9 | 8.2 | 4.0275
11063 | R-514A | 106.8 | 22.94 | 8.24 | 4.0471
11064 | R-514A | 106.9 | 22.98 | 8.28 | 4.0668
11065 | R-514A | 107 | 23.02 | 8.32 | 4.0864
11066 | R-514A | 107.1 | 23.07 | 8.37 | 4.111
11067 | R-514A | 107.2 | 23.11 | 8.41 | 4.1306
11068 | R-514A | 107.3 | 23.15 | 8.45 | 4.1502
11069 | R-514A | 107.4 | 23.19 | 8.49 | 4.1699
11070 | R-514A | 107.5 | 23.24 | 8.54 | 4.1945
11071 | R-514A | 107.6 | 23.28 | 8.58 | 4.2141
11072 | R-514A | 107.7 | 23.32 | 8.62 | 4.2337
11073 | R-514A | 107.8 | 23.37 | 8.67 | 4.2583
11074 | R-514A | 107.9 | 23.41 | 8.71 | 4.2779
11075 | R-514A | 108 | 23.45 | 8.75 | 4.2976
11076 | R-514A | 108.1 | 23.49 | 8.79 | 4.3172
11077 | R-514A | 108.2 | 23.54 | 8.84 | 4.3418
11078 | R-514A | 108.3 | 23.58 | 8.88 | 4.3614
11079 | R-514A | 108.4 | 23.62 | 8.92 | 4.3811
11080 | R-514A | 108.5 | 23.67 | 8.97 | 4.4056
11081 | R-514A | 108.6 | 23.71 | 9.01 | 4.4253
11082 | R-514A | 108.7 | 23.76 | 9.06 | 4.4499
11083 | R-514A | 108.8 | 23.8 | 9.1 | 4.4695
11084 | R-514A | 108.9 | 23.84 | 9.14 | 4.4892
11085 | R-514A | 109 | 23.89 | 9.19 | 4.5137
11086 | R-514A | 109.1 | 23.93 | 9.23 | 4.5334
11087 | R-514A | 109.2 | 23.97 | 9.27 | 4.553
11088 | R-514A | 109.3 | 24.02 | 9.32 | 4.5776
11089 | R-514A | 109.4 | 24.06 | 9.36 | 4.5972
11090 | R-514A | 109.5 | 24.11 | 9.41 | 4.6218
11091 | R-514A | 109.6 | 24.15 | 9.45 | 4.6414
11092 | R-514A | 109.7 | 24.19 | 9.49 | 4.6611
11093 | R-514A | 109.8 | 24.24 | 9.54 | 4.6856
11094 | R-514A | 109.9 | 24.28 | 9.58 | 4.7053
11095 | R-514A | 110 | 24.33 | 9.63 | 4.7298
11096 | R-514A | 110.1 | 24.37 | 9.67 | 4.7495
11097 | R-514A | 110.2 | 24.42 | 9.72 | 4.774
11098 | R-514A | 110.3 | 24.46 | 9.76 | 4.7937
11099 | R-514A | 110.4 | 24.5 | 9.8 | 4.8133
11100 | R-514A | 110.5 | 24.55 | 9.85 | 4.8379
11101 | R-514A | 110.6 | 24.59 | 9.89 | 4.8575
11102 | R-514A | 110.7 | 24.64 | 9.94 | 4.8821
11103 | R-514A | 110.8 | 24.68 | 9.98 | 4.9017
11104 | R-514A | 110.9 | 24.73 | 10.03 | 4.9263
11105 | R-514A | 111 | 24.77 | 10.07 | 4.9459
11106 | R-514A | 111.1 | 24.82 | 10.12 | 4.9705
11107 | R-514A | 111.2 | 24.86 | 10.16 | 4.9901
11108 | R-514A | 111.3 | 24.91 | 10.21 | 5.0147
11109 | R-514A | 111.4 | 24.95 | 10.25 | 5.0343
11110 | R-514A | 111.5 | 25 | 10.3 | 5.0589
11111 | R-514A | 111.6 | 25.04 | 10.34 | 5.0785
11112 | R-514A | 111.7 | 25.09 | 10.39 | 5.1031
11113 | R-514A | 111.8 | 25.14 | 10.44 | 5.1277
11114 | R-514A | 111.9 | 25.18 | 10.48 | 5.1473
11115 | R-514A | 112 | 25.23 | 10.53 | 5.1719
11116 | R-514A | 112.1 | 25.27 | 10.57 | 5.1915
11117 | R-514A | 112.2 | 25.32 | 10.62 | 5.2161
11118 | R-514A | 112.3 | 25.36 | 10.66 | 5.2357
11119 | R-514A | 112.4 | 25.41 | 10.71 | 5.2603
11120 | R-514A | 112.5 | 25.46 | 10.76 | 5.2848
11121 | R-514A | 112.6 | 25.5 | 10.8 | 5.3045
11122 | R-514A | 112.7 | 25.55 | 10.85 | 5.329
11123 | R-514A | 112.8 | 25.59 | 10.89 | 5.3487
11124 | R-514A | 112.9 | 25.64 | 10.94 | 5.3732
11125 | R-514A | 113 | 25.69 | 10.99 | 5.3978
11126 | R-514A | 113.1 | 25.73 | 11.03 | 5.4174
11127 | R-514A | 113.2 | 25.78 | 11.08 | 5.442
11128 | R-514A | 113.3 | 25.83 | 11.13 | 5.4665
11129 | R-514A | 113.4 | 25.87 | 11.17 | 5.4862
11130 | R-514A | 113.5 | 25.92 | 11.22 | 5.5107
11131 | R-514A | 113.6 | 25.96 | 11.26 | 5.5304
11132 | R-514A | 113.7 | 26.01 | 11.31 | 5.555
11133 | R-514A | 113.8 | 26.06 | 11.36 | 5.5795
11134 | R-514A | 113.9 | 26.1 | 11.4 | 5.5992
11135 | R-514A | 114 | 26.15 | 11.45 | 5.6237
11136 | R-514A | 114.1 | 26.2 | 11.5 | 5.6483
11137 | R-514A | 114.2 | 26.25 | 11.55 | 5.6728
11138 | R-514A | 114.3 | 26.29 | 11.59 | 5.6925
11139 | R-514A | 114.4 | 26.34 | 11.64 | 5.717
11140 | R-514A | 114.5 | 26.39 | 11.69 | 5.7416
11141 | R-514A | 114.6 | 26.43 | 11.73 | 5.7612
11142 | R-514A | 114.7 | 26.48 | 11.78 | 5.7858
11143 | R-514A | 114.8 | 26.53 | 11.83 | 5.8104
11144 | R-514A | 114.9 | 26.58 | 11.88 | 5.8349
11145 | R-514A | 115 | 26.62 | 11.92 | 5.8546
11146 | R-514A | 115.1 | 26.67 | 11.97 | 5.8791
11147 | R-514A | 115.2 | 26.72 | 12.02 | 5.9037
11148 | R-514A | 115.3 | 26.77 | 12.07 | 5.9282
11149 | R-514A | 115.4 | 26.82 | 12.12 | 5.9528
11150 | R-514A | 115.5 | 26.86 | 12.16 | 5.9724
11151 | R-514A | 115.6 | 26.91 | 12.21 | 5.997
11152 | R-514A | 115.7 | 26.96 | 12.26 | 6.0216
11153 | R-514A | 115.8 | 27.01 | 12.31 | 6.0461
11154 | R-514A | 115.9 | 27.06 | 12.36 | 6.0707
11155 | R-514A | 116 | 27.1 | 12.4 | 6.0903
11156 | R-514A | 116.1 | 27.15 | 12.45 | 6.1149
11157 | R-514A | 116.2 | 27.2 | 12.5 | 6.1394
11158 | R-514A | 116.3 | 27.25 | 12.55 | 6.164
11159 | R-514A | 116.4 | 27.3 | 12.6 | 6.1885
11160 | R-514A | 116.5 | 27.35 | 12.65 | 6.2131
11161 | R-514A | 116.6 | 27.39 | 12.69 | 6.2328
11162 | R-514A | 116.7 | 27.44 | 12.74 | 6.2573
11163 | R-514A | 116.8 | 27.49 | 12.79 | 6.2819
11164 | R-514A | 116.9 | 27.54 | 12.84 | 6.3064
11165 | R-514A | 117 | 27.59 | 12.89 | 6.331
11166 | R-514A | 117.1 | 27.64 | 12.94 | 6.3555
11167 | R-514A | 117.2 | 27.69 | 12.99 | 6.3801
11168 | R-514A | 117.3 | 27.74 | 13.04 | 6.4047
11169 | R-514A | 117.4 | 27.79 | 13.09 | 6.4292
11170 | R-514A | 117.5 | 27.83 | 13.13 | 6.4489
11171 | R-514A | 117.6 | 27.88 | 13.18 | 6.4734
11172 | R-514A | 117.7 | 27.93 | 13.23 | 6.498
11173 | R-514A | 117.8 | 27.98 | 13.28 | 6.5225
11174 | R-514A | 117.9 | 28.03 | 13.33 | 6.5471
11175 | R-514A | 118 | 28.08 | 13.38 | 6.5716
11176 | R-514A | 118.1 | 28.13 | 13.43 | 6.5962
11177 | R-514A | 118.2 | 28.18 | 13.48 | 6.6208
11178 | R-514A | 118.3 | 28.23 | 13.53 | 6.6453
11179 | R-514A | 118.4 | 28.28 | 13.58 | 6.6699
11180 | R-514A | 118.5 | 28.33 | 13.63 | 6.6944
11181 | R-514A | 118.6 | 28.38 | 13.68 | 6.719
11182 | R-514A | 118.7 | 28.43 | 13.73 | 6.7435
11183 | R-514A | 118.8 | 28.48 | 13.78 | 6.7681
11184 | R-514A | 118.9 | 28.53 | 13.83 | 6.7927
11185 | R-514A | 119 | 28.58 | 13.88 | 6.8172
11186 | R-514A | 119.1 | 28.63 | 13.93 | 6.8418
11187 | R-514A | 119.2 | 28.68 | 13.98 | 6.8663
11188 | R-514A | 119.3 | 28.73 | 14.03 | 6.8909
11189 | R-514A | 119.4 | 28.78 | 14.08 | 6.9154
11190 | R-514A | 119.5 | 28.83 | 14.13 | 6.94
11191 | R-514A | 119.6 | 28.88 | 14.18 | 6.9646
11192 | R-514A | 119.7 | 28.93 | 14.23 | 6.9891
11193 | R-514A | 119.8 | 28.99 | 14.29 | 7.0186
11194 | R-514A | 119.9 | 29.04 | 14.34 | 7.0431
11195 | R-514A | 120 | 29.09 | 14.39 | 7.0677
11196 | R-514A | 120.1 | 29.14 | 14.44 | 7.0923
11197 | R-514A | 120.2 | 29.19 | 14.49 | 7.1168
11198 | R-514A | 120.3 | 29.24 | 14.54 | 7.1414
11199 | R-514A | 120.4 | 29.29 | 14.59 | 7.1659
11200 | R-514A | 120.5 | 29.34 | 14.64 | 7.1905
11201 | R-514A | 120.6 | 29.39 | 14.69 | 7.2151
11202 | R-514A | 120.7 | 29.45 | 14.75 | 7.2445
11203 | R-514A | 120.8 | 29.5 | 14.8 | 7.2691
11204 | R-514A | 120.9 | 29.55 | 14.85 | 7.2936
11205 | R-514A | 121 | 29.6 | 14.9 | 7.3182
11206 | R-514A | 121.1 | 29.65 | 14.95 | 7.3428
11207 | R-514A | 121.2 | 29.7 | 15 | 7.3673
11208 | R-514A | 121.3 | 29.76 | 15.06 | 7.3968
11209 | R-514A | 121.4 | 29.81 | 15.11 | 7.4213
11210 | R-514A | 121.5 | 29.86 | 15.16 | 7.4459
11211 | R-514A | 121.6 | 29.91 | 15.21 | 7.4705
11212 | R-514A | 121.7 | 29.96 | 15.26 | 7.495
11213 | R-514A | 121.8 | 30.02 | 15.32 | 7.5245
11214 | R-514A | 121.9 | 30.07 | 15.37 | 7.549
11215 | R-514A | 122 | 30.12 | 15.42 | 7.5736
11216 | R-514A | 122.1 | 30.17 | 15.47 | 7.5982
11217 | R-514A | 122.2 | 30.22 | 15.52 | 7.6227
11218 | R-514A | 122.3 | 30.28 | 15.58 | 7.6522
11219 | R-514A | 122.4 | 30.33 | 15.63 | 7.6767
11220 | R-514A | 122.5 | 30.38 | 15.68 | 7.7013
11221 | R-514A | 122.6 | 30.44 | 15.74 | 7.7308
11222 | R-514A | 122.7 | 30.49 | 15.79 | 7.7553
11223 | R-514A | 122.8 | 30.54 | 15.84 | 7.7799
11224 | R-514A | 122.9 | 30.59 | 15.89 | 7.8044
11225 | R-514A | 123 | 30.65 | 15.95 | 7.8339
11226 | R-514A | 123.1 | 30.7 | 16 | 7.8585
11227 | R-514A | 123.2 | 30.75 | 16.05 | 7.883
11228 | R-514A | 123.3 | 30.81 | 16.11 | 7.9125
11229 | R-514A | 123.4 | 30.86 | 16.16 | 7.9371
11230 | R-514A | 123.5 | 30.91 | 16.21 | 7.9616
11231 | R-514A | 123.6 | 30.97 | 16.27 | 7.9911
11232 | R-514A | 123.7 | 31.02 | 16.32 | 8.0156
11233 | R-514A | 123.8 | 31.07 | 16.37 | 8.0402
11234 | R-514A | 123.9 | 31.13 | 16.43 | 8.0697
11235 | R-514A | 124 | 31.18 | 16.48 | 8.0942
11236 | R-514A | 124.1 | 31.23 | 16.53 | 8.1188
11237 | R-514A | 124.2 | 31.29 | 16.59 | 8.1483
11238 | R-514A | 124.3 | 31.34 | 16.64 | 8.1728
11239 | R-514A | 124.4 | 31.4 | 16.7 | 8.2023
11240 | R-514A | 124.5 | 31.45 | 16.75 | 8.2268
11241 | R-514A | 124.6 | 31.51 | 16.81 | 8.2563
11242 | R-514A | 124.7 | 31.56 | 16.86 | 8.2809
11243 | R-514A | 124.8 | 31.61 | 16.91 | 8.3054
11244 | R-514A | 124.9 | 31.67 | 16.97 | 8.3349
11245 | R-514A | 125 | 31.72 | 17.02 | 8.3595
11246 | R-514A | 125.1 | 31.78 | 17.08 | 8.3889
11247 | R-514A | 125.2 | 31.83 | 17.13 | 8.4135
11248 | R-514A | 125.3 | 31.89 | 17.19 | 8.4429
11249 | R-514A | 125.4 | 31.94 | 17.24 | 8.4675
11250 | R-514A | 125.5 | 32 | 17.3 | 8.497
11251 | R-514A | 125.6 | 32.05 | 17.35 | 8.5215
11252 | R-514A | 125.7 | 32.11 | 17.41 | 8.551
11253 | R-514A | 125.8 | 32.16 | 17.46 | 8.5755
11254 | R-514A | 125.9 | 32.22 | 17.52 | 8.605
11255 | R-514A | 126 | 32.27 | 17.57 | 8.6296
11256 | R-514A | 126.1 | 32.33 | 17.63 | 8.6591
11257 | R-514A | 126.2 | 32.38 | 17.68 | 8.6836
11258 | R-514A | 126.3 | 32.44 | 17.74 | 8.7131
11259 | R-514A | 126.4 | 32.49 | 17.79 | 8.7376
11260 | R-514A | 126.5 | 32.55 | 17.85 | 8.7671
11261 | R-514A | 126.6 | 32.6 | 17.9 | 8.7917
11262 | R-514A | 126.7 | 32.66 | 17.96 | 8.8211
11263 | R-514A | 126.8 | 32.71 | 18.01 | 8.8457
11264 | R-514A | 126.9 | 32.77 | 18.07 | 8.8752
11265 | R-514A | 127 | 32.83 | 18.13 | 8.9046
11266 | R-514A | 127.1 | 32.88 | 18.18 | 8.9292
11267 | R-514A | 127.2 | 32.94 | 18.24 | 8.9587
11268 | R-514A | 127.3 | 32.99 | 18.29 | 8.9832
11269 | R-514A | 127.4 | 33.05 | 18.35 | 9.0127
11270 | R-514A | 127.5 | 33.11 | 18.41 | 9.0421
11271 | R-514A | 127.6 | 33.16 | 18.46 | 9.0667
11272 | R-514A | 127.7 | 33.22 | 18.52 | 9.0962
11273 | R-514A | 127.8 | 33.28 | 18.58 | 9.1257
11274 | R-514A | 127.9 | 33.33 | 18.63 | 9.1502
11275 | R-514A | 128 | 33.39 | 18.69 | 9.1797
11276 | R-514A | 128.1 | 33.45 | 18.75 | 9.2091
11277 | R-514A | 128.2 | 33.5 | 18.8 | 9.2337
11278 | R-514A | 128.3 | 33.56 | 18.86 | 9.2632
11279 | R-514A | 128.4 | 33.62 | 18.92 | 9.2926
11280 | R-514A | 128.5 | 33.67 | 18.97 | 9.3172
11281 | R-514A | 128.6 | 33.73 | 19.03 | 9.3467
11282 | R-514A | 128.7 | 33.79 | 19.09 | 9.3761
11283 | R-514A | 128.8 | 33.85 | 19.15 | 9.4056
11284 | R-514A | 128.9 | 33.9 | 19.2 | 9.4302
11285 | R-514A | 129 | 33.96 | 19.26 | 9.4596
11286 | R-514A | 129.1 | 34.02 | 19.32 | 9.4891
11287 | R-514A | 129.2 | 34.08 | 19.38 | 9.5186
11288 | R-514A | 129.3 | 34.13 | 19.43 | 9.5431
11289 | R-514A | 129.4 | 34.19 | 19.49 | 9.5726
11290 | R-514A | 129.5 | 34.25 | 19.55 | 9.6021
11291 | R-514A | 129.6 | 34.31 | 19.61 | 9.6315
11292 | R-514A | 129.7 | 34.36 | 19.66 | 9.6561
11293 | R-514A | 129.8 | 34.42 | 19.72 | 9.6856
11294 | R-514A | 129.9 | 34.48 | 19.78 | 9.715
11295 | R-514A | 130 | 34.54 | 19.84 | 9.7445
11296 | R-514A | 130.1 | 34.6 | 19.9 | 9.774
11297 | R-514A | 130.2 | 34.65 | 19.95 | 9.7985
11298 | R-514A | 130.3 | 34.71 | 20.01 | 9.828
11299 | R-514A | 130.4 | 34.77 | 20.07 | 9.8575
11300 | R-514A | 130.5 | 34.83 | 20.13 | 9.8869
11301 | R-514A | 130.6 | 34.89 | 20.19 | 9.9164
11302 | R-514A | 130.7 | 34.95 | 20.25 | 9.9459
11303 | R-514A | 130.8 | 35.01 | 20.31 | 9.9753
11304 | R-514A | 130.9 | 35.06 | 20.36 | 9.9999
11305 | R-514A | 131 | 35.12 | 20.42 | 10.0294
11306 | R-514A | 131.1 | 35.18 | 20.48 | 10.0588
11307 | R-514A | 131.2 | 35.24 | 20.54 | 10.0883
11308 | R-514A | 131.3 | 35.3 | 20.6 | 10.1178
11309 | R-514A | 131.4 | 35.36 | 20.66 | 10.1472
11310 | R-514A | 131.5 | 35.42 | 20.72 | 10.1767
11311 | R-514A | 131.6 | 35.48 | 20.78 | 10.2062
11312 | R-514A | 131.7 | 35.54 | 20.84 | 10.2357
11313 | R-514A | 131.8 | 35.6 | 20.9 | 10.2651
11314 | R-514A | 131.9 | 35.66 | 20.96 | 10.2946
11315 | R-514A | 132 | 35.72 | 21.02 | 10.3241
11316 | R-514A | 132.1 | 35.78 | 21.08 | 10.3535
11317 | R-514A | 132.2 | 35.84 | 21.14 | 10.383
11318 | R-514A | 132.3 | 35.9 | 21.2 | 10.4125
11319 | R-514A | 132.4 | 35.96 | 21.26 | 10.4419
11320 | R-514A | 132.5 | 36.02 | 21.32 | 10.4714
11321 | R-514A | 132.6 | 36.08 | 21.38 | 10.5009
11322 | R-514A | 132.7 | 36.14 | 21.44 | 10.5304
11323 | R-514A | 132.8 | 36.2 | 21.5 | 10.5598
11324 | R-514A | 132.9 | 36.26 | 21.56 | 10.5893
11325 | R-514A | 133 | 36.32 | 21.62 | 10.6188
11326 | R-514A | 133.1 | 36.38 | 21.68 | 10.6482
11327 | R-514A | 133.2 | 36.44 | 21.74 | 10.6777
11328 | R-514A | 133.3 | 36.5 | 21.8 | 10.7072
11329 | R-514A | 133.4 | 36.56 | 21.86 | 10.7366
11330 | R-514A | 133.5 | 36.62 | 21.92 | 10.7661
11331 | R-514A | 133.6 | 36.68 | 21.98 | 10.7956
11332 | R-514A | 133.7 | 36.74 | 22.04 | 10.825
11333 | R-514A | 133.8 | 36.8 | 22.1 | 10.8545
11334 | R-514A | 133.9 | 36.86 | 22.16 | 10.884
11335 | R-514A | 134 | 36.93 | 22.23 | 10.9184
11336 | R-514A | 134.1 | 36.99 | 22.29 | 10.9478
11337 | R-514A | 134.2 | 37.05 | 22.35 | 10.9773
11338 | R-514A | 134.3 | 37.11 | 22.41 | 11.0068
11339 | R-514A | 134.4 | 37.17 | 22.47 | 11.0362
11340 | R-514A | 134.5 | 37.23 | 22.53 | 11.0657
11341 | R-514A | 134.6 | 37.3 | 22.6 | 11.1001
11342 | R-514A | 134.7 | 37.36 | 22.66 | 11.1296
11343 | R-514A | 134.8 | 37.42 | 22.72 | 11.159
11344 | R-514A | 134.9 | 37.48 | 22.78 | 11.1885
11345 | R-514A | 135 | 37.54 | 22.84 | 11.218
11346 | R-514A | 135.1 | 37.6 | 22.9 | 11.2474
11347 | R-514A | 135.2 | 37.67 | 22.97 | 11.2818
11348 | R-514A | 135.3 | 37.73 | 23.03 | 11.3113
11349 | R-514A | 135.4 | 37.79 | 23.09 | 11.3407
11350 | R-514A | 135.5 | 37.85 | 23.15 | 11.3702
11351 | R-514A | 135.6 | 37.92 | 23.22 | 11.4046
11352 | R-514A | 135.7 | 37.98 | 23.28 | 11.4341
11353 | R-514A | 135.8 | 38.04 | 23.34 | 11.4635
11354 | R-514A | 135.9 | 38.1 | 23.4 | 11.493
11355 | R-514A | 136 | 38.17 | 23.47 | 11.5274
11356 | R-514A | 136.1 | 38.23 | 23.53 | 11.5569
11357 | R-514A | 136.2 | 38.29 | 23.59 | 11.5863
11358 | R-514A | 136.3 | 38.36 | 23.66 | 11.6207
11359 | R-514A | 136.4 | 38.42 | 23.72 | 11.6502
11360 | R-514A | 136.5 | 38.48 | 23.78 | 11.6797
11361 | R-514A | 136.6 | 38.55 | 23.85 | 11.714
11362 | R-514A | 136.7 | 38.61 | 23.91 | 11.7435
11363 | R-514A | 136.8 | 38.67 | 23.97 | 11.773
11364 | R-514A | 136.9 | 38.74 | 24.04 | 11.8073
11365 | R-514A | 137 | 38.8 | 24.1 | 11.8368
11366 | R-514A | 137.1 | 38.86 | 24.16 | 11.8663
11367 | R-514A | 137.2 | 38.93 | 24.23 | 11.9007
11368 | R-514A | 137.3 | 38.99 | 24.29 | 11.9301
11369 | R-514A | 137.4 | 39.05 | 24.35 | 11.9596
11370 | R-514A | 137.5 | 39.12 | 24.42 | 11.994
11371 | R-514A | 137.6 | 39.18 | 24.48 | 12.0235
11372 | R-514A | 137.7 | 39.25 | 24.55 | 12.0578
11373 | R-514A | 137.8 | 39.31 | 24.61 | 12.0873
11374 | R-514A | 137.9 | 39.37 | 24.67 | 12.1168
11375 | R-514A | 138 | 39.44 | 24.74 | 12.1512
11376 | R-514A | 138.1 | 39.5 | 24.8 | 12.1806
11377 | R-514A | 138.2 | 39.57 | 24.87 | 12.215
11378 | R-514A | 138.3 | 39.63 | 24.93 | 12.2445
11379 | R-514A | 138.4 | 39.7 | 25 | 12.2789
11380 | R-514A | 138.5 | 39.76 | 25.06 | 12.3083
11381 | R-514A | 138.6 | 39.83 | 25.13 | 12.3427
11382 | R-514A | 138.7 | 39.89 | 25.19 | 12.3722
11383 | R-514A | 138.8 | 39.96 | 25.26 | 12.4066
11384 | R-514A | 138.9 | 40.02 | 25.32 | 12.436
11385 | R-514A | 139 | 40.09 | 25.39 | 12.4704
11386 | R-514A | 139.1 | 40.15 | 25.45 | 12.4999
11387 | R-514A | 139.2 | 40.22 | 25.52 | 12.5343
11388 | R-514A | 139.3 | 40.28 | 25.58 | 12.5637
11389 | R-514A | 139.4 | 40.35 | 25.65 | 12.5981
11390 | R-514A | 139.5 | 40.41 | 25.71 | 12.6276
11391 | R-514A | 139.6 | 40.48 | 25.78 | 12.662
11392 | R-514A | 139.7 | 40.55 | 25.85 | 12.6963
11393 | R-514A | 139.8 | 40.61 | 25.91 | 12.7258
11394 | R-514A | 139.9 | 40.68 | 25.98 | 12.7602
11395 | R-514A | 140 | 40.74 | 26.04 | 12.7897
11396 | R-514A | 140.1 | 40.81 | 26.11 | 12.824
11397 | R-514A | 140.2 | 40.88 | 26.18 | 12.8584
11398 | R-514A | 140.3 | 40.94 | 26.24 | 12.8879
11399 | R-514A | 140.4 | 41.01 | 26.31 | 12.9223
11400 | R-514A | 140.5 | 41.08 | 26.38 | 12.9566
11401 | R-514A | 140.6 | 41.14 | 26.44 | 12.9861
11402 | R-514A | 140.7 | 41.21 | 26.51 | 13.0205
11403 | R-514A | 140.8 | 41.27 | 26.57 | 13.05
11404 | R-514A | 140.9 | 41.34 | 26.64 | 13.0844
11405 | R-514A | 141 | 41.41 | 26.71 | 13.1187
11406 | R-514A | 141.1 | 41.48 | 26.78 | 13.1531
11407 | R-514A | 141.2 | 41.54 | 26.84 | 13.1826
11408 | R-514A | 141.3 | 41.61 | 26.91 | 13.217
11409 | R-514A | 141.4 | 41.68 | 26.98 | 13.2513
11410 | R-514A | 141.5 | 41.74 | 27.04 | 13.2808
11411 | R-514A | 141.6 | 41.81 | 27.11 | 13.3152
11412 | R-514A | 141.7 | 41.88 | 27.18 | 13.3496
11413 | R-514A | 141.8 | 41.95 | 27.25 | 13.384
11414 | R-514A | 141.9 | 42.01 | 27.31 | 13.4134
11415 | R-514A | 142 | 42.08 | 27.38 | 13.4478
11416 | R-514A | 142.1 | 42.15 | 27.45 | 13.4822
11417 | R-514A | 142.2 | 42.22 | 27.52 | 13.5166
11418 | R-514A | 142.3 | 42.29 | 27.59 | 13.551
11419 | R-514A | 142.4 | 42.35 | 27.65 | 13.5804
11420 | R-514A | 142.5 | 42.42 | 27.72 | 13.6148
11421 | R-514A | 142.6 | 42.49 | 27.79 | 13.6492
11422 | R-514A | 142.7 | 42.56 | 27.86 | 13.6836
11423 | R-514A | 142.8 | 42.63 | 27.93 | 13.7179
11424 | R-514A | 142.9 | 42.69 | 27.99 | 13.7474
11425 | R-514A | 143 | 42.76 | 28.06 | 13.7818
11426 | R-514A | 143.1 | 42.83 | 28.13 | 13.8162
11427 | R-514A | 143.2 | 42.9 | 28.2 | 13.8506
11428 | R-514A | 143.3 | 42.97 | 28.27 | 13.8849
11429 | R-514A | 143.4 | 43.04 | 28.34 | 13.9193
11430 | R-514A | 143.5 | 43.11 | 28.41 | 13.9537
11431 | R-514A | 143.6 | 43.18 | 28.48 | 13.9881
11432 | R-514A | 143.7 | 43.24 | 28.54 | 14.0175
11433 | R-514A | 143.8 | 43.31 | 28.61 | 14.0519
11434 | R-514A | 143.9 | 43.38 | 28.68 | 14.0863
11435 | R-514A | 144 | 43.45 | 28.75 | 14.1207
11436 | R-514A | 144.1 | 43.52 | 28.82 | 14.1551
11437 | R-514A | 144.2 | 43.59 | 28.89 | 14.1895
11438 | R-514A | 144.3 | 43.66 | 28.96 | 14.2238
11439 | R-514A | 144.4 | 43.73 | 29.03 | 14.2582
11440 | R-514A | 144.5 | 43.8 | 29.1 | 14.2926
11441 | R-514A | 144.6 | 43.87 | 29.17 | 14.327
11442 | R-514A | 144.7 | 43.94 | 29.24 | 14.3613
11443 | R-514A | 144.8 | 44.01 | 29.31 | 14.3957
11444 | R-514A | 144.9 | 44.08 | 29.38 | 14.4301
11445 | R-514A | 145 | 44.15 | 29.45 | 14.4645
11446 | R-514A | 145.1 | 44.22 | 29.52 | 14.4989
11447 | R-514A | 145.2 | 44.29 | 29.59 | 14.5333
11448 | R-514A | 145.3 | 44.36 | 29.66 | 14.5676
11449 | R-514A | 145.4 | 44.43 | 29.73 | 14.602
11450 | R-514A | 145.5 | 44.5 | 29.8 | 14.6364
11451 | R-514A | 145.6 | 44.57 | 29.87 | 14.6708
11452 | R-514A | 145.7 | 44.64 | 29.94 | 14.7052
11453 | R-514A | 145.8 | 44.72 | 30.02 | 14.7445
11454 | R-514A | 145.9 | 44.79 | 30.09 | 14.7788
11455 | R-514A | 146 | 44.86 | 30.16 | 14.8132
11456 | R-514A | 146.1 | 44.93 | 30.23 | 14.8476
11457 | R-514A | 146.2 | 45 | 30.3 | 14.882
11458 | R-514A | 146.3 | 45.07 | 30.37 | 14.9164
11459 | R-514A | 146.4 | 45.14 | 30.44 | 14.9507
11460 | R-514A | 146.5 | 45.21 | 30.51 | 14.9851
11461 | R-514A | 146.6 | 45.29 | 30.59 | 15.0244
11462 | R-514A | 146.7 | 45.36 | 30.66 | 15.0588
11463 | R-514A | 146.8 | 45.43 | 30.73 | 15.0932
11464 | R-514A | 146.9 | 45.5 | 30.8 | 15.1275
11465 | R-514A | 147 | 45.57 | 30.87 | 15.1619
11466 | R-514A | 147.1 | 45.64 | 30.94 | 15.1963
11467 | R-514A | 147.2 | 45.72 | 31.02 | 15.2356
11468 | R-514A | 147.3 | 45.79 | 31.09 | 15.27
11469 | R-514A | 147.4 | 45.86 | 31.16 | 15.3044
11470 | R-514A | 147.5 | 45.93 | 31.23 | 15.3387
11471 | R-514A | 147.6 | 46.01 | 31.31 | 15.378
11472 | R-514A | 147.7 | 46.08 | 31.38 | 15.4124
11473 | R-514A | 147.8 | 46.15 | 31.45 | 15.4468
11474 | R-514A | 147.9 | 46.22 | 31.52 | 15.4812
11475 | R-514A | 148 | 46.3 | 31.6 | 15.5205
11476 | R-514A | 148.1 | 46.37 | 31.67 | 15.5549
11477 | R-514A | 148.2 | 46.44 | 31.74 | 15.5892
11478 | R-514A | 148.3 | 46.52 | 31.82 | 15.6285
11479 | R-514A | 148.4 | 46.59 | 31.89 | 15.6629
11480 | R-514A | 148.5 | 46.66 | 31.96 | 15.6973
11481 | R-514A | 148.6 | 46.74 | 32.04 | 15.7366
11482 | R-514A | 148.7 | 46.81 | 32.11 | 15.771
11483 | R-514A | 148.8 | 46.88 | 32.18 | 15.8054
11484 | R-514A | 148.9 | 46.96 | 32.26 | 15.8446
11485 | R-514A | 149 | 47.03 | 32.33 | 15.879
11486 | R-514A | 149.1 | 47.1 | 32.4 | 15.9134
11487 | R-514A | 149.2 | 47.18 | 32.48 | 15.9527
11488 | R-514A | 149.3 | 47.25 | 32.55 | 15.9871
11489 | R-514A | 149.4 | 47.33 | 32.63 | 16.0264
11490 | R-514A | 149.5 | 47.4 | 32.7 | 16.0607
11491 | R-514A | 149.6 | 47.47 | 32.77 | 16.0951
11492 | R-514A | 149.7 | 47.55 | 32.85 | 16.1344
11493 | R-514A | 149.8 | 47.62 | 32.92 | 16.1688
11494 | R-514A | 149.9 | 47.7 | 33 | 16.2081
11495 | R-514A | 150 | 47.77 | 33.07 | 16.2425
11496 | R-514A | 150.1 | 47.85 | 33.15 | 16.2818
11497 | R-514A | 150.2 | 47.92 | 33.22 | 16.3162
11498 | R-514A | 150.3 | 48 | 33.3 | 16.3554
11499 | R-514A | 150.4 | 48.07 | 33.37 | 16.3898
11500 | R-514A | 150.5 | 48.15 | 33.45 | 16.4291
11501 | R-514A | 150.6 | 48.22 | 33.52 | 16.4635
11502 | R-514A | 150.7 | 48.3 | 33.6 | 16.5028
11503 | R-514A | 150.8 | 48.37 | 33.67 | 16.5372
11504 | R-514A | 150.9 | 48.45 | 33.75 | 16.5765
11505 | R-514A | 151 | 48.52 | 33.82 | 16.6108
11506 | R-514A | 151.1 | 48.6 | 33.9 | 16.6501
11507 | R-514A | 151.2 | 48.67 | 33.97 | 16.6845
11508 | R-514A | 151.3 | 48.75 | 34.05 | 16.7238
11509 | R-514A | 151.4 | 48.82 | 34.12 | 16.7582
11510 | R-514A | 151.5 | 48.9 | 34.2 | 16.7975
11511 | R-514A | 151.6 | 48.98 | 34.28 | 16.8368
11512 | R-514A | 151.7 | 49.05 | 34.35 | 16.8712
11513 | R-514A | 151.8 | 49.13 | 34.43 | 16.9104
11514 | R-514A | 151.9 | 49.2 | 34.5 | 16.9448
11515 | R-514A | 152 | 49.28 | 34.58 | 16.9841
11516 | R-514A | 152.1 | 49.36 | 34.66 | 17.0234
11517 | R-514A | 152.2 | 49.43 | 34.73 | 17.0578
11518 | R-514A | 152.3 | 49.51 | 34.81 | 17.0971
11519 | R-514A | 152.4 | 49.59 | 34.89 | 17.1364
11520 | R-514A | 152.5 | 49.66 | 34.96 | 17.1708
11521 | R-514A | 152.6 | 49.74 | 35.04 | 17.21
11522 | R-514A | 152.7 | 49.82 | 35.12 | 17.2493
11523 | R-514A | 152.8 | 49.89 | 35.19 | 17.2837
11524 | R-514A | 152.9 | 49.97 | 35.27 | 17.323
11525 | R-514A | 153 | 50.05 | 35.35 | 17.3623
11526 | R-514A | 153.1 | 50.13 | 35.43 | 17.4016
11527 | R-514A | 153.2 | 50.2 | 35.5 | 17.436
11528 | R-514A | 153.3 | 50.28 | 35.58 | 17.4753
11529 | R-514A | 153.4 | 50.36 | 35.66 | 17.5146
11530 | R-514A | 153.5 | 50.44 | 35.74 | 17.5539
11531 | R-514A | 153.6 | 50.51 | 35.81 | 17.5882
11532 | R-514A | 153.7 | 50.59 | 35.89 | 17.6275
11533 | R-514A | 153.8 | 50.67 | 35.97 | 17.6668
11534 | R-514A | 153.9 | 50.75 | 36.05 | 17.7061
11535 | R-514A | 154 | 50.83 | 36.13 | 17.7454
11536 | R-514A | 154.1 | 50.9 | 36.2 | 17.7798
11537 | R-514A | 154.2 | 50.98 | 36.28 | 17.8191
11538 | R-514A | 154.3 | 51.06 | 36.36 | 17.8584
11539 | R-514A | 154.4 | 51.14 | 36.44 | 17.8977
11540 | R-514A | 154.5 | 51.22 | 36.52 | 17.937
11541 | R-514A | 154.6 | 51.3 | 36.6 | 17.9763
11542 | R-514A | 154.7 | 51.38 | 36.68 | 18.0155
11543 | R-514A | 154.8 | 51.46 | 36.76 | 18.0548
11544 | R-514A | 154.9 | 51.53 | 36.83 | 18.0892
11545 | R-514A | 155 | 51.61 | 36.91 | 18.1285
11546 | R-514A | 155.1 | 51.69 | 36.99 | 18.1678
11547 | R-514A | 155.2 | 51.77 | 37.07 | 18.2071
11548 | R-514A | 155.3 | 51.85 | 37.15 | 18.2464
11549 | R-514A | 155.4 | 51.93 | 37.23 | 18.2857
11550 | R-514A | 155.5 | 52.01 | 37.31 | 18.325
11551 | R-514A | 155.6 | 52.09 | 37.39 | 18.3643
11552 | R-514A | 155.7 | 52.17 | 37.47 | 18.4035
11553 | R-514A | 155.8 | 52.25 | 37.55 | 18.4428
11554 | R-514A | 155.9 | 52.33 | 37.63 | 18.4821
11555 | R-514A | 156 | 52.41 | 37.71 | 18.5214
11556 | R-514A | 156.1 | 52.49 | 37.79 | 18.5607
11557 | R-514A | 156.2 | 52.57 | 37.87 | 18.6
11558 | R-514A | 156.3 | 52.65 | 37.95 | 18.6393
11559 | R-514A | 156.4 | 52.73 | 38.03 | 18.6786
11560 | R-514A | 156.5 | 52.81 | 38.11 | 18.7179
11561 | R-514A | 156.6 | 52.89 | 38.19 | 18.7572
11562 | R-514A | 156.7 | 52.97 | 38.27 | 18.7965
11563 | R-514A | 156.8 | 53.05 | 38.35 | 18.8358
11564 | R-514A | 156.9 | 53.13 | 38.43 | 18.8751
11565 | R-514A | 157 | 53.21 | 38.51 | 18.9143
11566 | R-514A | 157.1 | 53.3 | 38.6 | 18.9586
11567 | R-514A | 157.2 | 53.38 | 38.68 | 18.9978
11568 | R-514A | 157.3 | 53.46 | 38.76 | 19.0371
11569 | R-514A | 157.4 | 53.54 | 38.84 | 19.0764
11570 | R-514A | 157.5 | 53.62 | 38.92 | 19.1157
11571 | R-514A | 157.6 | 53.7 | 39 | 19.155
11572 | R-514A | 157.7 | 53.78 | 39.08 | 19.1943
11573 | R-514A | 157.8 | 53.87 | 39.17 | 19.2385
11574 | R-514A | 157.9 | 53.95 | 39.25 | 19.2778
11575 | R-514A | 158 | 54.03 | 39.33 | 19.3171
11576 | R-514A | 158.1 | 54.11 | 39.41 | 19.3564
11577 | R-514A | 158.2 | 54.19 | 39.49 | 19.3957
11578 | R-514A | 158.3 | 54.28 | 39.58 | 19.4399
11579 | R-514A | 158.4 | 54.36 | 39.66 | 19.4792
11580 | R-514A | 158.5 | 54.44 | 39.74 | 19.5185
11581 | R-514A | 158.6 | 54.52 | 39.82 | 19.5578
11582 | R-514A | 158.7 | 54.61 | 39.91 | 19.602
11583 | R-514A | 158.8 | 54.69 | 39.99 | 19.6413
11584 | R-514A | 158.9 | 54.77 | 40.07 | 19.6806
11585 | R-514A | 159 | 54.85 | 40.15 | 19.7199
11586 | R-514A | 159.1 | 54.94 | 40.24 | 19.7641
11587 | R-514A | 159.2 | 55.02 | 40.32 | 19.8033
11588 | R-514A | 159.3 | 55.1 | 40.4 | 19.8426
11589 | R-514A | 159.4 | 55.19 | 40.49 | 19.8868
11590 | R-514A | 159.5 | 55.27 | 40.57 | 19.9261
11591 | R-514A | 159.6 | 55.35 | 40.65 | 19.9654
11592 | R-514A | 159.7 | 55.44 | 40.74 | 20.0096
11593 | R-514A | 159.8 | 55.52 | 40.82 | 20.0489
11594 | R-514A | 159.9 | 55.6 | 40.9 | 20.0882
11595 | R-514A | 160 | 55.69 | 40.99 | 20.1324
11596 | R-514A | 160.1 | 55.77 | 41.07 | 20.1717
11597 | R-514A | 160.2 | 55.86 | 41.16 | 20.2159
11598 | R-514A | 160.3 | 55.94 | 41.24 | 20.2552
11599 | R-514A | 160.4 | 56.02 | 41.32 | 20.2945
11600 | R-514A | 160.5 | 56.11 | 41.41 | 20.3387
11601 | R-514A | 160.6 | 56.19 | 41.49 | 20.378
11602 | R-514A | 160.7 | 56.28 | 41.58 | 20.4222
11603 | R-514A | 160.8 | 56.36 | 41.66 | 20.4615
11604 | R-514A | 160.9 | 56.45 | 41.75 | 20.5057
11605 | R-514A | 161 | 56.53 | 41.83 | 20.545
11606 | R-514A | 161.1 | 56.62 | 41.92 | 20.5892
11607 | R-514A | 161.2 | 56.7 | 42 | 20.6285
11608 | R-514A | 161.3 | 56.79 | 42.09 | 20.6727
11609 | R-514A | 161.4 | 56.87 | 42.17 | 20.712
11610 | R-514A | 161.5 | 56.96 | 42.26 | 20.7562
11611 | R-514A | 161.6 | 57.04 | 42.34 | 20.7955
11612 | R-514A | 161.7 | 57.13 | 42.43 | 20.8397
11613 | R-514A | 161.8 | 57.21 | 42.51 | 20.879
11614 | R-514A | 161.9 | 57.3 | 42.6 | 20.9232
11615 | R-514A | 162 | 57.38 | 42.68 | 20.9625
11616 | R-514A | 162.1 | 57.47 | 42.77 | 21.0067
11617 | R-514A | 162.2 | 57.56 | 42.86 | 21.0509
11618 | R-514A | 162.3 | 57.64 | 42.94 | 21.0902
11619 | R-514A | 162.4 | 57.73 | 43.03 | 21.1344
11620 | R-514A | 162.5 | 57.81 | 43.11 | 21.1737
11621 | R-514A | 162.6 | 57.9 | 43.2 | 21.2179
11622 | R-514A | 162.7 | 57.99 | 43.29 | 21.2621
11623 | R-514A | 162.8 | 58.07 | 43.37 | 21.3014
11624 | R-514A | 162.9 | 58.16 | 43.46 | 21.3456
11625 | R-514A | 163 | 58.25 | 43.55 | 21.3898
11626 | R-514A | 163.1 | 58.33 | 43.63 | 21.4291
11627 | R-514A | 163.2 | 58.42 | 43.72 | 21.4733
11628 | R-514A | 163.3 | 58.51 | 43.81 | 21.5175
11629 | R-514A | 163.4 | 58.6 | 43.9 | 21.5617
11630 | R-514A | 163.5 | 58.68 | 43.98 | 21.601
11631 | R-514A | 163.6 | 58.77 | 44.07 | 21.6452
11632 | R-514A | 163.7 | 58.86 | 44.16 | 21.6894
11633 | R-514A | 163.8 | 58.94 | 44.24 | 21.7287
11634 | R-514A | 163.9 | 59.03 | 44.33 | 21.7729
11635 | R-514A | 164 | 59.12 | 44.42 | 21.8171
11636 | R-514A | 164.1 | 59.21 | 44.51 | 21.8613
11637 | R-514A | 164.2 | 59.3 | 44.6 | 21.9055
11638 | R-514A | 164.3 | 59.38 | 44.68 | 21.9448
11639 | R-514A | 164.4 | 59.47 | 44.77 | 21.989
11640 | R-514A | 164.5 | 59.56 | 44.86 | 22.0332
11641 | R-514A | 164.6 | 59.65 | 44.95 | 22.0774
11642 | R-514A | 164.7 | 59.74 | 45.04 | 22.1216
11643 | R-514A | 164.8 | 59.82 | 45.12 | 22.1609
11644 | R-514A | 164.9 | 59.91 | 45.21 | 22.2051
11645 | R-514A | 165 | 60 | 45.3 | 22.2493
11646 | R-514A | 165.1 | 60.09 | 45.39 | 22.2935
11647 | R-514A | 165.2 | 60.18 | 45.48 | 22.3377
11648 | R-514A | 165.3 | 60.27 | 45.57 | 22.3819
11649 | R-514A | 165.4 | 60.36 | 45.66 | 22.4261
11650 | R-514A | 165.5 | 60.45 | 45.75 | 22.4703
11651 | R-514A | 165.6 | 60.54 | 45.84 | 22.5145
11652 | R-514A | 165.7 | 60.63 | 45.93 | 22.5587
11653 | R-514A | 165.8 | 60.72 | 46.02 | 22.6029
11654 | R-514A | 165.9 | 60.8 | 46.1 | 22.6422
11655 | R-514A | 166 | 60.89 | 46.19 | 22.6864
11656 | R-514A | 166.1 | 60.98 | 46.28 | 22.7306
11657 | R-514A | 166.2 | 61.07 | 46.37 | 22.7748
11658 | R-514A | 166.3 | 61.16 | 46.46 | 22.819
11659 | R-514A | 166.4 | 61.26 | 46.56 | 22.8681
11660 | R-514A | 166.5 | 61.35 | 46.65 | 22.9123
11661 | R-514A | 166.6 | 61.44 | 46.74 | 22.9566
11662 | R-514A | 166.7 | 61.53 | 46.83 | 23.0008
11663 | R-514A | 166.8 | 61.62 | 46.92 | 23.045
11664 | R-514A | 166.9 | 61.71 | 47.01 | 23.0892
11665 | R-514A | 167 | 61.8 | 47.1 | 23.1334
11666 | R-514A | 167.1 | 61.89 | 47.19 | 23.1776
11667 | R-514A | 167.2 | 61.98 | 47.28 | 23.2218
11668 | R-514A | 167.3 | 62.07 | 47.37 | 23.266
11669 | R-514A | 167.4 | 62.16 | 47.46 | 23.3102
11670 | R-514A | 167.5 | 62.25 | 47.55 | 23.3544
11671 | R-514A | 167.6 | 62.34 | 47.64 | 23.3986
11672 | R-514A | 167.7 | 62.44 | 47.74 | 23.4477
11673 | R-514A | 167.8 | 62.53 | 47.83 | 23.4919
11674 | R-514A | 167.9 | 62.62 | 47.92 | 23.5361
11675 | R-514A | 168 | 62.71 | 48.01 | 23.5803
11676 | R-514A | 168.1 | 62.8 | 48.1 | 23.6245
11677 | R-514A | 168.2 | 62.89 | 48.19 | 23.6687
11678 | R-514A | 168.3 | 62.99 | 48.29 | 23.7178
11679 | R-514A | 168.4 | 63.08 | 48.38 | 23.762
11680 | R-514A | 168.5 | 63.17 | 48.47 | 23.8062
11681 | R-514A | 168.6 | 63.26 | 48.56 | 23.8504
11682 | R-514A | 168.7 | 63.36 | 48.66 | 23.8996
11683 | R-514A | 168.8 | 63.45 | 48.75 | 23.9438
11684 | R-514A | 168.9 | 63.54 | 48.84 | 23.988
11685 | R-514A | 169 | 63.63 | 48.93 | 24.0322
11686 | R-514A | 169.1 | 63.73 | 49.03 | 24.0813
11687 | R-514A | 169.2 | 63.82 | 49.12 | 24.1255
11688 | R-514A | 169.3 | 63.91 | 49.21 | 24.1697
11689 | R-514A | 169.4 | 64.01 | 49.31 | 24.2188
11690 | R-514A | 169.5 | 64.1 | 49.4 | 24.263
11691 | R-514A | 169.6 | 64.19 | 49.49 | 24.3072
11692 | R-514A | 169.7 | 64.29 | 49.59 | 24.3563
11693 | R-514A | 169.8 | 64.38 | 49.68 | 24.4005
11694 | R-514A | 169.9 | 64.47 | 49.77 | 24.4447
11695 | R-514A | 170 | 64.57 | 49.87 | 24.4939
11696 | R-514A | 170.1 | 64.66 | 49.96 | 24.5381
11697 | R-514A | 170.2 | 64.75 | 50.05 | 24.5823
11698 | R-514A | 170.3 | 64.85 | 50.15 | 24.6314
11699 | R-514A | 170.4 | 64.94 | 50.24 | 24.6756
11700 | R-514A | 170.5 | 65.04 | 50.34 | 24.7247
11701 | R-514A | 170.6 | 65.13 | 50.43 | 24.7689
11702 | R-514A | 170.7 | 65.23 | 50.53 | 24.818
11703 | R-514A | 170.8 | 65.32 | 50.62 | 24.8622
11704 | R-514A | 170.9 | 65.41 | 50.71 | 24.9064
11705 | R-514A | 171 | 65.51 | 50.81 | 24.9555
11706 | R-514A | 171.1 | 65.6 | 50.9 | 24.9997
11707 | R-514A | 171.2 | 65.7 | 51 | 25.0489
11708 | R-514A | 171.3 | 65.8 | 51.1 | 25.098
11709 | R-514A | 171.4 | 65.89 | 51.19 | 25.1422
11710 | R-514A | 171.5 | 65.99 | 51.29 | 25.1913
11711 | R-514A | 171.6 | 66.08 | 51.38 | 25.2355
11712 | R-514A | 171.7 | 66.18 | 51.48 | 25.2846
11713 | R-514A | 171.8 | 66.27 | 51.57 | 25.3288
11714 | R-514A | 171.9 | 66.37 | 51.67 | 25.3779
11715 | R-514A | 172 | 66.46 | 51.76 | 25.4221
11716 | R-514A | 172.1 | 66.56 | 51.86 | 25.4713
11717 | R-514A | 172.2 | 66.66 | 51.96 | 25.5204
11718 | R-514A | 172.3 | 66.75 | 52.05 | 25.5646
11719 | R-514A | 172.4 | 66.85 | 52.15 | 25.6137
11720 | R-514A | 172.5 | 66.95 | 52.25 | 25.6628
11721 | R-514A | 172.6 | 67.04 | 52.34 | 25.707
11722 | R-514A | 172.7 | 67.14 | 52.44 | 25.7561
11723 | R-514A | 172.8 | 67.23 | 52.53 | 25.8003
11724 | R-514A | 172.9 | 67.33 | 52.63 | 25.8495
11725 | R-514A | 173 | 67.43 | 52.73 | 25.8986
11726 | R-514A | 173.1 | 67.53 | 52.83 | 25.9477
11727 | R-514A | 173.2 | 67.62 | 52.92 | 25.9919
11728 | R-514A | 173.3 | 67.72 | 53.02 | 26.041
11729 | R-514A | 173.4 | 67.82 | 53.12 | 26.0901
11730 | R-514A | 173.5 | 67.92 | 53.22 | 26.1392
11731 | R-514A | 173.6 | 68.01 | 53.31 | 26.1834
11732 | R-514A | 173.7 | 68.11 | 53.41 | 26.2325
11733 | R-514A | 173.8 | 68.21 | 53.51 | 26.2817
11734 | R-514A | 173.9 | 68.31 | 53.61 | 26.3308
11735 | R-514A | 174 | 68.4 | 53.7 | 26.375
11736 | R-514A | 174.1 | 68.5 | 53.8 | 26.4241
11737 | R-514A | 174.2 | 68.6 | 53.9 | 26.4732
11738 | R-514A | 174.3 | 68.7 | 54 | 26.5223
11739 | R-514A | 174.4 | 68.8 | 54.1 | 26.5714
11740 | R-514A | 174.5 | 68.9 | 54.2 | 26.6206
11741 | R-514A | 174.6 | 68.99 | 54.29 | 26.6648
11742 | R-514A | 174.7 | 69.09 | 54.39 | 26.7139
11743 | R-514A | 174.8 | 69.19 | 54.49 | 26.763
11744 | R-514A | 174.9 | 69.29 | 54.59 | 26.8121
11745 | R-514A | 175 | 69.39 | 54.69 | 26.8612
11746 | R-514A | 175.1 | 69.49 | 54.79 | 26.9103
11747 | R-514A | 175.2 | 69.59 | 54.89 | 26.9595
11748 | R-514A | 175.3 | 69.69 | 54.99 | 27.0086
11749 | R-514A | 175.4 | 69.79 | 55.09 | 27.0577
11750 | R-514A | 175.5 | 69.89 | 55.19 | 27.1068
11751 | R-514A | 175.6 | 69.99 | 55.29 | 27.1559
11752 | R-514A | 175.7 | 70.09 | 55.39 | 27.205
11753 | R-514A | 175.8 | 70.19 | 55.49 | 27.2541
11754 | R-514A | 175.9 | 70.29 | 55.59 | 27.3033
11755 | R-514A | 176 | 70.38 | 55.68 | 27.3475
11756 | R-514A | 176.1 | 70.49 | 55.79 | 27.4015
11757 | R-514A | 176.2 | 70.59 | 55.89 | 27.4506
11758 | R-514A | 176.3 | 70.69 | 55.99 | 27.4997
11759 | R-514A | 176.4 | 70.79 | 56.09 | 27.5489
11760 | R-514A | 176.5 | 70.89 | 56.19 | 27.598
11761 | R-514A | 176.6 | 70.99 | 56.29 | 27.6471
11762 | R-514A | 176.7 | 71.09 | 56.39 | 27.6962
11763 | R-514A | 176.8 | 71.19 | 56.49 | 27.7453
11764 | R-514A | 176.9 | 71.29 | 56.59 | 27.7944
11765 | R-514A | 177 | 71.39 | 56.69 | 27.8435
11766 | R-514A | 177.1 | 71.49 | 56.79 | 27.8926
11767 | R-514A | 177.2 | 71.6 | 56.9 | 27.9467
11768 | R-514A | 177.3 | 71.7 | 57 | 27.9958
11769 | R-514A | 177.4 | 71.8 | 57.1 | 28.0449
11770 | R-514A | 177.5 | 71.9 | 57.2 | 28.094
11771 | R-514A | 177.6 | 72 | 57.3 | 28.1431
11772 | R-514A | 177.7 | 72.1 | 57.4 | 28.1923
11773 | R-514A | 177.8 | 72.21 | 57.51 | 28.2463
11774 | R-514A | 177.9 | 72.31 | 57.61 | 28.2954
11775 | R-514A | 178 | 72.41 | 57.71 | 28.3445
11776 | R-514A | 178.1 | 72.51 | 57.81 | 28.3936
11777 | R-514A | 178.2 | 72.62 | 57.92 | 28.4477
11778 | R-514A | 178.3 | 72.72 | 58.02 | 28.4968
11779 | R-514A | 178.4 | 72.82 | 58.12 | 28.5459
11780 | R-514A | 178.5 | 72.92 | 58.22 | 28.595
11781 | R-514A | 178.6 | 73.03 | 58.33 | 28.649
11782 | R-514A | 178.7 | 73.13 | 58.43 | 28.6981
11783 | R-514A | 178.8 | 73.23 | 58.53 | 28.7473
11784 | R-514A | 178.9 | 73.34 | 58.64 | 28.8013
11785 | R-514A | 179 | 73.44 | 58.74 | 28.8504
11786 | R-514A | 179.1 | 73.54 | 58.84 | 28.8995
11787 | R-514A | 179.2 | 73.65 | 58.95 | 28.9535
11788 | R-514A | 179.3 | 73.75 | 59.05 | 29.0027
11789 | R-514A | 179.4 | 73.86 | 59.16 | 29.0567
11790 | R-514A | 179.5 | 73.96 | 59.26 | 29.1058
11791 | R-514A | 179.6 | 74.06 | 59.36 | 29.1549
11792 | R-514A | 179.7 | 74.17 | 59.47 | 29.209
11793 | R-514A | 179.8 | 74.27 | 59.57 | 29.2581
11794 | R-514A | 179.9 | 74.38 | 59.68 | 29.3121
11795 | R-514A | 180 | 74.48 | 59.78 | 29.3612
11796 | R-514A | 180.1 | 74.58 | 59.88 | 29.4103
11797 | R-514A | 180.2 | 74.69 | 59.99 | 29.4643
11798 | R-514A | 180.3 | 74.8 | 60.1 | 29.5184
11799 | R-514A | 180.4 | 74.9 | 60.2 | 29.5675
11800 | R-514A | 180.5 | 75.01 | 60.31 | 29.6215
11801 | R-514A | 180.6 | 75.11 | 60.41 | 29.6706
11802 | R-514A | 180.7 | 75.22 | 60.52 | 29.7247
11803 | R-514A | 180.8 | 75.32 | 60.62 | 29.7738
11804 | R-514A | 180.9 | 75.43 | 60.73 | 29.8278
11805 | R-514A | 181 | 75.53 | 60.83 | 29.8769
11806 | R-514A | 181.1 | 75.64 | 60.94 | 29.9309
11807 | R-514A | 181.2 | 75.74 | 61.04 | 29.9801
11808 | R-514A | 181.3 | 75.85 | 61.15 | 30.0341
11809 | R-514A | 181.4 | 75.96 | 61.26 | 30.0881
11810 | R-514A | 181.5 | 76.06 | 61.36 | 30.1372
11811 | R-514A | 181.6 | 76.17 | 61.47 | 30.1913
11812 | R-514A | 181.7 | 76.27 | 61.57 | 30.2404
11813 | R-514A | 181.8 | 76.38 | 61.68 | 30.2944
11814 | R-514A | 181.9 | 76.49 | 61.79 | 30.3484
11815 | R-514A | 182 | 76.59 | 61.89 | 30.3975
11816 | R-514A | 182.1 | 76.7 | 62 | 30.4516
11817 | R-514A | 182.2 | 76.81 | 62.11 | 30.5056
11818 | R-514A | 182.3 | 76.92 | 62.22 | 30.5596
11819 | R-514A | 182.4 | 77.02 | 62.32 | 30.6087
11820 | R-514A | 182.5 | 77.13 | 62.43 | 30.6628
11821 | R-514A | 182.6 | 77.24 | 62.54 | 30.7168
11822 | R-514A | 182.7 | 77.35 | 62.65 | 30.7708
11823 | R-514A | 182.8 | 77.45 | 62.75 | 30.8199
11824 | R-514A | 182.9 | 77.56 | 62.86 | 30.874
11825 | R-514A | 183 | 77.67 | 62.97 | 30.928
11826 | R-514A | 183.1 | 77.78 | 63.08 | 30.982
11827 | R-514A | 183.2 | 77.88 | 63.18 | 31.0311
11828 | R-514A | 183.3 | 77.99 | 63.29 | 31.0852
11829 | R-514A | 183.4 | 78.1 | 63.4 | 31.1392
11830 | R-514A | 183.5 | 78.21 | 63.51 | 31.1932
11831 | R-514A | 183.6 | 78.32 | 63.62 | 31.2472
11832 | R-514A | 183.7 | 78.43 | 63.73 | 31.3013
11833 | R-514A | 183.8 | 78.54 | 63.84 | 31.3553
11834 | R-514A | 183.9 | 78.64 | 63.94 | 31.4044
11835 | R-514A | 184 | 78.75 | 64.05 | 31.4584
11836 | R-514A | 184.1 | 78.86 | 64.16 | 31.5125
11837 | R-514A | 184.2 | 78.97 | 64.27 | 31.5665
11838 | R-514A | 184.3 | 79.08 | 64.38 | 31.6205
11839 | R-514A | 184.4 | 79.19 | 64.49 | 31.6745
11840 | R-514A | 184.5 | 79.3 | 64.6 | 31.7286
11841 | R-514A | 184.6 | 79.41 | 64.71 | 31.7826
11842 | R-514A | 184.7 | 79.52 | 64.82 | 31.8366
11843 | R-514A | 184.8 | 79.63 | 64.93 | 31.8907
11844 | R-514A | 184.9 | 79.74 | 65.04 | 31.9447
11845 | R-514A | 185 | 79.85 | 65.15 | 31.9987
11846 | R-514A | 185.1 | 79.96 | 65.26 | 32.0527
11847 | R-514A | 185.2 | 80.07 | 65.37 | 32.1068
11848 | R-514A | 185.3 | 80.18 | 65.48 | 32.1608
11849 | R-514A | 185.4 | 80.29 | 65.59 | 32.2148
11850 | R-514A | 185.5 | 80.4 | 65.7 | 32.2688
11851 | R-514A | 185.6 | 80.51 | 65.81 | 32.3229
11852 | R-514A | 185.7 | 80.62 | 65.92 | 32.3769
11853 | R-514A | 185.8 | 80.74 | 66.04 | 32.4358
11854 | R-514A | 185.9 | 80.85 | 66.15 | 32.4899
11855 | R-514A | 186 | 80.96 | 66.26 | 32.5439
11856 | R-514A | 186.1 | 81.07 | 66.37 | 32.5979
11857 | R-514A | 186.2 | 81.18 | 66.48 | 32.6519
11858 | R-514A | 186.3 | 81.29 | 66.59 | 32.706
11859 | R-514A | 186.4 | 81.4 | 66.7 | 32.76
11860 | R-514A | 186.5 | 81.52 | 66.82 | 32.8189
11861 | R-514A | 186.6 | 81.63 | 66.93 | 32.873
11862 | R-514A | 186.7 | 81.74 | 67.04 | 32.927
11863 | R-514A | 186.8 | 81.85 | 67.15 | 32.981
11864 | R-514A | 186.9 | 81.96 | 67.26 | 33.035
11865 | R-514A | 187 | 82.08 | 67.38 | 33.094
11866 | R-514A | 187.1 | 82.19 | 67.49 | 33.148
11867 | R-514A | 187.2 | 82.3 | 67.6 | 33.202
11868 | R-514A | 187.3 | 82.42 | 67.72 | 33.261
11869 | R-514A | 187.4 | 82.53 | 67.83 | 33.315
11870 | R-514A | 187.5 | 82.64 | 67.94 | 33.369
11871 | R-514A | 187.6 | 82.76 | 68.06 | 33.428
11872 | R-514A | 187.7 | 82.87 | 68.17 | 33.482
11873 | R-514A | 187.8 | 82.98 | 68.28 | 33.536
11874 | R-514A | 187.9 | 83.09 | 68.39 | 33.59
11875 | R-514A | 188 | 83.21 | 68.51 | 33.649
11876 | R-514A | 188.1 | 83.32 | 68.62 | 33.703
11877 | R-514A | 188.2 | 83.44 | 68.74 | 33.7619
11878 | R-514A | 188.3 | 83.55 | 68.85 | 33.816
11879 | R-514A | 188.4 | 83.66 | 68.96 | 33.87
11880 | R-514A | 188.5 | 83.78 | 69.08 | 33.9289
11881 | R-514A | 188.6 | 83.89 | 69.19 | 33.983
11882 | R-514A | 188.7 | 84.01 | 69.31 | 34.0419
11883 | R-514A | 188.8 | 84.12 | 69.42 | 34.0959
11884 | R-514A | 188.9 | 84.24 | 69.54 | 34.1549
11885 | R-514A | 189 | 84.35 | 69.65 | 34.2089
11886 | R-514A | 189.1 | 84.47 | 69.77 | 34.2678
11887 | R-514A | 189.2 | 84.58 | 69.88 | 34.3219
11888 | R-514A | 189.3 | 84.7 | 70 | 34.3808
11889 | R-514A | 189.4 | 84.81 | 70.11 | 34.4348
11890 | R-514A | 189.5 | 84.93 | 70.23 | 34.4938
11891 | R-514A | 189.6 | 85.04 | 70.34 | 34.5478
11892 | R-514A | 189.7 | 85.16 | 70.46 | 34.6067
11893 | R-514A | 189.8 | 85.27 | 70.57 | 34.6608
11894 | R-514A | 189.9 | 85.39 | 70.69 | 34.7197
11895 | R-514A | 190 | 85.51 | 70.81 | 34.7786
11896 | R-514A | 190.1 | 85.62 | 70.92 | 34.8327
11897 | R-514A | 190.2 | 85.74 | 71.04 | 34.8916
11898 | R-514A | 190.3 | 85.86 | 71.16 | 34.9505
11899 | R-514A | 190.4 | 85.97 | 71.27 | 35.0046
11900 | R-514A | 190.5 | 86.09 | 71.39 | 35.0635
11901 | R-514A | 190.6 | 86.21 | 71.51 | 35.1224
11902 | R-514A | 190.7 | 86.32 | 71.62 | 35.1765
11903 | R-514A | 190.8 | 86.44 | 71.74 | 35.2354
11904 | R-514A | 190.9 | 86.56 | 71.86 | 35.2944
11905 | R-514A | 191 | 86.67 | 71.97 | 35.3484
11906 | R-514A | 191.1 | 86.79 | 72.09 | 35.4073
11907 | R-514A | 191.2 | 86.91 | 72.21 | 35.4663
11908 | R-514A | 191.3 | 87.03 | 72.33 | 35.5252
11909 | R-514A | 191.4 | 87.14 | 72.44 | 35.5792
11910 | R-514A | 191.5 | 87.26 | 72.56 | 35.6382
11911 | R-514A | 191.6 | 87.38 | 72.68 | 35.6971
11912 | R-514A | 191.7 | 87.5 | 72.8 | 35.756
11913 | R-514A | 191.8 | 87.62 | 72.92 | 35.815
11914 | R-514A | 191.9 | 87.73 | 73.03 | 35.869
11915 | R-514A | 192 | 87.85 | 73.15 | 35.9279
11916 | R-514A | 192.1 | 87.97 | 73.27 | 35.9869
11917 | R-514A | 192.2 | 88.09 | 73.39 | 36.0458
11918 | R-514A | 192.3 | 88.21 | 73.51 | 36.1048
11919 | R-514A | 192.4 | 88.33 | 73.63 | 36.1637
11920 | R-514A | 192.5 | 88.45 | 73.75 | 36.2226
11921 | R-514A | 192.6 | 88.57 | 73.87 | 36.2816
11922 | R-514A | 192.7 | 88.68 | 73.98 | 36.3356
11923 | R-514A | 192.8 | 88.8 | 74.1 | 36.3945
11924 | R-514A | 192.9 | 88.92 | 74.22 | 36.4535
11925 | R-514A | 193 | 89.04 | 74.34 | 36.5124
11926 | R-514A | 193.1 | 89.16 | 74.46 | 36.5714
11927 | R-514A | 193.2 | 89.28 | 74.58 | 36.6303
11928 | R-514A | 193.3 | 89.4 | 74.7 | 36.6892
11929 | R-514A | 193.4 | 89.52 | 74.82 | 36.7482
11930 | R-514A | 193.5 | 89.64 | 74.94 | 36.8071
11931 | R-514A | 193.6 | 89.76 | 75.06 | 36.866
11932 | R-514A | 193.7 | 89.88 | 75.18 | 36.925
11933 | R-514A | 193.8 | 90 | 75.3 | 36.9839
11934 | R-514A | 193.9 | 90.12 | 75.42 | 37.0429
11935 | R-514A | 194 | 90.25 | 75.55 | 37.1067
11936 | R-514A | 194.1 | 90.37 | 75.67 | 37.1656
11937 | R-514A | 194.2 | 90.49 | 75.79 | 37.2246
11938 | R-514A | 194.3 | 90.61 | 75.91 | 37.2835
11939 | R-514A | 194.4 | 90.73 | 76.03 | 37.3425
11940 | R-514A | 194.5 | 90.85 | 76.15 | 37.4014
11941 | R-514A | 194.6 | 90.97 | 76.27 | 37.4603
11942 | R-514A | 194.7 | 91.1 | 76.4 | 37.5242
11943 | R-514A | 194.8 | 91.22 | 76.52 | 37.5831
11944 | R-514A | 194.9 | 91.34 | 76.64 | 37.6421
11945 | R-514A | 195 | 91.46 | 76.76 | 37.701
11946 | R-514A | 195.1 | 91.58 | 76.88 | 37.7599
11947 | R-514A | 195.2 | 91.71 | 77.01 | 37.8238
11948 | R-514A | 195.3 | 91.83 | 77.13 | 37.8827
11949 | R-514A | 195.4 | 91.95 | 77.25 | 37.9417
11950 | R-514A | 195.5 | 92.07 | 77.37 | 38.0006
11951 | R-514A | 195.6 | 92.2 | 77.5 | 38.0645
11952 | R-514A | 195.7 | 92.32 | 77.62 | 38.1234
11953 | R-514A | 195.8 | 92.44 | 77.74 | 38.1823
11954 | R-514A | 195.9 | 92.57 | 77.87 | 38.2462
11955 | R-514A | 196 | 92.69 | 77.99 | 38.3051
11956 | R-514A | 196.1 | 92.81 | 78.11 | 38.3641
11957 | R-514A | 196.2 | 92.94 | 78.24 | 38.4279
11958 | R-514A | 196.3 | 93.06 | 78.36 | 38.4868
11959 | R-514A | 196.4 | 93.18 | 78.48 | 38.5458
11960 | R-514A | 196.5 | 93.31 | 78.61 | 38.6096
11961 | R-514A | 196.6 | 93.43 | 78.73 | 38.6686
11962 | R-514A | 196.7 | 93.56 | 78.86 | 38.7324
11963 | R-514A | 196.8 | 93.68 | 78.98 | 38.7914
11964 | R-514A | 196.9 | 93.8 | 79.1 | 38.8503
11965 | R-514A | 197 | 93.93 | 79.23 | 38.9142
11966 | R-514A | 197.1 | 94.05 | 79.35 | 38.9731
11967 | R-514A | 197.2 | 94.18 | 79.48 | 39.0369
11968 | R-514A | 197.3 | 94.3 | 79.6 | 39.0959
11969 | R-514A | 197.4 | 94.43 | 79.73 | 39.1597
11970 | R-514A | 197.5 | 94.55 | 79.85 | 39.2187
11971 | R-514A | 197.6 | 94.68 | 79.98 | 39.2825
11972 | R-514A | 197.7 | 94.8 | 80.1 | 39.3415
11973 | R-514A | 197.8 | 94.93 | 80.23 | 39.4053
11974 | R-514A | 197.9 | 95.06 | 80.36 | 39.4692
11975 | R-514A | 198 | 95.18 | 80.48 | 39.5281
11976 | R-514A | 198.1 | 95.31 | 80.61 | 39.5919
11977 | R-514A | 198.2 | 95.43 | 80.73 | 39.6509
11978 | R-514A | 198.3 | 95.56 | 80.86 | 39.7147
11979 | R-514A | 198.4 | 95.69 | 80.99 | 39.7786
11980 | R-514A | 198.5 | 95.81 | 81.11 | 39.8375
11981 | R-514A | 198.6 | 95.94 | 81.24 | 39.9014
11982 | R-514A | 198.7 | 96.07 | 81.37 | 39.9652
11983 | R-514A | 198.8 | 96.19 | 81.49 | 40.0242
11984 | R-514A | 198.9 | 96.32 | 81.62 | 40.088
11985 | R-514A | 199 | 96.45 | 81.75 | 40.1519
11986 | R-514A | 199.1 | 96.57 | 81.87 | 40.2108
11987 | R-514A | 199.2 | 96.7 | 82 | 40.2747
11988 | R-514A | 199.3 | 96.83 | 82.13 | 40.3385
11989 | R-514A | 199.4 | 96.96 | 82.26 | 40.4023
11990 | R-514A | 199.5 | 97.08 | 82.38 | 40.4613
11991 | R-514A | 199.6 | 97.21 | 82.51 | 40.5251
11992 | R-514A | 199.7 | 97.34 | 82.64 | 40.589
11993 | R-514A | 199.8 | 97.47 | 82.77 | 40.6528
11994 | R-514A | 199.9 | 97.6 | 82.9 | 40.7167
11995 | R-514A | 200 | 97.72 | 83.02 | 40.7756
11996 | R-514A | 200.1 | 97.85 | 83.15 | 40.8395
11997 | R-514A | 200.2 | 97.98 | 83.28 | 40.9033
11998 | R-514A | 200.3 | 98.11 | 83.41 | 40.9672
11999 | R-514A | 200.4 | 98.24 | 83.54 | 41.031
12000 | R-514A | 200.5 | 98.37 | 83.67 | 41.0949
12001 | R-514A | 200.6 | 98.5 | 83.8 | 41.1587
12002 | R-514A | 200.7 | 98.63 | 83.93 | 41.2226
12003 | R-514A | 200.8 | 98.76 | 84.06 | 41.2864
12004 | R-514A | 200.9 | 98.88 | 84.18 | 41.3454
12005 | R-514A | 201 | 99.01 | 84.31 | 41.4092
12006 | R-514A | 201.1 | 99.14 | 84.44 | 41.4731
12007 | R-514A | 201.2 | 99.27 | 84.57 | 41.5369
12008 | R-514A | 201.3 | 99.4 | 84.7 | 41.6008
12009 | R-514A | 201.4 | 99.53 | 84.83 | 41.6646
12010 | R-514A | 201.5 | 99.66 | 84.96 | 41.7285
12011 | R-514A | 201.6 | 99.8 | 85.1 | 41.7972
12012 | R-514A | 201.7 | 99.93 | 85.23 | 41.8611
12013 | R-514A | 201.8 | 100.06 | 85.36 | 41.9249
12014 | R-514A | 201.9 | 100.19 | 85.49 | 41.9888
12015 | R-514A | 202 | 100.32 | 85.62 | 42.0526
12016 | R-514A | 202.1 | 100.45 | 85.75 | 42.1165
12017 | R-514A | 202.2 | 100.58 | 85.88 | 42.1803
12018 | R-514A | 202.3 | 100.71 | 86.01 | 42.2442
12019 | R-514A | 202.4 | 100.84 | 86.14 | 42.308
12020 | R-514A | 202.5 | 100.97 | 86.27 | 42.3719
12021 | R-514A | 202.6 | 101.11 | 86.41 | 42.4406
12022 | R-514A | 202.7 | 101.24 | 86.54 | 42.5045
12023 | R-514A | 202.8 | 101.37 | 86.67 | 42.5683
12024 | R-514A | 202.9 | 101.5 | 86.8 | 42.6322
12025 | R-514A | 203 | 101.63 | 86.93 | 42.696
12026 | R-514A | 203.1 | 101.77 | 87.07 | 42.7648
12027 | R-514A | 203.2 | 101.9 | 87.2 | 42.8287
12028 | R-514A | 203.3 | 102.03 | 87.33 | 42.8925
12029 | R-514A | 203.4 | 102.16 | 87.46 | 42.9564
12030 | R-514A | 203.5 | 102.3 | 87.6 | 43.0251
12031 | R-514A | 203.6 | 102.43 | 87.73 | 43.089
12032 | R-514A | 203.7 | 102.56 | 87.86 | 43.1528
12033 | R-514A | 203.8 | 102.7 | 88 | 43.2216
12034 | R-514A | 203.9 | 102.83 | 88.13 | 43.2854
12035 | R-514A | 204 | 102.96 | 88.26 | 43.3493
12036 | R-514A | 204.1 | 103.1 | 88.4 | 43.418
12037 | R-514A | 204.2 | 103.23 | 88.53 | 43.4819
12038 | R-514A | 204.3 | 103.36 | 88.66 | 43.5457
12039 | R-514A | 204.4 | 103.5 | 88.8 | 43.6145
12040 | R-514A | 204.5 | 103.63 | 88.93 | 43.6784
12041 | R-514A | 204.6 | 103.77 | 89.07 | 43.7471
12042 | R-514A | 204.7 | 103.9 | 89.2 | 43.811
12043 | R-514A | 204.8 | 104.04 | 89.34 | 43.8797
12044 | R-514A | 204.9 | 104.17 | 89.47 | 43.9436
12045 | R-514A | 205 | 104.3 | 89.6 | 44.0074
12046 | R-514A | 205.1 | 104.44 | 89.74 | 44.0762
12047 | R-514A | 205.2 | 104.57 | 89.87 | 44.14
12048 | R-514A | 205.3 | 104.71 | 90.01 | 44.2088
12049 | R-514A | 205.4 | 104.85 | 90.15 | 44.2776
12050 | R-514A | 205.5 | 104.98 | 90.28 | 44.3414
12051 | R-514A | 205.6 | 105.12 | 90.42 | 44.4102
12052 | R-514A | 205.7 | 105.25 | 90.55 | 44.474
12053 | R-514A | 205.8 | 105.39 | 90.69 | 44.5428
12054 | R-514A | 205.9 | 105.52 | 90.82 | 44.6066
12055 | R-514A | 206 | 105.66 | 90.96 | 44.6754
12056 | R-514A | 206.1 | 105.8 | 91.1 | 44.7442
12057 | R-514A | 206.2 | 105.93 | 91.23 | 44.808
12058 | R-514A | 206.3 | 106.07 | 91.37 | 44.8768
12059 | R-514A | 206.4 | 106.21 | 91.51 | 44.9455
12060 | R-514A | 206.5 | 106.34 | 91.64 | 45.0094
12061 | R-514A | 206.6 | 106.48 | 91.78 | 45.0781
12062 | R-514A | 206.7 | 106.62 | 91.92 | 45.1469
12063 | R-514A | 206.8 | 106.75 | 92.05 | 45.2107
12064 | R-514A | 206.9 | 106.89 | 92.19 | 45.2795
12065 | R-514A | 207 | 107.03 | 92.33 | 45.3483
12066 | R-514A | 207.1 | 107.17 | 92.47 | 45.417
12067 | R-514A | 207.2 | 107.3 | 92.6 | 45.4809
12068 | R-514A | 207.3 | 107.44 | 92.74 | 45.5496
12069 | R-514A | 207.4 | 107.58 | 92.88 | 45.6184
12070 | R-514A | 207.5 | 107.72 | 93.02 | 45.6872
12071 | R-514A | 207.6 | 107.86 | 93.16 | 45.7559
12072 | R-514A | 207.7 | 107.99 | 93.29 | 45.8198
12073 | R-514A | 207.8 | 108.13 | 93.43 | 45.8886
12074 | R-514A | 207.9 | 108.27 | 93.57 | 45.9573
12075 | R-514A | 208 | 108.41 | 93.71 | 46.0261
12076 | R-514A | 208.1 | 108.55 | 93.85 | 46.0948
12077 | R-514A | 208.2 | 108.69 | 93.99 | 46.1636
12078 | R-514A | 208.3 | 108.83 | 94.13 | 46.2324
12079 | R-514A | 208.4 | 108.97 | 94.27 | 46.3011
12080 | R-514A | 208.5 | 109.11 | 94.41 | 46.3699
12081 | R-514A | 208.6 | 109.25 | 94.55 | 46.4386
12082 | R-514A | 208.7 | 109.39 | 94.69 | 46.5074
12083 | R-514A | 208.8 | 109.53 | 94.83 | 46.5762
12084 | R-514A | 208.9 | 109.67 | 94.97 | 46.6449
12085 | R-514A | 209 | 109.8 | 95.1 | 46.7088
12086 | R-514A | 209.1 | 109.95 | 95.25 | 46.7824
12087 | R-514A | 209.2 | 110.09 | 95.39 | 46.8512
12088 | R-514A | 209.3 | 110.23 | 95.53 | 46.92
12089 | R-514A | 209.4 | 110.37 | 95.67 | 46.9887
12090 | R-514A | 209.5 | 110.51 | 95.81 | 47.0575
12091 | R-514A | 209.6 | 110.65 | 95.95 | 47.1263
12092 | R-514A | 209.7 | 110.79 | 96.09 | 47.195
12093 | R-514A | 209.8 | 110.93 | 96.23 | 47.2638
12094 | R-514A | 209.9 | 111.07 | 96.37 | 47.3325
12095 | R-514A | 210 | 111.21 | 96.51 | 47.4013
12096 | R-514A | 210.1 | 111.36 | 96.66 | 47.475
12097 | R-514A | 210.2 | 111.5 | 96.8 | 47.5437
12098 | R-514A | 210.3 | 111.64 | 96.94 | 47.6125
12099 | R-514A | 210.4 | 111.78 | 97.08 | 47.6813
12100 | R-514A | 210.5 | 111.92 | 97.22 | 47.75
12101 | R-514A | 210.6 | 112.07 | 97.37 | 47.8237
12102 | R-514A | 210.7 | 112.21 | 97.51 | 47.8925
12103 | R-514A | 210.8 | 112.35 | 97.65 | 47.9612
12104 | R-514A | 210.9 | 112.49 | 97.79 | 48.03
12105 | R-514A | 211 | 112.64 | 97.94 | 48.1037
12106 | R-514A | 211.1 | 112.78 | 98.08 | 48.1724
12107 | R-514A | 211.2 | 112.92 | 98.22 | 48.2412
12108 | R-514A | 211.3 | 113.07 | 98.37 | 48.3148
12109 | R-514A | 211.4 | 113.21 | 98.51 | 48.3836
12110 | R-514A | 211.5 | 113.35 | 98.65 | 48.4524
12111 | R-514A | 211.6 | 113.5 | 98.8 | 48.526
12112 | R-514A | 211.7 | 113.64 | 98.94 | 48.5948
12113 | R-514A | 211.8 | 113.78 | 99.08 | 48.6636
12114 | R-514A | 211.9 | 113.93 | 99.23 | 48.7372
12115 | R-514A | 212 | 114.07 | 99.37 | 48.806
12116 | R-514A | 212.1 | 114.22 | 99.52 | 48.8797
12117 | R-514A | 212.2 | 114.36 | 99.66 | 48.9484
12118 | R-514A | 212.3 | 114.51 | 99.81 | 49.0221
12119 | R-514A | 212.4 | 114.65 | 99.95 | 49.0909
12120 | R-514A | 212.5 | 114.8 | 100.1 | 49.1645
12121 | R-514A | 212.6 | 114.94 | 100.24 | 49.2333
12122 | R-514A | 212.7 | 115.09 | 100.39 | 49.307
12123 | R-514A | 212.8 | 115.23 | 100.53 | 49.3757
12124 | R-514A | 212.9 | 115.38 | 100.68 | 49.4494
12125 | R-514A | 213 | 115.52 | 100.82 | 49.5182
12126 | R-514A | 213.1 | 115.67 | 100.97 | 49.5919
12127 | R-514A | 213.2 | 115.81 | 101.11 | 49.6606
12128 | R-514A | 213.3 | 115.96 | 101.26 | 49.7343
12129 | R-514A | 213.4 | 116.11 | 101.41 | 49.808
12130 | R-514A | 213.5 | 116.25 | 101.55 | 49.8767
12131 | R-514A | 213.6 | 116.4 | 101.7 | 49.9504
12132 | R-514A | 213.7 | 116.55 | 101.85 | 50.0241
12133 | R-514A | 213.8 | 116.69 | 101.99 | 50.0928
12134 | R-514A | 213.9 | 116.84 | 102.14 | 50.1665
12135 | R-514A | 214 | 116.98 | 102.28 | 50.2353
12136 | R-514A | 214.1 | 117.13 | 102.43 | 50.3089
12137 | R-514A | 214.2 | 117.28 | 102.58 | 50.3826
12138 | R-514A | 214.3 | 117.43 | 102.73 | 50.4563
12139 | R-514A | 214.4 | 117.58 | 102.88 | 50.53
12140 | R-514A | 214.5 | 117.72 | 103.02 | 50.5987
12141 | R-514A | 214.6 | 117.87 | 103.17 | 50.6724
12142 | R-514A | 214.7 | 118.02 | 103.32 | 50.7461
12143 | R-514A | 214.8 | 118.17 | 103.47 | 50.8197
12144 | R-514A | 214.9 | 118.31 | 103.61 | 50.8885
12145 | R-514A | 215 | 118.46 | 103.76 | 50.9622
12146 | R-514A | 215.1 | 118.61 | 103.91 | 51.0358
12147 | R-514A | 215.2 | 118.76 | 104.06 | 51.1095
12148 | R-514A | 215.3 | 118.91 | 104.21 | 51.1832
12149 | R-514A | 215.4 | 119.06 | 104.36 | 51.2569
12150 | R-514A | 215.5 | 119.21 | 104.51 | 51.3305
12151 | R-514A | 215.6 | 119.36 | 104.66 | 51.4042
12152 | R-514A | 215.7 | 119.51 | 104.81 | 51.4779
12153 | R-514A | 215.8 | 119.66 | 104.96 | 51.5516
12154 | R-514A | 215.9 | 119.8 | 105.1 | 51.6203
12155 | R-514A | 216 | 119.95 | 105.25 | 51.694
12156 | R-514A | 216.1 | 120.1 | 105.4 | 51.7677
12157 | R-514A | 216.2 | 120.26 | 105.56 | 51.8462
12158 | R-514A | 216.3 | 120.41 | 105.71 | 51.9199
12159 | R-514A | 216.4 | 120.56 | 105.86 | 51.9936
12160 | R-514A | 216.5 | 120.71 | 106.01 | 52.0673
12161 | R-514A | 216.6 | 120.86 | 106.16 | 52.1409
12162 | R-514A | 216.7 | 121.01 | 106.31 | 52.2146
12163 | R-514A | 216.8 | 121.16 | 106.46 | 52.2883
12164 | R-514A | 216.9 | 121.31 | 106.61 | 52.362
12165 | R-514A | 217 | 121.46 | 106.76 | 52.4356
12166 | R-514A | 217.1 | 121.61 | 106.91 | 52.5093
12167 | R-514A | 217.2 | 121.76 | 107.06 | 52.583
12168 | R-514A | 217.3 | 121.92 | 107.22 | 52.6616
12169 | R-514A | 217.4 | 122.07 | 107.37 | 52.7352
12170 | R-514A | 217.5 | 122.22 | 107.52 | 52.8089
12171 | R-514A | 217.6 | 122.37 | 107.67 | 52.8826
12172 | R-514A | 217.7 | 122.52 | 107.82 | 52.9563
12173 | R-514A | 217.8 | 122.68 | 107.98 | 53.0348
12174 | R-514A | 217.9 | 122.83 | 108.13 | 53.1085
12175 | R-514A | 218 | 122.98 | 108.28 | 53.1822
12176 | R-514A | 218.1 | 123.13 | 108.43 | 53.2559
12177 | R-514A | 218.2 | 123.29 | 108.59 | 53.3344
12178 | R-514A | 218.3 | 123.44 | 108.74 | 53.4081
12179 | R-514A | 218.4 | 123.59 | 108.89 | 53.4818
12180 | R-514A | 218.5 | 123.75 | 109.05 | 53.5604
12181 | R-514A | 218.6 | 123.9 | 109.2 | 53.6341
12182 | R-514A | 218.7 | 124.05 | 109.35 | 53.7077
12183 | R-514A | 218.8 | 124.21 | 109.51 | 53.7863
12184 | R-514A | 218.9 | 124.36 | 109.66 | 53.86
12185 | R-514A | 219 | 124.51 | 109.81 | 53.9337
12186 | R-514A | 219.1 | 124.67 | 109.97 | 54.0122
12187 | R-514A | 219.2 | 124.82 | 110.12 | 54.0859
12188 | R-514A | 219.3 | 124.98 | 110.28 | 54.1645
12189 | R-514A | 219.4 | 125.13 | 110.43 | 54.2382
12190 | R-514A | 219.5 | 125.29 | 110.59 | 54.3168
12191 | R-514A | 219.6 | 125.44 | 110.74 | 54.3904
12192 | R-514A | 219.7 | 125.6 | 110.9 | 54.469
12193 | R-514A | 219.8 | 125.75 | 111.05 | 54.5427
12194 | R-514A | 219.9 | 125.91 | 111.21 | 54.6213
12195 | R-514A | 220 | 126.06 | 111.36 | 54.6949
12196 | R-514A | 220.1 | 126.22 | 111.52 | 54.7735
12197 | R-514A | 220.2 | 126.37 | 111.67 | 54.8472
12198 | R-514A | 220.3 | 126.53 | 111.83 | 54.9258
12199 | R-514A | 220.4 | 126.69 | 111.99 | 55.0044
12200 | R-514A | 220.5 | 126.84 | 112.14 | 55.078
12201 | R-514A | 220.6 | 127 | 112.3 | 55.1566
12202 | R-514A | 220.7 | 127.16 | 112.46 | 55.2352
12203 | R-514A | 220.8 | 127.31 | 112.61 | 55.3089
12204 | R-514A | 220.9 | 127.47 | 112.77 | 55.3875
12205 | R-514A | 221 | 127.63 | 112.93 | 55.4661
12206 | R-514A | 221.1 | 127.78 | 113.08 | 55.5397
12207 | R-514A | 221.2 | 127.94 | 113.24 | 55.6183
12208 | R-514A | 221.3 | 128.1 | 113.4 | 55.6969
12209 | R-514A | 221.4 | 128.26 | 113.56 | 55.7755
12210 | R-514A | 221.5 | 128.41 | 113.71 | 55.8492
12211 | R-514A | 221.6 | 128.57 | 113.87 | 55.9277
12212 | R-514A | 221.7 | 128.73 | 114.03 | 56.0063
12213 | R-514A | 221.8 | 128.89 | 114.19 | 56.0849
12214 | R-514A | 221.9 | 129.04 | 114.34 | 56.1586
12215 | R-514A | 222 | 129.2 | 114.5 | 56.2372
12216 | R-514A | 222.1 | 129.36 | 114.66 | 56.3158
12217 | R-514A | 222.2 | 129.52 | 114.82 | 56.3943
12218 | R-514A | 222.3 | 129.68 | 114.98 | 56.4729
12219 | R-514A | 222.4 | 129.84 | 115.14 | 56.5515
12220 | R-514A | 222.5 | 130 | 115.3 | 56.6301
12221 | R-514A | 222.6 | 130.16 | 115.46 | 56.7087
12222 | R-514A | 222.7 | 130.32 | 115.62 | 56.7873
12223 | R-514A | 222.8 | 130.48 | 115.78 | 56.8659
12224 | R-514A | 222.9 | 130.64 | 115.94 | 56.9444
12225 | R-514A | 223 | 130.79 | 116.09 | 57.0181
12226 | R-514A | 223.1 | 130.96 | 116.26 | 57.1016
12227 | R-514A | 223.2 | 131.12 | 116.42 | 57.1802
12228 | R-514A | 223.3 | 131.28 | 116.58 | 57.2588
12229 | R-514A | 223.4 | 131.44 | 116.74 | 57.3374
12230 | R-514A | 223.5 | 131.6 | 116.9 | 57.4159
12231 | R-514A | 223.6 | 131.76 | 117.06 | 57.4945
12232 | R-514A | 223.7 | 131.92 | 117.22 | 57.5731
12233 | R-514A | 223.8 | 132.08 | 117.38 | 57.6517
12234 | R-514A | 223.9 | 132.24 | 117.54 | 57.7303
12235 | R-514A | 224 | 132.4 | 117.7 | 57.8089
12236 | R-514A | 224.1 | 132.56 | 117.86 | 57.8875
12237 | R-514A | 224.2 | 132.73 | 118.03 | 57.9709
12238 | R-514A | 224.3 | 132.89 | 118.19 | 58.0495
12239 | R-514A | 224.4 | 133.05 | 118.35 | 58.1281
12240 | R-514A | 224.5 | 133.21 | 118.51 | 58.2067
12241 | R-514A | 224.6 | 133.37 | 118.67 | 58.2853
12242 | R-514A | 224.7 | 133.54 | 118.84 | 58.3688
12243 | R-514A | 224.8 | 133.7 | 119 | 58.4474
12244 | R-514A | 224.9 | 133.86 | 119.16 | 58.526
12245 | R-514A | 225 | 134.02 | 119.32 | 58.6045
12246 | R-514A | 225.1 | 134.19 | 119.49 | 58.688
12247 | R-514A | 225.2 | 134.35 | 119.65 | 58.7666
12248 | R-514A | 225.3 | 134.51 | 119.81 | 58.8452
12249 | R-514A | 225.4 | 134.68 | 119.98 | 58.9287
12250 | R-514A | 225.5 | 134.84 | 120.14 | 59.0073
12251 | R-514A | 225.6 | 135.01 | 120.31 | 59.0908
12252 | R-514A | 225.7 | 135.17 | 120.47 | 59.1694
12253 | R-514A | 225.8 | 135.33 | 120.63 | 59.2479
12254 | R-514A | 225.9 | 135.5 | 120.8 | 59.3314
12255 | R-514A | 226 | 135.66 | 120.96 | 59.41
12256 | R-514A | 226.1 | 135.83 | 121.13 | 59.4935
12257 | R-514A | 226.2 | 135.99 | 121.29 | 59.5721
12258 | R-514A | 226.3 | 136.16 | 121.46 | 59.6556
12259 | R-514A | 226.4 | 136.32 | 121.62 | 59.7342
12260 | R-514A | 226.5 | 136.49 | 121.79 | 59.8177
12261 | R-514A | 226.6 | 136.65 | 121.95 | 59.8963
12262 | R-514A | 226.7 | 136.82 | 122.12 | 59.9798
12263 | R-514A | 226.8 | 136.98 | 122.28 | 60.0583
12264 | R-514A | 226.9 | 137.15 | 122.45 | 60.1418
12265 | R-514A | 227 | 137.31 | 122.61 | 60.2204
12266 | R-514A | 227.1 | 137.48 | 122.78 | 60.3039
12267 | R-514A | 227.2 | 137.65 | 122.95 | 60.3874
12268 | R-514A | 227.3 | 137.81 | 123.11 | 60.466
12269 | R-514A | 227.4 | 137.98 | 123.28 | 60.5495
12270 | R-514A | 227.5 | 138.15 | 123.45 | 60.633
12271 | R-514A | 227.6 | 138.31 | 123.61 | 60.7116
12272 | R-514A | 227.7 | 138.48 | 123.78 | 60.7951
12273 | R-514A | 227.8 | 138.65 | 123.95 | 60.8786
12274 | R-514A | 227.9 | 138.81 | 124.11 | 60.9572
12275 | R-514A | 228 | 138.98 | 124.28 | 61.0407
12276 | R-514A | 228.1 | 139.15 | 124.45 | 61.1242
12277 | R-514A | 228.2 | 139.32 | 124.62 | 61.2077
12278 | R-514A | 228.3 | 139.48 | 124.78 | 61.2862
12279 | R-514A | 228.4 | 139.65 | 124.95 | 61.3697
12280 | R-514A | 228.5 | 139.82 | 125.12 | 61.4532
12281 | R-514A | 228.6 | 139.99 | 125.29 | 61.5367
12282 | R-514A | 228.7 | 140.16 | 125.46 | 61.6202
12283 | R-514A | 228.8 | 140.32 | 125.62 | 61.6988
12284 | R-514A | 228.9 | 140.49 | 125.79 | 61.7823
12285 | R-514A | 229 | 140.66 | 125.96 | 61.8658
12286 | R-514A | 229.1 | 140.83 | 126.13 | 61.9493
12287 | R-514A | 229.2 | 141 | 126.3 | 62.0328
12288 | R-514A | 229.3 | 141.17 | 126.47 | 62.1163
12289 | R-514A | 229.4 | 141.34 | 126.64 | 62.1998
12290 | R-514A | 229.5 | 141.51 | 126.81 | 62.2833
12291 | R-514A | 229.6 | 141.68 | 126.98 | 62.3668
12292 | R-514A | 229.7 | 141.85 | 127.15 | 62.4503
12293 | R-514A | 229.8 | 142.02 | 127.32 | 62.5338
12294 | R-514A | 229.9 | 142.19 | 127.49 | 62.6173
12295 | R-514A | 230 | 142.36 | 127.66 | 62.7008
12296 | R-514A | 230.1 | 142.53 | 127.83 | 62.7843
12297 | R-514A | 230.2 | 142.7 | 128 | 62.8678
12298 | R-514A | 230.3 | 142.87 | 128.17 | 62.9513
12299 | R-514A | 230.4 | 143.04 | 128.34 | 63.0347
12300 | R-514A | 230.5 | 143.21 | 128.51 | 63.1182
12301 | R-514A | 230.6 | 143.39 | 128.69 | 63.2067
12302 | R-514A | 230.7 | 143.56 | 128.86 | 63.2901
12303 | R-514A | 230.8 | 143.73 | 129.03 | 63.3736
12304 | R-514A | 230.9 | 143.9 | 129.2 | 63.4571
12305 | R-514A | 231 | 144.07 | 129.37 | 63.5406
12306 | R-514A | 231.1 | 144.24 | 129.54 | 63.6241
12307 | R-514A | 231.2 | 144.42 | 129.72 | 63.7125
12308 | R-514A | 231.3 | 144.59 | 129.89 | 63.796
12309 | R-514A | 231.4 | 144.76 | 130.06 | 63.8795
12310 | R-514A | 231.5 | 144.93 | 130.23 | 63.963
12311 | R-514A | 231.6 | 145.11 | 130.41 | 64.0514
12312 | R-514A | 231.7 | 145.28 | 130.58 | 64.1349
12313 | R-514A | 231.8 | 145.45 | 130.75 | 64.2184
12314 | R-514A | 231.9 | 145.63 | 130.93 | 64.3068
12315 | R-514A | 232 | 145.8 | 131.1 | 64.3903
12316 | R-514A | 232.1 | 145.97 | 131.27 | 64.4738
12317 | R-514A | 232.2 | 146.15 | 131.45 | 64.5622
12318 | R-514A | 232.3 | 146.32 | 131.62 | 64.6457
12319 | R-514A | 232.4 | 146.5 | 131.8 | 64.7341
12320 | R-514A | 232.5 | 146.67 | 131.97 | 64.8176
12321 | R-514A | 232.6 | 146.85 | 132.15 | 64.906
12322 | R-514A | 232.7 | 147.02 | 132.32 | 64.9895
12323 | R-514A | 232.8 | 147.19 | 132.49 | 65.073
12324 | R-514A | 232.9 | 147.37 | 132.67 | 65.1614
12325 | R-514A | 233 | 147.54 | 132.84 | 65.2449
12326 | R-514A | 233.1 | 147.72 | 133.02 | 65.3333
12327 | R-514A | 233.2 | 147.89 | 133.19 | 65.4168
12328 | R-514A | 233.3 | 148.07 | 133.37 | 65.5053
12329 | R-514A | 233.4 | 148.25 | 133.55 | 65.5937
12330 | R-514A | 233.5 | 148.42 | 133.72 | 65.6771
12331 | R-514A | 233.6 | 148.6 | 133.9 | 65.7656
12332 | R-514A | 233.7 | 148.77 | 134.07 | 65.8491
12333 | R-514A | 233.8 | 148.95 | 134.25 | 65.9375
12334 | R-514A | 233.9 | 149.13 | 134.43 | 66.0259
12335 | R-514A | 234 | 149.3 | 134.6 | 66.1094
12336 | R-514A | 234.1 | 149.48 | 134.78 | 66.1978
12337 | R-514A | 234.2 | 149.66 | 134.96 | 66.2862
12338 | R-514A | 234.3 | 149.83 | 135.13 | 66.3697
12339 | R-514A | 234.4 | 150.01 | 135.31 | 66.4581
12340 | R-514A | 234.5 | 150.19 | 135.49 | 66.5465
12341 | R-514A | 234.6 | 150.37 | 135.67 | 66.6349
12342 | R-514A | 234.7 | 150.54 | 135.84 | 66.7184
12343 | R-514A | 234.8 | 150.72 | 136.02 | 66.8068
12344 | R-514A | 234.9 | 150.9 | 136.2 | 66.8952
12345 | R-514A | 235 | 151.08 | 136.38 | 66.9836
12346 | R-514A | 235.1 | 151.26 | 136.56 | 67.072
12347 | R-514A | 235.2 | 151.44 | 136.74 | 67.1604
12348 | R-514A | 235.3 | 151.61 | 136.91 | 67.2439
12349 | R-514A | 235.4 | 151.79 | 137.09 | 67.3323
12350 | R-514A | 235.5 | 151.97 | 137.27 | 67.4207
12351 | R-514A | 235.6 | 152.15 | 137.45 | 67.5092
12352 | R-514A | 235.7 | 152.33 | 137.63 | 67.5976
12353 | R-514A | 235.8 | 152.51 | 137.81 | 67.686
12354 | R-514A | 235.9 | 152.69 | 137.99 | 67.7744
12355 | R-514A | 236 | 152.87 | 138.17 | 67.8628
12356 | R-514A | 236.1 | 153.05 | 138.35 | 67.9512
12357 | R-514A | 236.2 | 153.23 | 138.53 | 68.0396
12358 | R-514A | 236.3 | 153.41 | 138.71 | 68.128
12359 | R-514A | 236.4 | 153.59 | 138.89 | 68.2164
12360 | R-514A | 236.5 | 153.77 | 139.07 | 68.3048
12361 | R-514A | 236.6 | 153.95 | 139.25 | 68.3932
12362 | R-514A | 236.7 | 154.13 | 139.43 | 68.4817
12363 | R-514A | 236.8 | 154.31 | 139.61 | 68.57
12364 | R-514A | 236.9 | 154.49 | 139.79 | 68.6585
12365 | R-514A | 237 | 154.68 | 139.98 | 68.7518
12366 | R-514A | 237.1 | 154.86 | 140.16 | 68.8402
12367 | R-514A | 237.2 | 155.04 | 140.34 | 68.9286
12368 | R-514A | 237.3 | 155.22 | 140.52 | 69.017
12369 | R-514A | 237.4 | 155.4 | 140.7 | 69.1054
12370 | R-514A | 237.5 | 155.59 | 140.89 | 69.1987
12371 | R-514A | 237.6 | 155.77 | 141.07 | 69.2871
12372 | R-514A | 237.7 | 155.95 | 141.25 | 69.3756
12373 | R-514A | 237.8 | 156.13 | 141.43 | 69.4639
12374 | R-514A | 237.9 | 156.32 | 141.62 | 69.5573
12375 | R-514A | 238 | 156.5 | 141.8 | 69.6457
12376 | R-514A | 238.1 | 156.68 | 141.98 | 69.7341
12377 | R-514A | 238.2 | 156.87 | 142.17 | 69.8274
12378 | R-514A | 238.3 | 157.05 | 142.35 | 69.9158
12379 | R-514A | 238.4 | 157.23 | 142.53 | 70.0042
12380 | R-514A | 238.5 | 157.42 | 142.72 | 70.0975
12381 | R-514A | 238.6 | 157.6 | 142.9 | 70.186
12382 | R-514A | 238.7 | 157.79 | 143.09 | 70.2793
12383 | R-514A | 238.8 | 157.97 | 143.27 | 70.3677
12384 | R-514A | 238.9 | 158.15 | 143.45 | 70.4561
12385 | R-514A | 239 | 158.34 | 143.64 | 70.5494
12386 | R-514A | 239.1 | 158.52 | 143.82 | 70.6378
12387 | R-514A | 239.2 | 158.71 | 144.01 | 70.7311
12388 | R-514A | 239.3 | 158.89 | 144.19 | 70.8195
12389 | R-514A | 239.4 | 159.08 | 144.38 | 70.9129
12390 | R-514A | 239.5 | 159.27 | 144.57 | 71.0062
12391 | R-514A | 239.6 | 159.45 | 144.75 | 71.0946
12392 | R-514A | 239.7 | 159.64 | 144.94 | 71.1879
12393 | R-514A | 239.8 | 159.82 | 145.12 | 71.2763
12394 | R-514A | 239.9 | 160.01 | 145.31 | 71.3696
12395 | R-514A | 240 | 160.19 | 145.49 | 71.458
12396 | R-514A | 240.1 | 160.38 | 145.68 | 71.5514
12397 | R-514A | 240.2 | 160.57 | 145.87 | 71.6447
12398 | R-514A | 240.3 | 160.76 | 146.06 | 71.738
12399 | R-514A | 240.4 | 160.94 | 146.24 | 71.8264
12400 | R-514A | 240.5 | 161.13 | 146.43 | 71.9197
12401 | R-514A | 240.6 | 161.32 | 146.62 | 72.0131
12402 | R-514A | 240.7 | 161.5 | 146.8 | 72.1014
12403 | R-514A | 240.8 | 161.69 | 146.99 | 72.1948
12404 | R-514A | 240.9 | 161.88 | 147.18 | 72.2881
12405 | R-514A | 241 | 162.07 | 147.37 | 72.3814
12406 | R-514A | 241.1 | 162.25 | 147.55 | 72.4698
12407 | R-514A | 241.2 | 162.44 | 147.74 | 72.5631
12408 | R-514A | 241.3 | 162.63 | 147.93 | 72.6565
12409 | R-514A | 241.4 | 162.82 | 148.12 | 72.7498
12410 | R-514A | 241.5 | 163.01 | 148.31 | 72.8431
12411 | R-514A | 241.6 | 163.2 | 148.5 | 72.9364
12412 | R-514A | 241.7 | 163.39 | 148.69 | 73.0297
12413 | R-514A | 241.8 | 163.58 | 148.88 | 73.1231
12414 | R-514A | 241.9 | 163.77 | 149.07 | 73.2164
12415 | R-514A | 242 | 163.95 | 149.25 | 73.3048
12416 | R-514A | 242.1 | 164.14 | 149.44 | 73.3981
12417 | R-514A | 242.2 | 164.34 | 149.64 | 73.4963
12418 | R-514A | 242.3 | 164.53 | 149.83 | 73.5897
12419 | R-514A | 242.4 | 164.72 | 150.02 | 73.683
12420 | R-514A | 242.5 | 164.91 | 150.21 | 73.7763
12421 | R-514A | 242.6 | 165.1 | 150.4 | 73.8696
12422 | R-514A | 242.7 | 165.29 | 150.59 | 73.9629
12423 | R-514A | 242.8 | 165.48 | 150.78 | 74.0563
12424 | R-514A | 242.9 | 165.67 | 150.97 | 74.1496
12425 | R-514A | 243 | 165.86 | 151.16 | 74.2429
12426 | R-514A | 243.1 | 166.05 | 151.35 | 74.3362
12427 | R-514A | 243.2 | 166.24 | 151.54 | 74.4295
12428 | R-514A | 243.3 | 166.44 | 151.74 | 74.5278
12429 | R-514A | 243.4 | 166.63 | 151.93 | 74.6211
12430 | R-514A | 243.5 | 166.82 | 152.12 | 74.7144
12431 | R-514A | 243.6 | 167.01 | 152.31 | 74.8077
12432 | R-514A | 243.7 | 167.2 | 152.5 | 74.901
12433 | R-514A | 243.8 | 167.4 | 152.7 | 74.9993
12434 | R-514A | 243.9 | 167.59 | 152.89 | 75.0926
12435 | R-514A | 244 | 167.78 | 153.08 | 75.1859
12436 | R-514A | 244.1 | 167.97 | 153.27 | 75.2792
12437 | R-514A | 244.2 | 168.17 | 153.47 | 75.3774
12438 | R-514A | 244.3 | 168.36 | 153.66 | 75.4708
12439 | R-514A | 244.4 | 168.56 | 153.86 | 75.569
12440 | R-514A | 244.5 | 168.75 | 154.05 | 75.6623
12441 | R-514A | 244.6 | 168.94 | 154.24 | 75.7556
12442 | R-514A | 244.7 | 169.14 | 154.44 | 75.8539
12443 | R-514A | 244.8 | 169.33 | 154.63 | 75.9472
12444 | R-514A | 244.9 | 169.53 | 154.83 | 76.0454
12445 | R-514A | 245 | 169.72 | 155.02 | 76.1387
12446 | R-514A | 245.1 | 169.91 | 155.21 | 76.2321
12447 | R-514A | 245.2 | 170.11 | 155.41 | 76.3303
12448 | R-514A | 245.3 | 170.31 | 155.61 | 76.4285
12449 | R-514A | 245.4 | 170.5 | 155.8 | 76.5218
12450 | R-514A | 245.5 | 170.7 | 156 | 76.6201
12451 | R-514A | 245.6 | 170.89 | 156.19 | 76.7134
12452 | R-514A | 245.7 | 171.09 | 156.39 | 76.8116
12453 | R-514A | 245.8 | 171.28 | 156.58 | 76.9049
12454 | R-514A | 245.9 | 171.48 | 156.78 | 77.0032
12455 | R-514A | 246 | 171.67 | 156.97 | 77.0965
12456 | R-514A | 246.1 | 171.87 | 157.17 | 77.1947
12457 | R-514A | 246.2 | 172.07 | 157.37 | 77.293
12458 | R-514A | 246.3 | 172.27 | 157.57 | 77.3912
12459 | R-514A | 246.4 | 172.46 | 157.76 | 77.4845
12460 | R-514A | 246.5 | 172.66 | 157.96 | 77.5827
12461 | R-514A | 246.6 | 172.86 | 158.16 | 77.681
12462 | R-514A | 246.7 | 173.06 | 158.36 | 77.7792
12463 | R-514A | 246.8 | 173.25 | 158.55 | 77.8725
12464 | R-514A | 246.9 | 173.45 | 158.75 | 77.9707
12465 | R-514A | 247 | 173.65 | 158.95 | 78.069
12466 | R-514A | 247.1 | 173.85 | 159.15 | 78.1672
12467 | R-514A | 247.2 | 174.04 | 159.34 | 78.2605
12468 | R-514A | 247.3 | 174.24 | 159.54 | 78.3588
12469 | R-514A | 247.4 | 174.44 | 159.74 | 78.457
12470 | R-514A | 247.5 | 174.64 | 159.94 | 78.5552
12471 | R-514A | 247.6 | 174.84 | 160.14 | 78.6535
12472 | R-514A | 247.7 | 175.04 | 160.34 | 78.7517
12473 | R-514A | 247.8 | 175.24 | 160.54 | 78.8499
12474 | R-514A | 247.9 | 175.44 | 160.74 | 78.9481
12475 | R-514A | 248 | 175.64 | 160.94 | 79.0464
12476 | R-514A | 248.1 | 175.84 | 161.14 | 79.1446
12477 | R-514A | 248.2 | 176.04 | 161.34 | 79.2428
12478 | R-514A | 248.3 | 176.24 | 161.54 | 79.3411
12479 | R-514A | 248.4 | 176.44 | 161.74 | 79.4393
12480 | R-514A | 248.5 | 176.64 | 161.94 | 79.5375
12481 | R-514A | 248.6 | 176.84 | 162.14 | 79.6358
12482 | R-514A | 248.7 | 177.04 | 162.34 | 79.734
12483 | R-514A | 248.8 | 177.24 | 162.54 | 79.8322
12484 | R-514A | 248.9 | 177.44 | 162.74 | 79.9304
12485 | R-514A | 249 | 177.64 | 162.94 | 80.0287
12486 | R-514A | 249.1 | 177.85 | 163.15 | 80.1318
12487 | R-514A | 249.2 | 178.05 | 163.35 | 80.2301
12488 | R-514A | 249.3 | 178.25 | 163.55 | 80.3283
12489 | R-514A | 249.4 | 178.45 | 163.75 | 80.4265
12490 | R-514A | 249.5 | 178.65 | 163.95 | 80.5247
12491 | R-514A | 249.6 | 178.86 | 164.16 | 80.6279
12492 | R-514A | 249.7 | 179.06 | 164.36 | 80.7261
12493 | R-514A | 249.8 | 179.26 | 164.56 | 80.8243
12494 | R-514A | 249.9 | 179.46 | 164.76 | 80.9226
12495 | R-514A | 250 | 179.67 | 164.97 | 81.0257
12496 | R-514A | 250.1 | 179.87 | 165.17 | 81.124
12497 | R-514A | 250.2 | 180.07 | 165.37 | 81.2222
12498 | R-514A | 250.3 | 180.28 | 165.58 | 81.3253
12499 | R-514A | 250.4 | 180.48 | 165.78 | 81.4236
12500 | R-514A | 250.5 | 180.69 | 165.99 | 81.5267
12501 | R-514A | 250.6 | 180.89 | 166.19 | 81.6249
12502 | R-514A | 250.7 | 181.1 | 166.4 | 81.7281
12503 | R-514A | 250.8 | 181.3 | 166.6 | 81.8263
12504 | R-514A | 250.9 | 181.5 | 166.8 | 81.9245
12505 | R-514A | 251 | 181.71 | 167.01 | 82.0277
12506 | R-514A | 251.1 | 181.91 | 167.21 | 82.1259
12507 | R-514A | 251.2 | 182.12 | 167.42 | 82.2291
12508 | R-514A | 251.3 | 182.33 | 167.63 | 82.3322
12509 | R-514A | 251.4 | 182.53 | 167.83 | 82.4304
12510 | R-514A | 251.5 | 182.74 | 168.04 | 82.5336
12511 | R-514A | 251.6 | 182.94 | 168.24 | 82.6318
12512 | R-514A | 251.7 | 183.15 | 168.45 | 82.7349
12513 | R-514A | 251.8 | 183.35 | 168.65 | 82.8332
12514 | R-514A | 251.9 | 183.56 | 168.86 | 82.9363
12515 | R-514A | 252 | 183.77 | 169.07 | 83.0395
12516 | R-514A | 252.1 | 183.97 | 169.27 | 83.1377
12517 | R-514A | 252.2 | 184.18 | 169.48 | 83.2408
12518 | R-514A | 252.3 | 184.39 | 169.69 | 83.344
12519 | R-514A | 252.4 | 184.6 | 169.9 | 83.4471
12520 | R-514A | 252.5 | 184.8 | 170.1 | 83.5453
12521 | R-514A | 252.6 | 185.01 | 170.31 | 83.6485
12522 | R-514A | 252.7 | 185.22 | 170.52 | 83.7516
12523 | R-514A | 252.8 | 185.43 | 170.73 | 83.8548
12524 | R-514A | 252.9 | 185.64 | 170.94 | 83.9579
12525 | R-514A | 253 | 185.84 | 171.14 | 84.0562
12526 | R-514A | 253.1 | 186.05 | 171.35 | 84.1593
12527 | R-514A | 253.2 | 186.26 | 171.56 | 84.2624
12528 | R-514A | 253.3 | 186.47 | 171.77 | 84.3656
12529 | R-514A | 253.4 | 186.68 | 171.98 | 84.4687
12530 | R-514A | 253.5 | 186.89 | 172.19 | 84.5719
12531 | R-514A | 253.6 | 187.1 | 172.4 | 84.675
12532 | R-514A | 253.7 | 187.31 | 172.61 | 84.7781
12533 | R-514A | 253.8 | 187.52 | 172.82 | 84.8813
12534 | R-514A | 253.9 | 187.73 | 173.03 | 84.9844
12535 | R-514A | 254 | 187.94 | 173.24 | 85.0876
12536 | R-514A | 254.1 | 188.15 | 173.45 | 85.1907
12537 | R-514A | 254.2 | 188.36 | 173.66 | 85.2939
12538 | R-514A | 254.3 | 188.57 | 173.87 | 85.397
12539 | R-514A | 254.4 | 188.78 | 174.08 | 85.5001
12540 | R-514A | 254.5 | 188.99 | 174.29 | 85.6033
12541 | R-514A | 254.6 | 189.2 | 174.5 | 85.7064
12542 | R-514A | 254.7 | 189.42 | 174.72 | 85.8145
12543 | R-514A | 254.8 | 189.63 | 174.93 | 85.9176
12544 | R-514A | 254.9 | 189.84 | 175.14 | 86.0208
12545 | R-514A | 255 | 190.05 | 175.35 | 86.1239
12546 | R-514A | 255.1 | 190.26 | 175.56 | 86.2271
12547 | R-514A | 255.2 | 190.48 | 175.78 | 86.3351
12548 | R-514A | 255.3 | 190.69 | 175.99 | 86.4382
12549 | R-514A | 255.4 | 190.9 | 176.2 | 86.5414
12550 | R-514A | 255.5 | 191.11 | 176.41 | 86.6445
12551 | R-514A | 255.6 | 191.33 | 176.63 | 86.7526
12552 | R-514A | 255.7 | 191.54 | 176.84 | 86.8557
12553 | R-514A | 255.8 | 191.75 | 177.05 | 86.9589
12554 | R-514A | 255.9 | 191.97 | 177.27 | 87.0669
12555 | R-514A | 256 | 192.18 | 177.48 | 87.1701
12556 | R-514A | 256.1 | 192.39 | 177.69 | 87.2732
12557 | R-514A | 256.2 | 192.61 | 177.91 | 87.3813
12558 | R-514A | 256.3 | 192.82 | 178.12 | 87.4844
12559 | R-514A | 256.4 | 193.04 | 178.34 | 87.5925
12560 | R-514A | 256.5 | 193.25 | 178.55 | 87.6956
12561 | R-514A | 256.6 | 193.47 | 178.77 | 87.8037
12562 | R-514A | 256.7 | 193.68 | 178.98 | 87.9068
12563 | R-514A | 256.8 | 193.9 | 179.2 | 88.0148
12564 | R-514A | 256.9 | 194.11 | 179.41 | 88.118
12565 | R-514A | 257 | 194.33 | 179.63 | 88.2261
12566 | R-514A | 257.1 | 194.54 | 179.84 | 88.3292
12567 | R-514A | 257.2 | 194.76 | 180.06 | 88.4373
12568 | R-514A | 257.3 | 194.98 | 180.28 | 88.5453
12569 | R-514A | 257.4 | 195.19 | 180.49 | 88.6484
12570 | R-514A | 257.5 | 195.41 | 180.71 | 88.7565
12571 | R-514A | 257.6 | 195.63 | 180.93 | 88.8645
12572 | R-514A | 257.7 | 195.84 | 181.14 | 88.9677
12573 | R-514A | 257.8 | 196.06 | 181.36 | 89.0757
12574 | R-514A | 257.9 | 196.28 | 181.58 | 89.1838
12575 | R-514A | 258 | 196.49 | 181.79 | 89.2869
12576 | R-514A | 258.1 | 196.71 | 182.01 | 89.395
12577 | R-514A | 258.2 | 196.93 | 182.23 | 89.5031
12578 | R-514A | 258.3 | 197.15 | 182.45 | 89.6111
12579 | R-514A | 258.4 | 197.37 | 182.67 | 89.7192
12580 | R-514A | 258.5 | 197.58 | 182.88 | 89.8223
12581 | R-514A | 258.6 | 197.8 | 183.1 | 89.9304
12582 | R-514A | 258.7 | 198.02 | 183.32 | 90.0384
12583 | R-514A | 258.8 | 198.24 | 183.54 | 90.1465
12584 | R-514A | 258.9 | 198.46 | 183.76 | 90.2545
12585 | R-514A | 259 | 198.68 | 183.98 | 90.3626
12586 | R-514A | 259.1 | 198.9 | 184.2 | 90.4706
12587 | R-514A | 259.2 | 199.12 | 184.42 | 90.5787
12588 | R-514A | 259.3 | 199.34 | 184.64 | 90.6867
12589 | R-514A | 259.4 | 199.56 | 184.86 | 90.7948
12590 | R-514A | 259.5 | 199.78 | 185.08 | 90.9028
12591 | R-514A | 259.6 | 200 | 185.3 | 91.0109
12592 | R-514A | 259.7 | 200.22 | 185.52 | 91.1189
12593 | R-514A | 259.8 | 200.44 | 185.74 | 91.227
12594 | R-514A | 259.9 | 200.66 | 185.96 | 91.3351
12595 | R-514A | 260 | 200.88 | 186.18 | 91.4431
12596 | R-514A | 260.1 | 201.1 | 186.4 | 91.5512
12597 | R-514A | 260.2 | 201.32 | 186.62 | 91.6592
12598 | R-514A | 260.3 | 201.55 | 186.85 | 91.7722
12599 | R-514A | 260.4 | 201.77 | 187.07 | 91.8802
12600 | R-514A | 260.5 | 201.99 | 187.29 | 91.9883
12601 | R-514A | 260.6 | 202.21 | 187.51 | 92.0963
12602 | R-514A | 260.7 | 202.43 | 187.73 | 92.2044
12603 | R-514A | 260.8 | 202.66 | 187.96 | 92.3174
12604 | R-514A | 260.9 | 202.88 | 188.18 | 92.4254
12605 | R-514A | 261 | 203.1 | 188.4 | 92.5335
12606 | R-514A | 261.1 | 203.32 | 188.62 | 92.6415
12607 | R-514A | 261.2 | 203.55 | 188.85 | 92.7545
12608 | R-514A | 261.3 | 203.77 | 189.07 | 92.8625
12609 | R-514A | 261.4 | 204 | 189.3 | 92.9755
12610 | R-514A | 261.5 | 204.22 | 189.52 | 93.0836
12611 | R-514A | 261.6 | 204.44 | 189.74 | 93.1916
12612 | R-514A | 261.7 | 204.67 | 189.97 | 93.3046
12613 | R-514A | 261.8 | 204.89 | 190.19 | 93.4126
12614 | R-514A | 261.9 | 205.12 | 190.42 | 93.5256
12615 | R-514A | 262 | 205.34 | 190.64 | 93.6337
12616 | R-514A | 262.1 | 205.57 | 190.87 | 93.7466
12617 | R-514A | 262.2 | 205.79 | 191.09 | 93.8547
12618 | R-514A | 262.3 | 206.02 | 191.32 | 93.9676
12619 | R-514A | 262.4 | 206.24 | 191.54 | 94.0757
12620 | R-514A | 262.5 | 206.47 | 191.77 | 94.1887
12621 | R-514A | 262.6 | 206.7 | 192 | 94.3016
12622 | R-514A | 262.7 | 206.92 | 192.22 | 94.4097
12623 | R-514A | 262.8 | 207.15 | 192.45 | 94.5226
12624 | R-514A | 262.9 | 207.37 | 192.67 | 94.6307
12625 | R-514A | 263 | 207.6 | 192.9 | 94.7437
12626 | R-514A | 263.1 | 207.83 | 193.13 | 94.8566
12627 | R-514A | 263.2 | 208.05 | 193.35 | 94.9647
12628 | R-514A | 263.3 | 208.28 | 193.58 | 95.0777
12629 | R-514A | 263.4 | 208.51 | 193.81 | 95.1906
12630 | R-514A | 263.5 | 208.74 | 194.04 | 95.3036
12631 | R-514A | 263.6 | 208.97 | 194.27 | 95.4166
12632 | R-514A | 263.7 | 209.19 | 194.49 | 95.5246
12633 | R-514A | 263.8 | 209.42 | 194.72 | 95.6376
12634 | R-514A | 263.9 | 209.65 | 194.95 | 95.7505
12635 | R-514A | 264 | 209.88 | 195.18 | 95.8635
12636 | R-514A | 264.1 | 210.11 | 195.41 | 95.9765
12637 | R-514A | 264.2 | 210.34 | 195.64 | 96.0894
12638 | R-514A | 264.3 | 210.57 | 195.87 | 96.2024
12639 | R-514A | 264.4 | 210.79 | 196.09 | 96.3105
12640 | R-514A | 264.5 | 211.02 | 196.32 | 96.4234
12641 | R-514A | 264.6 | 211.25 | 196.55 | 96.5364
12642 | R-514A | 264.7 | 211.48 | 196.78 | 96.6493
12643 | R-514A | 264.8 | 211.71 | 197.01 | 96.7623
12644 | R-514A | 264.9 | 211.94 | 197.24 | 96.8753
12645 | R-514A | 265 | 212.17 | 197.47 | 96.9882
12646 | R-514A | 265.1 | 212.4 | 197.7 | 97.1012
12647 | R-514A | 265.2 | 212.64 | 197.94 | 97.2191
12648 | R-514A | 265.3 | 212.87 | 198.17 | 97.332
12649 | R-514A | 265.4 | 213.1 | 198.4 | 97.445
12650 | R-514A | 265.5 | 213.33 | 198.63 | 97.558
12651 | R-514A | 265.6 | 213.56 | 198.86 | 97.671
12652 | R-514A | 265.7 | 213.79 | 199.09 | 97.7839
12653 | R-514A | 265.8 | 214.02 | 199.32 | 97.8969
12654 | R-514A | 265.9 | 214.26 | 199.56 | 98.0148
12655 | R-514A | 266 | 214.49 | 199.79 | 98.1277
12656 | R-514A | 266.1 | 214.72 | 200.02 | 98.2407
12657 | R-514A | 266.2 | 214.95 | 200.25 | 98.3537
12658 | R-514A | 266.3 | 215.19 | 200.49 | 98.4715
12659 | R-514A | 266.4 | 215.42 | 200.72 | 98.5845
12660 | R-514A | 266.5 | 215.66 | 200.96 | 98.7024
12661 | R-514A | 266.6 | 215.89 | 201.19 | 98.8153
12662 | R-514A | 266.7 | 216.12 | 201.42 | 98.9283
12663 | R-514A | 266.8 | 216.36 | 201.66 | 99.0462
12664 | R-514A | 266.9 | 216.59 | 201.89 | 99.1591
12665 | R-514A | 267 | 216.82 | 202.12 | 99.2721
12666 | R-514A | 267.1 | 217.06 | 202.36 | 99.39
12667 | R-514A | 267.2 | 217.29 | 202.59 | 99.5029
12668 | R-514A | 267.3 | 217.53 | 202.83 | 99.6208
12669 | R-514A | 267.4 | 217.76 | 203.06 | 99.7338
12670 | R-514A | 267.5 | 218 | 203.3 | 99.8517
12671 | R-514A | 267.6 | 218.23 | 203.53 | 99.9646
12672 | R-514A | 267.7 | 218.47 | 203.77 | 100.0825
12673 | R-514A | 267.8 | 218.71 | 204.01 | 100.2004
12674 | R-514A | 267.9 | 218.94 | 204.24 | 100.3134
12675 | R-514A | 268 | 219.18 | 204.48 | 100.4312
12676 | R-514A | 268.1 | 219.41 | 204.71 | 100.5442
12677 | R-514A | 268.2 | 219.65 | 204.95 | 100.6621
12678 | R-514A | 268.3 | 219.89 | 205.19 | 100.7799
12679 | R-514A | 268.4 | 220.13 | 205.43 | 100.8978
12680 | R-514A | 268.5 | 220.36 | 205.66 | 101.0108
12681 | R-514A | 268.6 | 220.6 | 205.9 | 101.1287
12682 | R-514A | 268.7 | 220.84 | 206.14 | 101.2465
12683 | R-514A | 268.8 | 221.07 | 206.37 | 101.3595
12684 | R-514A | 268.9 | 221.31 | 206.61 | 101.4774
12685 | R-514A | 269 | 221.55 | 206.85 | 101.5953
12686 | R-514A | 269.1 | 221.79 | 207.09 | 101.7131
12687 | R-514A | 269.2 | 222.03 | 207.33 | 101.831
12688 | R-514A | 269.3 | 222.27 | 207.57 | 101.9489
12689 | R-514A | 269.4 | 222.51 | 207.81 | 102.0668
12690 | R-514A | 269.5 | 222.75 | 208.05 | 102.1847
12691 | R-514A | 269.6 | 222.98 | 208.28 | 102.2976
12692 | R-514A | 269.7 | 223.22 | 208.52 | 102.4155
12693 | R-514A | 269.8 | 223.46 | 208.76 | 102.5334
12694 | R-514A | 269.9 | 223.7 | 209 | 102.6513
12695 | R-514A | 270 | 223.94 | 209.24 | 102.7691
12696 | R-514A | 270.1 | 224.18 | 209.48 | 102.887
12697 | R-514A | 270.2 | 224.42 | 209.72 | 103.0049
12698 | R-514A | 270.3 | 224.67 | 209.97 | 103.1277
12699 | R-514A | 270.4 | 224.91 | 210.21 | 103.2455
12700 | R-514A | 270.5 | 225.15 | 210.45 | 103.3634
12701 | R-514A | 270.6 | 225.39 | 210.69 | 103.4813
12702 | R-514A | 270.7 | 225.63 | 210.93 | 103.5992
12703 | R-514A | 270.8 | 225.87 | 211.17 | 103.7171
12704 | R-514A | 270.9 | 226.11 | 211.41 | 103.8349
12705 | R-514A | 271 | 226.35 | 211.65 | 103.9528
12706 | R-514A | 271.1 | 226.6 | 211.9 | 104.0756
12707 | R-514A | 271.2 | 226.84 | 212.14 | 104.1935
12708 | R-514A | 271.3 | 227.08 | 212.38 | 104.3114
12709 | R-514A | 271.4 | 227.33 | 212.63 | 104.4341
12710 | R-514A | 271.5 | 227.57 | 212.87 | 104.552
12711 | R-514A | 271.6 | 227.81 | 213.11 | 104.6699
12712 | R-514A | 271.7 | 228.06 | 213.36 | 104.7927
12713 | R-514A | 271.8 | 228.3 | 213.6 | 104.9106
12714 | R-514A | 271.9 | 228.54 | 213.84 | 105.0284
12715 | R-514A | 272 | 228.79 | 214.09 | 105.1512
12716 | R-514A | 272.1 | 229.03 | 214.33 | 105.2691
12717 | R-514A | 272.2 | 229.28 | 214.58 | 105.3919
12718 | R-514A | 272.3 | 229.52 | 214.82 | 105.5098
12719 | R-514A | 272.4 | 229.77 | 215.07 | 105.6326
12720 | R-514A | 272.5 | 230.01 | 215.31 | 105.7504
12721 | R-514A | 272.6 | 230.26 | 215.56 | 105.8732
12722 | R-514A | 272.7 | 230.5 | 215.8 | 105.9911
12723 | R-514A | 272.8 | 230.75 | 216.05 | 106.1139
12724 | R-514A | 272.9 | 230.99 | 216.29 | 106.2318
12725 | R-514A | 273 | 231.24 | 216.54 | 106.3546
12726 | R-514A | 273.1 | 231.49 | 216.79 | 106.4773
12727 | R-514A | 273.2 | 231.73 | 217.03 | 106.5952
12728 | R-514A | 273.3 | 231.98 | 217.28 | 106.718
12729 | R-514A | 273.4 | 232.23 | 217.53 | 106.8408
12730 | R-514A | 273.5 | 232.47 | 217.77 | 106.9587
12731 | R-514A | 273.6 | 232.72 | 218.02 | 107.0815
12732 | R-514A | 273.7 | 232.97 | 218.27 | 107.2043
12733 | R-514A | 273.8 | 233.22 | 218.52 | 107.327
12734 | R-514A | 273.9 | 233.46 | 218.76 | 107.4449
12735 | R-514A | 274 | 233.71 | 219.01 | 107.5677
12736 | R-514A | 274.1 | 233.96 | 219.26 | 107.6905
12737 | R-514A | 274.2 | 234.21 | 219.51 | 107.8133
12738 | R-514A | 274.3 | 234.46 | 219.76 | 107.9361
12739 | R-514A | 274.4 | 234.71 | 220.01 | 108.0589
12740 | R-514A | 274.5 | 234.96 | 220.26 | 108.1817
12741 | R-514A | 274.6 | 235.21 | 220.51 | 108.3044
12742 | R-514A | 274.7 | 235.46 | 220.76 | 108.4272
12743 | R-514A | 274.8 | 235.7 | 221 | 108.5451
12744 | R-514A | 274.9 | 235.95 | 221.25 | 108.6679
12745 | R-514A | 275 | 236.2 | 221.5 | 108.7907
12746 | R-514A | 275.1 | 236.45 | 221.75 | 108.9135
12747 | R-514A | 275.2 | 236.71 | 222.01 | 109.0412
12748 | R-514A | 275.3 | 236.96 | 222.26 | 109.164
12749 | R-514A | 275.4 | 237.21 | 222.51 | 109.2867
12750 | R-514A | 275.5 | 237.46 | 222.76 | 109.4095
12751 | R-514A | 275.6 | 237.71 | 223.01 | 109.5323
12752 | R-514A | 275.7 | 237.96 | 223.26 | 109.6551
12753 | R-514A | 275.8 | 238.21 | 223.51 | 109.7779
12754 | R-514A | 275.9 | 238.46 | 223.76 | 109.9007
12755 | R-514A | 276 | 238.72 | 224.02 | 110.0284
12756 | R-514A | 276.1 | 238.97 | 224.27 | 110.1512
12757 | R-514A | 276.2 | 239.22 | 224.52 | 110.274
12758 | R-514A | 276.3 | 239.48 | 224.78 | 110.4017
12759 | R-514A | 276.4 | 239.73 | 225.03 | 110.5245
12760 | R-514A | 276.5 | 239.98 | 225.28 | 110.6472
12761 | R-514A | 276.6 | 240.24 | 225.54 | 110.7749
12762 | R-514A | 276.7 | 240.49 | 225.79 | 110.8977
12763 | R-514A | 276.8 | 240.74 | 226.04 | 111.0205
12764 | R-514A | 276.9 | 240.99 | 226.29 | 111.1433
12765 | R-514A | 277 | 241.25 | 226.55 | 111.271
12766 | R-514A | 277.1 | 241.5 | 226.8 | 111.3938
12767 | R-514A | 277.2 | 241.76 | 227.06 | 111.5215
12768 | R-514A | 277.3 | 242.01 | 227.31 | 111.6443
12769 | R-514A | 277.4 | 242.27 | 227.57 | 111.772
12770 | R-514A | 277.5 | 242.52 | 227.82 | 111.8948
12771 | R-514A | 277.6 | 242.78 | 228.08 | 112.0225
12772 | R-514A | 277.7 | 243.04 | 228.34 | 112.1502
12773 | R-514A | 277.8 | 243.29 | 228.59 | 112.273
12774 | R-514A | 277.9 | 243.55 | 228.85 | 112.4007
12775 | R-514A | 278 | 243.8 | 229.1 | 112.5234
12776 | R-514A | 278.1 | 244.06 | 229.36 | 112.6512
12777 | R-514A | 278.2 | 244.32 | 229.62 | 112.7789
12778 | R-514A | 278.3 | 244.57 | 229.87 | 112.9016
12779 | R-514A | 278.4 | 244.83 | 230.13 | 113.0293
12780 | R-514A | 278.5 | 245.09 | 230.39 | 113.157
12781 | R-514A | 278.6 | 245.35 | 230.65 | 113.2847
12782 | R-514A | 278.7 | 245.6 | 230.9 | 113.4075
12783 | R-514A | 278.8 | 245.86 | 231.16 | 113.5352
12784 | R-514A | 278.9 | 246.12 | 231.42 | 113.6629
12785 | R-514A | 279 | 246.38 | 231.68 | 113.7906
12786 | R-514A | 279.1 | 246.64 | 231.94 | 113.9183
12787 | R-514A | 279.2 | 246.89 | 232.19 | 114.0411
12788 | R-514A | 279.3 | 247.15 | 232.45 | 114.1688
12789 | R-514A | 279.4 | 247.41 | 232.71 | 114.2965
12790 | R-514A | 279.5 | 247.67 | 232.97 | 114.4242
12791 | R-514A | 279.6 | 247.93 | 233.23 | 114.5519
12792 | R-514A | 279.7 | 248.19 | 233.49 | 114.6796
12793 | R-514A | 279.8 | 248.45 | 233.75 | 114.8073
12794 | R-514A | 279.9 | 248.71 | 234.01 | 114.935
12795 | R-514A | 280 | 248.97 | 234.27 | 115.0627
12796 | R-514A | 280.1 | 249.23 | 234.53 | 115.1904
12797 | R-514A | 280.2 | 249.49 | 234.79 | 115.3181
12798 | R-514A | 280.3 | 249.76 | 235.06 | 115.4507
12799 | R-514A | 280.4 | 250.02 | 235.32 | 115.5784
12800 | R-514A | 280.5 | 250.28 | 235.58 | 115.7061
12801 | R-514A | 280.6 | 250.54 | 235.84 | 115.8338
12802 | R-514A | 280.7 | 250.8 | 236.1 | 115.9615
12803 | R-514A | 280.8 | 251.06 | 236.36 | 116.0892
12804 | R-514A | 280.9 | 251.32 | 236.62 | 116.2169
12805 | R-514A | 281 | 251.59 | 236.89 | 116.3495
12806 | R-514A | 281.1 | 251.85 | 237.15 | 116.4772
12807 | R-514A | 281.2 | 252.11 | 237.41 | 116.6049
12808 | R-514A | 281.3 | 252.38 | 237.68 | 116.7376
12809 | R-514A | 281.4 | 252.64 | 237.94 | 116.8653
12810 | R-514A | 281.5 | 252.9 | 238.2 | 116.993
12811 | R-514A | 281.6 | 253.17 | 238.47 | 117.1256
12812 | R-514A | 281.7 | 253.43 | 238.73 | 117.2533
12813 | R-514A | 281.8 | 253.7 | 239 | 117.3859
12814 | R-514A | 281.9 | 253.96 | 239.26 | 117.5136
12815 | R-514A | 282 | 254.22 | 239.52 | 117.6413
12816 | R-514A | 282.1 | 254.49 | 239.79 | 117.7739
12817 | R-514A | 282.2 | 254.75 | 240.05 | 117.9016
12818 | R-514A | 282.3 | 255.02 | 240.32 | 118.0342
12819 | R-514A | 282.4 | 255.29 | 240.59 | 118.1668
12820 | R-514A | 282.5 | 255.55 | 240.85 | 118.2945
12821 | R-514A | 282.6 | 255.82 | 241.12 | 118.4271
12822 | R-514A | 282.7 | 256.08 | 241.38 | 118.5548
12823 | R-514A | 282.8 | 256.35 | 241.65 | 118.6874
12824 | R-514A | 282.9 | 256.62 | 241.92 | 118.82
12825 | R-514A | 283 | 256.88 | 242.18 | 118.9477
12826 | R-514A | 283.1 | 257.15 | 242.45 | 119.0804
12827 | R-514A | 283.2 | 257.42 | 242.72 | 119.213
12828 | R-514A | 283.3 | 257.69 | 242.99 | 119.3456
12829 | R-514A | 283.4 | 257.95 | 243.25 | 119.4733
12830 | R-514A | 283.5 | 258.22 | 243.52 | 119.6059
12831 | R-514A | 283.6 | 258.49 | 243.79 | 119.7385
12832 | R-514A | 283.7 | 258.76 | 244.06 | 119.8711
12833 | R-514A | 283.8 | 259.02 | 244.32 | 119.9988
12834 | R-514A | 283.9 | 259.29 | 244.59 | 120.1314
12835 | R-514A | 284 | 259.56 | 244.86 | 120.264
12836 | R-514A | 284.1 | 259.83 | 245.13 | 120.3967
12837 | R-514A | 284.2 | 260.1 | 245.4 | 120.5293
12838 | R-514A | 284.3 | 260.37 | 245.67 | 120.6619
12839 | R-514A | 284.4 | 260.64 | 245.94 | 120.7945
12840 | R-514A | 284.5 | 260.91 | 246.21 | 120.9271
12841 | R-514A | 284.6 | 261.18 | 246.48 | 121.0597
12842 | R-514A | 284.7 | 261.45 | 246.75 | 121.1923
12843 | R-514A | 284.8 | 261.72 | 247.02 | 121.3249
12844 | R-514A | 284.9 | 261.99 | 247.29 | 121.4575
12845 | R-514A | 285 | 262.26 | 247.56 | 121.5902
12846 | R-514A | 285.1 | 262.53 | 247.83 | 121.7228
12847 | R-514A | 285.2 | 262.81 | 248.11 | 121.8603
12848 | R-514A | 285.3 | 263.08 | 248.38 | 121.9929
12849 | R-514A | 285.4 | 263.35 | 248.65 | 122.1255
12850 | R-514A | 285.5 | 263.62 | 248.92 | 122.2581
12851 | R-514A | 285.6 | 263.89 | 249.19 | 122.3907
12852 | R-514A | 285.7 | 264.17 | 249.47 | 122.5283
12853 | R-514A | 285.8 | 264.44 | 249.74 | 122.6609
12854 | R-514A | 285.9 | 264.71 | 250.01 | 122.7935
12855 | R-514A | 286 | 264.98 | 250.28 | 122.9261
12856 | R-514A | 286.1 | 265.26 | 250.56 | 123.0636
12857 | R-514A | 286.2 | 265.53 | 250.83 | 123.1962
12858 | R-514A | 286.3 | 265.81 | 251.11 | 123.3338
12859 | R-514A | 286.4 | 266.08 | 251.38 | 123.4664
12860 | R-514A | 286.5 | 266.36 | 251.66 | 123.6039
12861 | R-514A | 286.6 | 266.63 | 251.93 | 123.7365
12862 | R-514A | 286.7 | 266.9 | 252.2 | 123.8691
12863 | R-514A | 286.8 | 267.18 | 252.48 | 124.0066
12864 | R-514A | 286.9 | 267.45 | 252.75 | 124.1393
12865 | R-514A | 287 | 267.73 | 253.03 | 124.2768
12866 | R-514A | 287.1 | 268 | 253.3 | 124.4094
12867 | R-514A | 287.2 | 268.28 | 253.58 | 124.5469
12868 | R-514A | 287.3 | 268.56 | 253.86 | 124.6844
12869 | R-514A | 287.4 | 268.83 | 254.13 | 124.817
12870 | R-514A | 287.5 | 269.11 | 254.41 | 124.9546
12871 | R-514A | 287.6 | 269.39 | 254.69 | 125.0921
12872 | R-514A | 287.7 | 269.66 | 254.96 | 125.2247
12873 | R-514A | 287.8 | 269.94 | 255.24 | 125.3622
12874 | R-514A | 287.9 | 270.22 | 255.52 | 125.4998
12875 | R-514A | 288 | 270.49 | 255.79 | 125.6324
12876 | R-514A | 288.1 | 270.77 | 256.07 | 125.7699
12877 | R-514A | 288.2 | 271.05 | 256.35 | 125.9074
12878 | R-514A | 288.3 | 271.33 | 256.63 | 126.0449
12879 | R-514A | 288.4 | 271.61 | 256.91 | 126.1825
12880 | R-514A | 288.5 | 271.89 | 257.19 | 126.32
12881 | R-514A | 288.6 | 272.17 | 257.47 | 126.4575
12882 | R-514A | 288.7 | 272.45 | 257.75 | 126.595
12883 | R-514A | 288.8 | 272.72 | 258.02 | 126.7276
12884 | R-514A | 288.9 | 273 | 258.3 | 126.8652
12885 | R-514A | 289 | 273.28 | 258.58 | 127.0027
12886 | R-514A | 289.1 | 273.56 | 258.86 | 127.1402
12887 | R-514A | 289.2 | 273.84 | 259.14 | 127.2777
12888 | R-514A | 289.3 | 274.13 | 259.43 | 127.4202
12889 | R-514A | 289.4 | 274.41 | 259.71 | 127.5577
12890 | R-514A | 289.5 | 274.69 | 259.99 | 127.6952
12891 | R-514A | 289.6 | 274.97 | 260.27 | 127.8327
12892 | R-514A | 289.7 | 275.25 | 260.55 | 127.9703
12893 | R-514A | 289.8 | 275.53 | 260.83 | 128.1078
12894 | R-514A | 289.9 | 275.81 | 261.11 | 128.2453
12895 | R-514A | 290 | 276.09 | 261.39 | 128.3828
12896 | R-514A | 290.1 | 276.38 | 261.68 | 128.5253
12897 | R-514A | 290.2 | 276.66 | 261.96 | 128.6628
12898 | R-514A | 290.3 | 276.94 | 262.24 | 128.8003
12899 | R-514A | 290.4 | 277.23 | 262.53 | 128.9427
12900 | R-514A | 290.5 | 277.51 | 262.81 | 129.0803
12901 | R-514A | 290.6 | 277.79 | 263.09 | 129.2178
12902 | R-514A | 290.7 | 278.08 | 263.38 | 129.3602
12903 | R-514A | 290.8 | 278.36 | 263.66 | 129.4977
12904 | R-514A | 290.9 | 278.64 | 263.94 | 129.6353
12905 | R-514A | 291 | 278.92 | 264.22 | 129.7728
12906 | R-514A | 291.1 | 279.21 | 264.51 | 129.9152
12907 | R-514A | 291.2 | 279.5 | 264.8 | 130.0577
12908 | R-514A | 291.3 | 279.78 | 265.08 | 130.1952
12909 | R-514A | 291.4 | 280.07 | 265.37 | 130.3376
12910 | R-514A | 291.5 | 280.35 | 265.65 | 130.4751
12911 | R-514A | 291.6 | 280.64 | 265.94 | 130.6176
12912 | R-514A | 291.7 | 280.92 | 266.22 | 130.7551
12913 | R-514A | 291.8 | 281.21 | 266.51 | 130.8975
12914 | R-514A | 291.9 | 281.49 | 266.79 | 131.0351
12915 | R-514A | 292 | 281.78 | 267.08 | 131.1775
12916 | R-514A | 292.1 | 282.07 | 267.37 | 131.3199
12917 | R-514A | 292.2 | 282.36 | 267.66 | 131.4624
12918 | R-514A | 292.3 | 282.64 | 267.94 | 131.5999
12919 | R-514A | 292.4 | 282.93 | 268.23 | 131.7423
12920 | R-514A | 292.5 | 283.22 | 268.52 | 131.8848
12921 | R-514A | 292.6 | 283.51 | 268.81 | 132.0272
12922 | R-514A | 292.7 | 283.79 | 269.09 | 132.1647
12923 | R-514A | 292.8 | 284.08 | 269.38 | 132.3072
12924 | R-514A | 292.9 | 284.37 | 269.67 | 132.4496
12925 | R-514A | 293 | 284.66 | 269.96 | 132.592
12926 | R-514A | 293.1 | 284.95 | 270.25 | 132.7345
12927 | R-514A | 293.2 | 285.24 | 270.54 | 132.8769
12928 | R-514A | 293.3 | 285.53 | 270.83 | 133.0193
12929 | R-514A | 293.4 | 285.82 | 271.12 | 133.1618
12930 | R-514A | 293.5 | 286.11 | 271.41 | 133.3042
12931 | R-514A | 293.6 | 286.4 | 271.7 | 133.4466
12932 | R-514A | 293.7 | 286.69 | 271.99 | 133.5891
12933 | R-514A | 293.8 | 286.98 | 272.28 | 133.7315
12934 | R-514A | 293.9 | 287.27 | 272.57 | 133.8739
12935 | R-514A | 294 | 287.56 | 272.86 | 134.0164
12936 | R-514A | 294.1 | 287.85 | 273.15 | 134.1588
12937 | R-514A | 294.2 | 288.14 | 273.44 | 134.3012
12938 | R-514A | 294.3 | 288.43 | 273.73 | 134.4437
12939 | R-514A | 294.4 | 288.73 | 274.03 | 134.591
12940 | R-514A | 294.5 | 289.02 | 274.32 | 134.7335
12941 | R-514A | 294.6 | 289.31 | 274.61 | 134.8759
12942 | R-514A | 294.7 | 289.6 | 274.9 | 135.0183
12943 | R-514A | 294.8 | 289.9 | 275.2 | 135.1657
12944 | R-514A | 294.9 | 290.19 | 275.49 | 135.3081
12945 | R-514A | 295 | 290.48 | 275.78 | 135.4505
12946 | R-514A | 295.1 | 290.78 | 276.08 | 135.5979
12947 | R-514A | 295.2 | 291.07 | 276.37 | 135.7403
12948 | R-514A | 295.3 | 291.37 | 276.67 | 135.8877
12949 | R-514A | 295.4 | 291.66 | 276.96 | 136.0301
12950 | R-514A | 295.5 | 291.95 | 277.25 | 136.1725
12951 | R-514A | 295.6 | 292.25 | 277.55 | 136.3199
12952 | R-514A | 295.7 | 292.54 | 277.84 | 136.4623
12953 | R-514A | 295.8 | 292.84 | 278.14 | 136.6097
12954 | R-514A | 295.9 | 293.13 | 278.43 | 136.7521
12955 | R-514A | 296 | 293.43 | 278.73 | 136.8994
12956 | R-514A | 296.1 | 293.72 | 279.02 | 137.0419
12957 | R-514A | 296.2 | 294.02 | 279.32 | 137.1892
12958 | R-514A | 296.3 | 294.32 | 279.62 | 137.3366
12959 | R-514A | 296.4 | 294.62 | 279.92 | 137.4839
12960 | R-514A | 296.5 | 294.91 | 280.21 | 137.6264
12961 | R-514A | 296.6 | 295.21 | 280.51 | 137.7737
12962 | R-514A | 296.7 | 295.51 | 280.81 | 137.921
12963 | R-514A | 296.8 | 295.8 | 281.1 | 138.0635
12964 | R-514A | 296.9 | 296.1 | 281.4 | 138.2108
12965 | R-514A | 297 | 296.4 | 281.7 | 138.3582
12966 | R-514A | 297.1 | 296.7 | 282 | 138.5055
12967 | R-514A | 297.2 | 297 | 282.3 | 138.6529
12968 | R-514A | 297.3 | 297.29 | 282.59 | 138.7953
12969 | R-514A | 297.4 | 297.59 | 282.89 | 138.9426
12970 | R-514A | 297.5 | 297.89 | 283.19 | 139.09
12971 | R-514A | 297.6 | 298.19 | 283.49 | 139.2373
12972 | R-514A | 297.7 | 298.49 | 283.79 | 139.3847
12973 | R-514A | 297.8 | 298.79 | 284.09 | 139.532
12974 | R-514A | 297.9 | 299.09 | 284.39 | 139.6794
12975 | R-514A | 298 | 299.39 | 284.69 | 139.8267
12976 | R-514A | 298.1 | 299.69 | 284.99 | 139.9741
12977 | R-514A | 298.2 | 299.99 | 285.29 | 140.1214
12978 | R-514A | 298.3 | 300.3 | 285.6 | 140.2737
12979 | R-514A | 298.4 | 300.6 | 285.9 | 140.421
12980 | R-514A | 298.5 | 300.9 | 286.2 | 140.5684
12981 | R-514A | 298.6 | 301.2 | 286.5 | 140.7157
12982 | R-514A | 298.7 | 301.5 | 286.8 | 140.8631
12983 | R-514A | 298.8 | 301.8 | 287.1 | 141.0104
12984 | R-514A | 298.9 | 302.1 | 287.4 | 141.1577
12985 | R-514A | 299 | 302.41 | 287.71 | 141.31
12986 | R-514A | 299.1 | 302.71 | 288.01 | 141.4573
12987 | R-514A | 299.2 | 303.01 | 288.31 | 141.6047
12988 | R-514A | 299.3 | 303.32 | 288.62 | 141.757
12989 | R-514A | 299.4 | 303.62 | 288.92 | 141.9043
12990 | R-514A | 299.5 | 303.93 | 289.23 | 142.0566
12991 | R-514A | 299.6 | 304.23 | 289.53 | 142.2039
12992 | R-514A | 299.7 | 304.53 | 289.83 | 142.3512
12993 | R-514A | 299.8 | 304.84 | 290.14 | 142.5035
12994 | R-514A | 299.9 | 305.14 | 290.44 | 142.6509
12995 | R-514A | 300 | 305.45 | 290.75 | 142.8031
12996 | R-514A | 300.1 | 305.75 | 291.05 | 142.9505
12997 | R-514A | 300.2 | 306.06 | 291.36 | 143.1027
12998 | R-514A | 300.3 | 306.37 | 291.67 | 143.255
12999 | R-514A | 300.4 | 306.67 | 291.97 | 143.4023
13000 | R-514A | 300.5 | 306.98 | 292.28 | 143.5546
13001 | R-514A | 300.6 | 307.29 | 292.59 | 143.7068
13002 | R-514A | 300.7 | 307.59 | 292.89 | 143.8542
13003 | R-514A | 300.8 | 307.9 | 293.2 | 144.0064
13004 | R-514A | 300.9 | 308.2 | 293.5 | 144.1538
13005 | R-514A | 301 | 308.51 | 293.81 | 144.306
13006 | R-514A | 301.1 | 308.82 | 294.12 | 144.4583
13007 | R-514A | 301.2 | 309.13 | 294.43 | 144.6106
13008 | R-514A | 301.3 | 309.44 | 294.74 | 144.7628
13009 | R-514A | 301.4 | 309.75 | 295.05 | 144.9151
13010 | R-514A | 301.5 | 310.05 | 295.35 | 145.0624
13011 | R-514A | 301.6 | 310.36 | 295.66 | 145.2147
13012 | R-514A | 301.7 | 310.67 | 295.97 | 145.3669
13013 | R-514A | 301.8 | 310.98 | 296.28 | 145.5192
13014 | R-514A | 301.9 | 311.29 | 296.59 | 145.6715
13015 | R-514A | 302 | 311.6 | 296.9 | 145.8237
13016 | R-514A | 302.1 | 311.91 | 297.21 | 145.976
13017 | R-514A | 302.2 | 312.22 | 297.52 | 146.1282
13018 | R-514A | 302.3 | 312.53 | 297.83 | 146.2805
13019 | R-514A | 302.4 | 312.84 | 298.14 | 146.4327
13020 | R-514A | 302.5 | 313.16 | 298.46 | 146.5899
13021 | R-514A | 302.6 | 313.47 | 298.77 | 146.7422
13022 | R-514A | 302.7 | 313.78 | 299.08 | 146.8944
13023 | R-514A | 302.8 | 314.09 | 299.39 | 147.0467
13024 | R-514A | 302.9 | 314.4 | 299.7 | 147.1989
13025 | R-514A | 303 | 314.71 | 300.01 | 147.3512
13026 | R-514A | 303.1 | 315.02 | 300.32 | 147.5035
13027 | R-514A | 303.2 | 315.34 | 300.64 | 147.6606
13028 | R-514A | 303.3 | 315.65 | 300.95 | 147.8129
13029 | R-514A | 303.4 | 315.97 | 301.27 | 147.9701
13030 | R-514A | 303.5 | 316.28 | 301.58 | 148.1223
13031 | R-514A | 303.6 | 316.59 | 301.89 | 148.2746
13032 | R-514A | 303.7 | 316.91 | 302.21 | 148.4317
13033 | R-514A | 303.8 | 317.22 | 302.52 | 148.584
13034 | R-514A | 303.9 | 317.53 | 302.83 | 148.7363
13035 | R-514A | 304 | 317.85 | 303.15 | 148.8934
13036 | R-514A | 304.1 | 318.16 | 303.46 | 149.0457
13037 | R-514A | 304.2 | 318.48 | 303.78 | 149.2029
13038 | R-514A | 304.3 | 318.8 | 304.1 | 149.36
13039 | R-514A | 304.4 | 319.11 | 304.41 | 149.5123
13040 | R-514A | 304.5 | 319.43 | 304.73 | 149.6695
13041 | R-514A | 304.6 | 319.74 | 305.04 | 149.8217
13042 | R-514A | 304.7 | 320.06 | 305.36 | 149.9789
13043 | R-514A | 304.8 | 320.38 | 305.68 | 150.1361
13044 | R-514A | 304.9 | 320.69 | 305.99 | 150.2883
13045 | R-514A | 305 | 321.01 | 306.31 | 150.4455
13046 | R-514A | 305.1 | 321.33 | 306.63 | 150.6027
13047 | R-514A | 305.2 | 321.65 | 306.95 | 150.7598
13048 | R-514A | 305.3 | 321.97 | 307.27 | 150.917
13049 | R-514A | 305.4 | 322.28 | 307.58 | 151.0692
13050 | R-514A | 305.5 | 322.6 | 307.9 | 151.2264
13051 | R-514A | 305.6 | 322.92 | 308.22 | 151.3836
13052 | R-514A | 305.7 | 323.24 | 308.54 | 151.5408
13053 | R-514A | 305.8 | 323.56 | 308.86 | 151.6979
13054 | R-514A | 305.9 | 323.88 | 309.18 | 151.8551
13055 | R-514A | 306 | 324.2 | 309.5 | 152.0123
13056 | R-514A | 306.1 | 324.52 | 309.82 | 152.1694
13057 | R-514A | 306.2 | 324.84 | 310.14 | 152.3266
13058 | R-514A | 306.3 | 325.16 | 310.46 | 152.4838
13059 | R-514A | 306.4 | 325.48 | 310.78 | 152.6409
13060 | R-514A | 306.5 | 325.8 | 311.1 | 152.7981
13061 | R-514A | 306.6 | 326.12 | 311.42 | 152.9553
13062 | R-514A | 306.7 | 326.44 | 311.74 | 153.1124
13063 | R-514A | 306.8 | 326.76 | 312.06 | 153.2696
13064 | R-514A | 306.9 | 327.09 | 312.39 | 153.4317
13065 | R-514A | 307 | 327.41 | 312.71 | 153.5889
13066 | R-514A | 307.1 | 327.73 | 313.03 | 153.746
13067 | R-514A | 307.2 | 328.05 | 313.35 | 153.9032
13068 | R-514A | 307.3 | 328.38 | 313.68 | 154.0653
13069 | R-514A | 307.4 | 328.7 | 314 | 154.2225
13070 | R-514A | 307.5 | 329.02 | 314.32 | 154.3796
13071 | R-514A | 307.6 | 329.35 | 314.65 | 154.5417
13072 | R-514A | 307.7 | 329.67 | 314.97 | 154.6989
13073 | R-514A | 307.8 | 330 | 315.3 | 154.861
13074 | R-514A | 307.9 | 330.32 | 315.62 | 155.0181
13075 | R-514A | 308 | 330.64 | 315.94 | 155.1753
13076 | R-514A | 308.1 | 330.97 | 316.27 | 155.3374
13077 | R-514A | 308.2 | 331.29 | 316.59 | 155.4945
13078 | R-514A | 308.3 | 331.62 | 316.92 | 155.6566
13079 | R-514A | 308.4 | 331.95 | 317.25 | 155.8187
13080 | R-514A | 308.5 | 332.27 | 317.57 | 155.9759
13081 | R-514A | 308.6 | 332.6 | 317.9 | 156.138
13082 | R-514A | 308.7 | 332.93 | 318.23 | 156.3
13083 | R-514A | 308.8 | 333.25 | 318.55 | 156.4572
13084 | R-514A | 308.9 | 333.58 | 318.88 | 156.6193
13085 | R-514A | 309 | 333.9 | 319.2 | 156.7765
13086 | R-514A | 309.1 | 334.23 | 319.53 | 156.9385
13087 | R-514A | 309.2 | 334.56 | 319.86 | 157.1006
13088 | R-514A | 309.3 | 334.89 | 320.19 | 157.2627
13089 | R-514A | 309.4 | 335.22 | 320.52 | 157.4248
13090 | R-514A | 309.5 | 335.55 | 320.85 | 157.5869
13091 | R-514A | 309.6 | 335.88 | 321.18 | 157.7489
13092 | R-514A | 309.7 | 336.2 | 321.5 | 157.9061
13093 | R-514A | 309.8 | 336.53 | 321.83 | 158.0682
13094 | R-514A | 309.9 | 336.86 | 322.16 | 158.2303
13095 | R-514A | 310 | 337.19 | 322.49 | 158.3923
13096 | R-514A | 310.1 | 337.52 | 322.82 | 158.5544
13097 | R-514A | 310.2 | 337.85 | 323.15 | 158.7165
13098 | R-514A | 310.3 | 338.18 | 323.48 | 158.8786
13099 | R-514A | 310.4 | 338.52 | 323.82 | 159.0456
13100 | R-514A | 310.5 | 338.85 | 324.15 | 159.2077
13101 | R-514A | 310.6 | 339.18 | 324.48 | 159.3698
13102 | R-514A | 310.7 | 339.51 | 324.81 | 159.5318
13103 | R-514A | 310.8 | 339.84 | 325.14 | 159.6939
13104 | R-514A | 310.9 | 340.17 | 325.47 | 159.856
13105 | R-514A | 311 | 340.5 | 325.8 | 160.0181
13106 | R-514A | 311.1 | 340.84 | 326.14 | 160.1851
13107 | R-514A | 311.2 | 341.17 | 326.47 | 160.3471
13108 | R-514A | 311.3 | 341.5 | 326.8 | 160.5092
13109 | R-514A | 311.4 | 341.84 | 327.14 | 160.6762
13110 | R-514A | 311.5 | 342.17 | 327.47 | 160.8383
13111 | R-514A | 311.6 | 342.51 | 327.81 | 161.0053
13112 | R-514A | 311.7 | 342.84 | 328.14 | 161.1674
13113 | R-514A | 311.8 | 343.17 | 328.47 | 161.3295
13114 | R-514A | 311.9 | 343.51 | 328.81 | 161.4965
13115 | R-514A | 312 | 343.84 | 329.14 | 161.6585
13116 | R-514A | 312.1 | 344.18 | 329.48 | 161.8255
13117 | R-514A | 312.2 | 344.51 | 329.81 | 161.9876
13118 | R-514A | 312.3 | 344.85 | 330.15 | 162.1546
13119 | R-514A | 312.4 | 345.19 | 330.49 | 162.3216
13120 | R-514A | 312.5 | 345.52 | 330.82 | 162.4837
13121 | R-514A | 312.6 | 345.86 | 331.16 | 162.6507
13122 | R-514A | 312.7 | 346.2 | 331.5 | 162.8176
13123 | R-514A | 312.8 | 346.53 | 331.83 | 162.9797
13124 | R-514A | 312.9 | 346.87 | 332.17 | 163.1467
13125 | R-514A | 313 | 347.21 | 332.51 | 163.3137
13126 | R-514A | 313.1 | 347.54 | 332.84 | 163.4758
13127 | R-514A | 313.2 | 347.88 | 333.18 | 163.6428
13128 | R-514A | 313.3 | 348.22 | 333.52 | 163.8098
13129 | R-514A | 313.4 | 348.56 | 333.86 | 163.9768
13130 | R-514A | 313.5 | 348.9 | 334.2 | 164.1438
13131 | R-514A | 313.6 | 349.24 | 334.54 | 164.3108
13132 | R-514A | 313.7 | 349.58 | 334.88 | 164.4778
13133 | R-514A | 313.8 | 349.92 | 335.22 | 164.6447
13134 | R-514A | 313.9 | 350.26 | 335.56 | 164.8117
13135 | R-514A | 314 | 350.6 | 335.9 | 164.9787
13136 | R-514A | 314.1 | 350.94 | 336.24 | 165.1457
13137 | R-514A | 314.2 | 351.28 | 336.58 | 165.3127
13138 | R-514A | 314.3 | 351.62 | 336.92 | 165.4797
13139 | R-514A | 314.4 | 351.96 | 337.26 | 165.6467
13140 | R-514A | 314.5 | 352.3 | 337.6 | 165.8137
13141 | R-514A | 314.6 | 352.65 | 337.95 | 165.9856
13142 | R-514A | 314.7 | 352.99 | 338.29 | 166.1526
13143 | R-514A | 314.8 | 353.33 | 338.63 | 166.3196
13144 | R-514A | 314.9 | 353.67 | 338.97 | 166.4866
13145 | R-514A | 315 | 354.01 | 339.31 | 166.6536
13146 | R-514A | 315.1 | 354.36 | 339.66 | 166.8255
13147 | R-514A | 315.2 | 354.7 | 340 | 166.9925
13148 | R-514A | 315.3 | 355.05 | 340.35 | 167.1644
13149 | R-514A | 315.4 | 355.39 | 340.69 | 167.3314
13150 | R-514A | 315.5 | 355.73 | 341.03 | 167.4983
13151 | R-514A | 315.6 | 356.08 | 341.38 | 167.6703
13152 | R-514A | 315.7 | 356.42 | 341.72 | 167.8373
13153 | R-514A | 315.8 | 356.77 | 342.07 | 168.0092
13154 | R-514A | 315.9 | 357.11 | 342.41 | 168.1762
13155 | R-514A | 316 | 357.46 | 342.76 | 168.3481
13156 | R-514A | 316.1 | 357.8 | 343.1 | 168.515
13157 | R-514A | 316.2 | 358.15 | 343.45 | 168.6869
13158 | R-514A | 316.3 | 358.5 | 343.8 | 168.8588
13159 | R-514A | 316.4 | 358.85 | 344.15 | 169.0308
13160 | R-514A | 316.5 | 359.19 | 344.49 | 169.1978
13161 | R-514A | 316.6 | 359.54 | 344.84 | 169.3697
13162 | R-514A | 316.7 | 359.89 | 345.19 | 169.5416
13163 | R-514A | 316.8 | 360.23 | 345.53 | 169.7086
13164 | R-514A | 316.9 | 360.58 | 345.88 | 169.8804
13165 | R-514A | 317 | 360.93 | 346.23 | 170.0524
13166 | R-514A | 317.1 | 361.28 | 346.58 | 170.2243
13167 | R-514A | 317.2 | 361.63 | 346.93 | 170.3962
13168 | R-514A | 317.3 | 361.98 | 347.28 | 170.5681
13169 | R-514A | 317.4 | 362.33 | 347.63 | 170.74
13170 | R-514A | 317.5 | 362.68 | 347.98 | 170.9119
13171 | R-514A | 317.6 | 363.03 | 348.33 | 171.0838
13172 | R-514A | 317.7 | 363.38 | 348.68 | 171.2557
13173 | R-514A | 317.8 | 363.73 | 349.03 | 171.4276
13174 | R-514A | 317.9 | 364.08 | 349.38 | 171.5995
13175 | R-514A | 318 | 364.43 | 349.73 | 171.7714
13176 | R-514A | 318.1 | 364.78 | 350.08 | 171.9433
13177 | R-514A | 318.2 | 365.13 | 350.43 | 172.1152
13178 | R-514A | 318.3 | 365.48 | 350.78 | 172.2871
13179 | R-514A | 318.4 | 365.84 | 351.14 | 172.4639
13180 | R-514A | 318.5 | 366.19 | 351.49 | 172.6358
13181 | R-514A | 318.6 | 366.54 | 351.84 | 172.8077
13182 | R-514A | 318.7 | 366.89 | 352.19 | 172.9796
13183 | R-514A | 318.8 | 367.25 | 352.55 | 173.1565
13184 | R-514A | 318.9 | 367.6 | 352.9 | 173.3284
13185 | R-514A | 319 | 367.95 | 353.25 | 173.5003
13186 | R-514A | 319.1 | 368.31 | 353.61 | 173.6771
13187 | R-514A | 319.2 | 368.66 | 353.96 | 173.849
13188 | R-514A | 319.3 | 369.02 | 354.32 | 174.0258
13189 | R-514A | 319.4 | 369.37 | 354.67 | 174.1977
13190 | R-514A | 319.5 | 369.73 | 355.03 | 174.3745
13191 | R-514A | 319.6 | 370.08 | 355.38 | 174.5464
13192 | R-514A | 319.7 | 370.44 | 355.74 | 174.7232
13193 | R-514A | 319.8 | 370.79 | 356.09 | 174.8951
13194 | R-514A | 319.9 | 371.15 | 356.45 | 175.0719
13195 | R-514A | 320 | 371.5 | 356.8 | 175.2439
13196 | R-514A | 320.1 | 371.86 | 357.16 | 175.4207
13197 | R-514A | 320.2 | 372.22 | 357.52 | 175.5975
13198 | R-514A | 320.3 | 372.58 | 357.88 | 175.7743
13199 | R-514A | 320.4 | 372.93 | 358.23 | 175.9462
13200 | R-514A | 320.5 | 373.29 | 358.59 | 176.123
13201 | R-514A | 320.6 | 373.65 | 358.95 | 176.2998
13202 | R-514A | 320.7 | 374.01 | 359.31 | 176.4767
13203 | R-514A | 320.8 | 374.37 | 359.67 | 176.6535
13204 | R-514A | 320.9 | 374.72 | 360.02 | 176.8254
13205 | R-514A | 321 | 375.08 | 360.38 | 177.0022
13206 | R-514A | 321.1 | 375.44 | 360.74 | 177.179
13207 | R-514A | 321.2 | 375.8 | 361.1 | 177.3558
13208 | R-514A | 321.3 | 376.17 | 361.47 | 177.5376
13209 | R-514A | 321.4 | 376.53 | 361.83 | 177.7144
13210 | R-514A | 321.5 | 376.89 | 362.19 | 177.8912
13211 | R-514A | 321.6 | 377.25 | 362.55 | 178.068
13212 | R-514A | 321.7 | 377.61 | 362.91 | 178.2448
13213 | R-514A | 321.8 | 377.97 | 363.27 | 178.4216
13214 | R-514A | 321.9 | 378.33 | 363.63 | 178.5984
13215 | R-514A | 322 | 378.69 | 363.99 | 178.7753
13216 | R-514A | 322.1 | 379.05 | 364.35 | 178.9521
13217 | R-514A | 322.2 | 379.42 | 364.72 | 179.1338
13218 | R-514A | 322.3 | 379.78 | 365.08 | 179.3106
13219 | R-514A | 322.4 | 380.15 | 365.45 | 179.4923
13220 | R-514A | 322.5 | 380.51 | 365.81 | 179.6692
13221 | R-514A | 322.6 | 380.87 | 366.17 | 179.846
13222 | R-514A | 322.7 | 381.24 | 366.54 | 180.0277
13223 | R-514A | 322.8 | 381.6 | 366.9 | 180.2045
13224 | R-514A | 322.9 | 381.96 | 367.26 | 180.3813
13225 | R-514A | 323 | 382.33 | 367.63 | 180.5631
13226 | R-514A | 323.1 | 382.69 | 367.99 | 180.7399
13227 | R-514A | 323.2 | 383.06 | 368.36 | 180.9216
13228 | R-514A | 323.3 | 383.43 | 368.73 | 181.1033
13229 | R-514A | 323.4 | 383.79 | 369.09 | 181.2801
13230 | R-514A | 323.5 | 384.16 | 369.46 | 181.4619
13231 | R-514A | 323.6 | 384.53 | 369.83 | 181.6436
13232 | R-514A | 323.7 | 384.89 | 370.19 | 181.8204
13233 | R-514A | 323.8 | 385.26 | 370.56 | 182.0021
13234 | R-514A | 323.9 | 385.63 | 370.93 | 182.1839
13235 | R-514A | 324 | 385.99 | 371.29 | 182.3607
13236 | R-514A | 324.1 | 386.36 | 371.66 | 182.5424
13237 | R-514A | 324.2 | 386.73 | 372.03 | 182.7241
13238 | R-514A | 324.3 | 387.1 | 372.4 | 182.9059
13239 | R-514A | 324.4 | 387.47 | 372.77 | 183.0876
13240 | R-514A | 324.5 | 387.84 | 373.14 | 183.2693
13241 | R-514A | 324.6 | 388.21 | 373.51 | 183.4511
13242 | R-514A | 324.7 | 388.58 | 373.88 | 183.6328
13243 | R-514A | 324.8 | 388.95 | 374.25 | 183.8145
13244 | R-514A | 324.9 | 389.32 | 374.62 | 183.9962
13245 | R-514A | 325 | 389.69 | 374.99 | 184.178
13246 | R-514A | 325.1 | 390.06 | 375.36 | 184.3597
13247 | R-514A | 325.2 | 390.43 | 375.73 | 184.5414
13248 | R-514A | 325.3 | 390.8 | 376.1 | 184.7231
13249 | R-514A | 325.4 | 391.17 | 376.47 | 184.9049
13250 | R-514A | 325.5 | 391.55 | 376.85 | 185.0915
13251 | R-514A | 325.6 | 391.92 | 377.22 | 185.2732
13252 | R-514A | 325.7 | 392.29 | 377.59 | 185.455
13253 | R-514A | 325.8 | 392.66 | 377.96 | 185.6367
13254 | R-514A | 325.9 | 393.04 | 378.34 | 185.8233
13255 | R-514A | 326 | 393.41 | 378.71 | 186.0051
13256 | R-514A | 326.1 | 393.78 | 379.08 | 186.1868
13257 | R-514A | 326.2 | 394.16 | 379.46 | 186.3734
13258 | R-514A | 326.3 | 394.53 | 379.83 | 186.5551
13259 | R-514A | 326.4 | 394.91 | 380.21 | 186.7418
13260 | R-514A | 326.5 | 395.28 | 380.58 | 186.9235
13261 | R-514A | 326.6 | 395.66 | 380.96 | 187.1102
13262 | R-514A | 326.7 | 396.03 | 381.33 | 187.2919
13263 | R-514A | 326.8 | 396.41 | 381.71 | 187.4785
13264 | R-514A | 326.9 | 396.78 | 382.08 | 187.6602
13265 | R-514A | 327 | 397.16 | 382.46 | 187.8469
13266 | R-514A | 327.1 | 397.54 | 382.84 | 188.0335
13267 | R-514A | 327.2 | 397.92 | 383.22 | 188.2202
13268 | R-514A | 327.3 | 398.29 | 383.59 | 188.4019
13269 | R-514A | 327.4 | 398.67 | 383.97 | 188.5885
13270 | R-514A | 327.5 | 399.05 | 384.35 | 188.7752
13271 | R-514A | 327.6 | 399.43 | 384.73 | 188.9618
13272 | R-514A | 327.7 | 399.81 | 385.11 | 189.1484
13273 | R-514A | 327.8 | 400.18 | 385.48 | 189.3302
13274 | R-514A | 327.9 | 400.56 | 385.86 | 189.5168
13275 | R-514A | 328 | 400.94 | 386.24 | 189.7034
13276 | R-514A | 328.1 | 401.32 | 386.62 | 189.8901
13277 | R-514A | 328.2 | 401.7 | 387 | 190.0767
13278 | R-514A | 328.3 | 402.08 | 387.38 | 190.2634
13279 | R-514A | 328.4 | 402.47 | 387.77 | 190.4549
13280 | R-514A | 328.5 | 402.85 | 388.15 | 190.6415
13281 | R-514A | 328.6 | 403.23 | 388.53 | 190.8282
13282 | R-514A | 328.7 | 403.61 | 388.91 | 191.0148
13283 | R-514A | 328.8 | 403.99 | 389.29 | 191.2015
13284 | R-514A | 328.9 | 404.37 | 389.67 | 191.3881
13285 | R-514A | 329 | 404.75 | 390.05 | 191.5747
13286 | R-514A | 329.1 | 405.14 | 390.44 | 191.7663
13287 | R-514A | 329.2 | 405.52 | 390.82 | 191.9529
13288 | R-514A | 329.3 | 405.9 | 391.2 | 192.1396
13289 | R-514A | 329.4 | 406.29 | 391.59 | 192.3311
13290 | R-514A | 329.5 | 406.67 | 391.97 | 192.5178
13291 | R-514A | 329.6 | 407.06 | 392.36 | 192.7093
13292 | R-514A | 329.7 | 407.44 | 392.74 | 192.8959
13293 | R-514A | 329.8 | 407.82 | 393.12 | 193.0826
13294 | R-514A | 329.9 | 408.21 | 393.51 | 193.2741
13295 | R-514A | 330 | 408.59 | 393.89 | 193.4608
13296 | R-514A | 330.1 | 408.98 | 394.28 | 193.6523
13297 | R-514A | 330.2 | 409.37 | 394.67 | 193.8439
13298 | R-514A | 330.3 | 409.75 | 395.05 | 194.0305
13299 | R-514A | 330.4 | 410.14 | 395.44 | 194.2221
13300 | R-514A | 330.5 | 410.53 | 395.83 | 194.4136
13301 | R-514A | 330.6 | 410.92 | 396.22 | 194.6052
13302 | R-514A | 330.7 | 411.3 | 396.6 | 194.7918
13303 | R-514A | 330.8 | 411.69 | 396.99 | 194.9834
13304 | R-514A | 330.9 | 412.08 | 397.38 | 195.1749
13305 | R-514A | 331 | 412.46 | 397.76 | 195.3615
13306 | R-514A | 331.1 | 412.85 | 398.15 | 195.5531
13307 | R-514A | 331.2 | 413.24 | 398.54 | 195.7446
13308 | R-514A | 331.3 | 413.63 | 398.93 | 195.9362
13309 | R-514A | 331.4 | 414.02 | 399.32 | 196.1277
13310 | R-514A | 331.5 | 414.41 | 399.71 | 196.3193
13311 | R-514A | 331.6 | 414.8 | 400.1 | 196.5108
13312 | R-514A | 331.7 | 415.2 | 400.5 | 196.7073
13313 | R-514A | 331.8 | 415.59 | 400.89 | 196.8989
13314 | R-514A | 331.9 | 415.98 | 401.28 | 197.0904
13315 | R-514A | 332 | 416.37 | 401.67 | 197.2819
13316 | R-514A | 332.1 | 416.76 | 402.06 | 197.4735
13317 | R-514A | 332.2 | 417.15 | 402.45 | 197.6651
13318 | R-514A | 332.3 | 417.55 | 402.85 | 197.8615
13319 | R-514A | 332.4 | 417.94 | 403.24 | 198.0531
13320 | R-514A | 332.5 | 418.33 | 403.63 | 198.2446
13321 | R-514A | 332.6 | 418.73 | 404.03 | 198.4411
13322 | R-514A | 332.7 | 419.12 | 404.42 | 198.6326
13323 | R-514A | 332.8 | 419.51 | 404.81 | 198.8242
13324 | R-514A | 332.9 | 419.9 | 405.2 | 199.0157
13325 | R-514A | 333 | 420.3 | 405.6 | 199.2122
13326 | R-514A | 333.1 | 420.69 | 405.99 | 199.4037
13327 | R-514A | 333.2 | 421.09 | 406.39 | 199.6002
13328 | R-514A | 333.3 | 421.49 | 406.79 | 199.7967
13329 | R-514A | 333.4 | 421.88 | 407.18 | 199.9882
13330 | R-514A | 333.5 | 422.28 | 407.58 | 200.1847
13331 | R-514A | 333.6 | 422.68 | 407.98 | 200.3811
13332 | R-514A | 333.7 | 423.07 | 408.37 | 200.5727
13333 | R-514A | 333.8 | 423.47 | 408.77 | 200.7691
13334 | R-514A | 333.9 | 423.87 | 409.17 | 200.9656
13335 | R-514A | 334 | 424.26 | 409.56 | 201.1572
13336 | R-514A | 334.1 | 424.66 | 409.96 | 201.3536
13337 | R-514A | 334.2 | 425.06 | 410.36 | 201.5501
13338 | R-514A | 334.3 | 425.46 | 410.76 | 201.7465
13339 | R-514A | 334.4 | 425.86 | 411.16 | 201.943
13340 | R-514A | 334.5 | 426.26 | 411.56 | 202.1395
13341 | R-514A | 334.6 | 426.66 | 411.96 | 202.3359
13342 | R-514A | 334.7 | 427.06 | 412.36 | 202.5324
13343 | R-514A | 334.8 | 427.46 | 412.76 | 202.7288
13344 | R-514A | 334.9 | 427.86 | 413.16 | 202.9253
13345 | R-514A | 335 | 428.26 | 413.56 | 203.1218
13346 | R-514A | 335.1 | 428.66 | 413.96 | 203.3182
13347 | R-514A | 335.2 | 429.06 | 414.36 | 203.5147
13348 | R-514A | 335.3 | 429.46 | 414.76 | 203.7112
13349 | R-514A | 335.4 | 429.87 | 415.17 | 203.9125
13350 | R-514A | 335.5 | 430.27 | 415.57 | 204.109
13351 | R-514A | 335.6 | 430.67 | 415.97 | 204.3055
13352 | R-514A | 335.7 | 431.08 | 416.38 | 204.5068
13353 | R-514A | 335.8 | 431.48 | 416.78 | 204.7033
13354 | R-514A | 335.9 | 431.88 | 417.18 | 204.8998
13355 | R-514A | 336 | 432.28 | 417.58 | 205.0962
13356 | R-514A | 336.1 | 432.69 | 417.99 | 205.2976
13357 | R-514A | 336.2 | 433.1 | 418.4 | 205.499
13358 | R-514A | 336.3 | 433.5 | 418.8 | 205.6954
13359 | R-514A | 336.4 | 433.91 | 419.21 | 205.8968
13360 | R-514A | 336.5 | 434.31 | 419.61 | 206.0933
13361 | R-514A | 336.6 | 434.72 | 420.02 | 206.2946
13362 | R-514A | 336.7 | 435.12 | 420.42 | 206.4911
13363 | R-514A | 336.8 | 435.53 | 420.83 | 206.6925
13364 | R-514A | 336.9 | 435.94 | 421.24 | 206.8938
13365 | R-514A | 337 | 436.34 | 421.64 | 207.0903
13366 | R-514A | 337.1 | 436.75 | 422.05 | 207.2917
13367 | R-514A | 337.2 | 437.16 | 422.46 | 207.4931
13368 | R-514A | 337.3 | 437.57 | 422.87 | 207.6944
13369 | R-514A | 337.4 | 437.98 | 423.28 | 207.8958
13370 | R-514A | 337.5 | 438.39 | 423.69 | 208.0972
13371 | R-514A | 337.6 | 438.8 | 424.1 | 208.2985
13372 | R-514A | 337.7 | 439.21 | 424.51 | 208.4999
13373 | R-514A | 337.8 | 439.62 | 424.92 | 208.7013
13374 | R-514A | 337.9 | 440.02 | 425.32 | 208.8978
13375 | R-514A | 338 | 440.43 | 425.73 | 209.0991
13376 | R-514A | 338.1 | 440.85 | 426.15 | 209.3054
13377 | R-514A | 338.2 | 441.26 | 426.56 | 209.5068
13378 | R-514A | 338.3 | 441.67 | 426.97 | 209.7082
13379 | R-514A | 338.4 | 442.08 | 427.38 | 209.9095
13380 | R-514A | 338.5 | 442.5 | 427.8 | 210.1158
13381 | R-514A | 338.6 | 442.91 | 428.21 | 210.3172
13382 | R-514A | 338.7 | 443.32 | 428.62 | 210.5186
13383 | R-514A | 338.8 | 443.73 | 429.03 | 210.7199
13384 | R-514A | 338.9 | 444.15 | 429.45 | 210.9262
13385 | R-514A | 339 | 444.56 | 429.86 | 211.1276
13386 | R-514A | 339.1 | 444.97 | 430.27 | 211.329
13387 | R-514A | 339.2 | 445.39 | 430.69 | 211.5352
13388 | R-514A | 339.3 | 445.81 | 431.11 | 211.7415
13389 | R-514A | 339.4 | 446.22 | 431.52 | 211.9429
13390 | R-514A | 339.5 | 446.64 | 431.94 | 212.1492
13391 | R-514A | 339.6 | 447.05 | 432.35 | 212.3506
13392 | R-514A | 339.7 | 447.47 | 432.77 | 212.5568
13393 | R-514A | 339.8 | 447.88 | 433.18 | 212.7582
13394 | R-514A | 339.9 | 448.3 | 433.6 | 212.9645
13395 | R-514A | 340 | 448.72 | 434.02 | 213.1708
13396 | R-514A | 340.1 | 449.13 | 434.43 | 213.3722
13397 | R-514A | 340.2 | 449.55 | 434.85 | 213.5785
13398 | R-514A | 340.3 | 449.97 | 435.27 | 213.7847
13399 | R-514A | 340.4 | 450.39 | 435.69 | 213.991
13400 | R-514A | 340.5 | 450.81 | 436.11 | 214.1973
13401 | R-514A | 340.6 | 451.23 | 436.53 | 214.4036
13402 | R-514A | 340.7 | 451.65 | 436.95 | 214.6099
13403 | R-514A | 340.8 | 452.07 | 437.37 | 214.8162
13404 | R-514A | 340.9 | 452.49 | 437.79 | 215.0224
13405 | R-514A | 341 | 452.91 | 438.21 | 215.2287
13406 | R-514A | 341.1 | 453.33 | 438.63 | 215.435
13407 | R-514A | 341.2 | 453.75 | 439.05 | 215.6413
13408 | R-514A | 341.3 | 454.17 | 439.47 | 215.8476
13409 | R-514A | 341.4 | 454.6 | 439.9 | 216.0588
13410 | R-514A | 341.5 | 455.02 | 440.32 | 216.2651
13411 | R-514A | 341.6 | 455.44 | 440.74 | 216.4714
13412 | R-514A | 341.7 | 455.86 | 441.16 | 216.6776
13413 | R-514A | 341.8 | 456.29 | 441.59 | 216.8888
13414 | R-514A | 341.9 | 456.71 | 442.01 | 217.0951
13415 | R-514A | 342 | 457.13 | 442.43 | 217.3014
13416 | R-514A | 342.1 | 457.56 | 442.86 | 217.5126
13417 | R-514A | 342.2 | 457.98 | 443.28 | 217.7189
13418 | R-514A | 342.3 | 458.41 | 443.71 | 217.9301
13419 | R-514A | 342.4 | 458.83 | 444.13 | 218.1364
13420 | R-514A | 342.5 | 459.26 | 444.56 | 218.3476
13421 | R-514A | 342.6 | 459.69 | 444.99 | 218.5588
13422 | R-514A | 342.7 | 460.11 | 445.41 | 218.765
13423 | R-514A | 342.8 | 460.54 | 445.84 | 218.9762
13424 | R-514A | 342.9 | 460.96 | 446.26 | 219.1825
13425 | R-514A | 343 | 461.39 | 446.69 | 219.3937
13426 | R-514A | 343.1 | 461.82 | 447.12 | 219.6049
13427 | R-514A | 343.2 | 462.25 | 447.55 | 219.8161
13428 | R-514A | 343.3 | 462.68 | 447.98 | 220.0273
13429 | R-514A | 343.4 | 463.11 | 448.41 | 220.2385
13430 | R-514A | 343.5 | 463.54 | 448.84 | 220.4497
13431 | R-514A | 343.6 | 463.97 | 449.27 | 220.6609
13432 | R-514A | 343.7 | 464.39 | 449.69 | 220.8672
13433 | R-514A | 343.8 | 464.82 | 450.12 | 221.0784
13434 | R-514A | 343.9 | 465.25 | 450.55 | 221.2896
13435 | R-514A | 344 | 465.68 | 450.98 | 221.5008
13436 | R-514A | 344.1 | 466.12 | 451.42 | 221.7169
13437 | R-514A | 344.2 | 466.55 | 451.85 | 221.9281
13438 | R-514A | 344.3 | 466.98 | 452.28 | 222.1393
13439 | R-514A | 344.4 | 467.41 | 452.71 | 222.3505
13440 | R-514A | 344.5 | 467.85 | 453.15 | 222.5666
13441 | R-514A | 344.6 | 468.28 | 453.58 | 222.7778
13442 | R-514A | 344.7 | 468.71 | 454.01 | 222.989
13443 | R-514A | 344.8 | 469.15 | 454.45 | 223.2051
13444 | R-514A | 344.9 | 469.58 | 454.88 | 223.4163
13445 | R-514A | 345 | 470.01 | 455.31 | 223.6275
13446 | R-514A | 345.1 | 470.45 | 455.75 | 223.8436
13447 | R-514A | 345.2 | 470.88 | 456.18 | 224.0548
13448 | R-514A | 345.3 | 471.32 | 456.62 | 224.2709
13449 | R-514A | 345.4 | 471.76 | 457.06 | 224.487
13450 | R-514A | 345.5 | 472.19 | 457.49 | 224.6982
13451 | R-514A | 345.6 | 472.63 | 457.93 | 224.9143
13452 | R-514A | 345.7 | 473.07 | 458.37 | 225.1304
13453 | R-514A | 345.8 | 473.5 | 458.8 | 225.3416
13454 | R-514A | 345.9 | 473.94 | 459.24 | 225.5577
13455 | R-514A | 346 | 474.38 | 459.68 | 225.7738
13456 | R-514A | 346.1 | 474.82 | 460.12 | 225.9899
13457 | R-514A | 346.2 | 475.26 | 460.56 | 226.206
13458 | R-514A | 346.3 | 475.7 | 461 | 226.4221
13459 | R-514A | 346.4 | 476.14 | 461.44 | 226.6382
13460 | R-514A | 346.5 | 476.58 | 461.88 | 226.8544
13461 | R-514A | 346.6 | 477.02 | 462.32 | 227.0705
13462 | R-514A | 346.7 | 477.46 | 462.76 | 227.2866
13463 | R-514A | 346.8 | 477.9 | 463.2 | 227.5027
13464 | R-514A | 346.9 | 478.34 | 463.64 | 227.7188
13465 | R-514A | 347 | 478.78 | 464.08 | 227.9349
13466 | R-514A | 347.1 | 479.22 | 464.52 | 228.151
13467 | R-514A | 347.2 | 479.66 | 464.96 | 228.3671
13468 | R-514A | 347.3 | 480.11 | 465.41 | 228.5881
13469 | R-514A | 347.4 | 480.55 | 465.85 | 228.8042
13470 | R-514A | 347.5 | 480.99 | 466.29 | 229.0203
13471 | R-514A | 347.6 | 481.44 | 466.74 | 229.2414
13472 | R-514A | 347.7 | 481.88 | 467.18 | 229.4575
13473 | R-514A | 347.8 | 482.32 | 467.62 | 229.6736
13474 | R-514A | 347.9 | 482.77 | 468.07 | 229.8946
13475 | R-514A | 348 | 483.21 | 468.51 | 230.1107
13476 | R-514A | 348.1 | 483.66 | 468.96 | 230.3317
13477 | R-514A | 348.2 | 484.11 | 469.41 | 230.5528
13478 | R-514A | 348.3 | 484.55 | 469.85 | 230.7688
13479 | R-514A | 348.4 | 485 | 470.3 | 230.9899
13480 | R-514A | 348.5 | 485.45 | 470.75 | 231.2109
13481 | R-514A | 348.6 | 485.9 | 471.2 | 231.4319
13482 | R-514A | 348.7 | 486.34 | 471.64 | 231.648
13483 | R-514A | 348.8 | 486.79 | 472.09 | 231.869
13484 | R-514A | 348.9 | 487.24 | 472.54 | 232.0901
13485 | R-514A | 349 | 487.68 | 472.98 | 232.3062
13486 | R-514A | 349.1 | 488.14 | 473.44 | 232.5321
13487 | R-514A | 349.2 | 488.59 | 473.89 | 232.7531
13488 | R-514A | 349.3 | 489.04 | 474.34 | 232.9741
13489 | R-514A | 349.4 | 489.49 | 474.79 | 233.1952
13490 | R-514A | 349.5 | 489.94 | 475.24 | 233.4162
13491 | R-514A | 349.6 | 490.39 | 475.69 | 233.6372
13492 | R-514A | 349.7 | 490.84 | 476.14 | 233.8582
13493 | R-514A | 349.8 | 491.29 | 476.59 | 234.0792
13494 | R-514A | 349.9 | 491.74 | 477.04 | 234.3003
13495 | R-514A | 350 | 492.19 | 477.49 | 234.5213

## Sheet1
DB Log Table Fields - chillercheck.LogRecords | Description / Notes | hide/show condition | validation conditions | required status | remarks | parameters calculated runtime on log creation | use | Conditions / Notes
ChillerID | Foreign key to the chiller | - | selected from the dropdown | required | Chiller types needs to be found from the database because they are refered to as TypeA, TypeB and so on but found no such reference in code base. | createLogRecord = 0 |  | Always required for record creation.
UserID | User who created the log entry | - | extracted from the request event | required |  | checkUnit = 0 |  | Automatically set as current datetime on insert/update.
ChangeUserID | User who last changed the record | - |  | required |  | purgeTime = 0 |  | Must not be future date. Validated in JS with _isValidReadingDate.
ChangeDate | Timestamp of last change | - | set to date on which the form was loaded | required |  | purgeTimeMinTemp = 0 |  | Validated as numeric. In numericFields array and form validation applied.
ReadingDate | Date/time when readings were taken | - | set to date on which the form was loaded | required |  | purgeTimeHrTemp = 0 |  | Numeric validation applied.
CondInletTemp | Condenser inlet water temperature | - | if in edit mode, last stored value is prefilled by using the getCondInletTemp function. If in new record mode, no value is prefilled, size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  | ret = true | used to hold the success status to return | Display/input depends on chiller property HighPressureRefrig. If high pressure, it's shown as readonly or no input.
CondOutletTemp | Condenser outlet water temperature | - | if in edit mode, last stored value is prefilled by using the getCondOutletTemp function. If in new record mode, no value is prefilled, size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  |  |  | Validated if numeric; null allowed.
CondRefrigTemp | Condenser refrigerant temperature | - | if in edit mode, last stored value is prefilled by using the getCondRefrigTemp function. If in new record mode, no value is prefilled, size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  |  |  | Validated if numeric; null allowed.
CondPressure | Condenser pressure | - | if in edit mode, last stored value is prefilled by using the getCondPressure function. If in new record mode, no value is prefilled, size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  |  |  | Numeric validation applied.
CondAPDrop | Condenser actual pressure drop | - | if in edit mode, last stored value is prefilled by using the getCondAPDrop() function. If in new record mode, no value is prefilled , size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  |  |  | Numeric validation applied.
EvapInletTemp | Evaporator inlet water temperature | - | if in edit mode, last stored value is prefilled by using the getEvapInletTemp() function. If in new record mode, no value is prefilled, size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  |  |  | Display/input depends on chiller property UseEvapRefrigTemp. Numeric if present; else calculated value shown.
EvapOutletTemp | Evaporator outlet water temperature | - | if in edit mode, the current EvapOutletTemp from the existing data is prefilled by using the getEvapOutletTemp() function, if in new record mode, no value is prefilled and size is set to 5, maxlength to 5 and converted to standard english decimal number for concistancy. | required |  |  |  | Validated if numeric; null allowed.
EvapRefrigTemp | Evaporator refrigerant temperature | based on the output of the function variables.chiller.getUseEvapRefrigTemp() | If it's not a new record (variables.newRecord is false), it will display the calculated refrigerant temperature value (getCalculatedEvapRefrigTemp()), formatted using LSNumberFormat("999.9") for consistency. If it is a new record (variables.newRecord is true), it will display empty cells (&nbsp;), essentially showing no input for this temperature field. If variables.chiller.getUseEvapRefrigTemp() is true (i.e., the chiller uses evaporator refrigerant temperature), the code inside this block will run. If variables.logRecord.getEvapRefrigTemp() is numeric, it displays an input field for the user to enter or modify the evaporator refrigerant temperature. If it is not a new record, the field will show the existing value of EvapRefrigTemp (formatted with LSNumberFormat).If variables.logRecord.getEvapRefrigTemp() is not numeric, it will show an input field with the calculated refrigerant temperature (getCalculatedEvapRefrigTemp()), formatted the same way as before. | required |  |  |  | Validated if numeric; null allowed.
EvapPressure | Evaporator pressure | - | If the record is not new (NOT variables.newRecord), it will populate the field with the EvapPressure value from the log record (variables.logRecord.getEvapPressure()). The value is formatted using LSNumberFormat("999.9") to ensure it is displayed with one decimal place. The #Trim(...)# function trims any extra whitespace from the value. For a new record: The field will be empty because the condition for newRecord will prevent any value from being populated. | required |  |  |  | Numeric validation.
EvapAPDrop | Evaporator actual pressure drop | - | NOT variables.newRecord: This checks if the form is not for a new record (i.e., it's an existing record being edited). isNumeric(variables.logRecord.getEvapAPDrop()): Ensures that the value of EvapAPDrop is a valid numeric value. If this condition is true, the field will be populated with the EvapAPDrop value from the logRecord object. If the record is not new and EvapAPDrop is numeric, it formats the value with LSNumberFormat("999.9"), which ensures the value is displayed with one decimal place Trim function: Removes any extra spaces around the value If it's a new record (variables.newRecord = true), the field will be empty, as no value is provided. | required |  |  |  | Included only if chiller property AmpChoice is false (i.e., multiple amps phases are used).
AmpsPhase1 | Amperage Phase 1 | - | <cfif NOT variables.newRecord>: Checks if the record is not new. If the form is for an existing record (i.e., the user is editing an existing log), the value will be pre-populated with the AmpsPhase1 from the logRecord object. If newRecord is true (meaning it's a new entry), the value will be empty. | required |  |  |  | Same as AmpsPhase2.
AmpsPhase2 | Amperage Phase 2 | - | <cfif NOT variables.newRecord>: This checks if the record is not new. If the record exists (i.e., it is being edited), it retrieves the value of AmpsPhase2 from the logRecord object. variables.logRecord.getAmpsPhase2(): This method call retrieves the AmpsPhase2 value from the logRecord object. If the record already has an AmpsPhase2 value (i.e., the form is being used to edit an existing record), that value will be pre-filled into the input field. If the record is new, the field will remain empty (as variables.newRecord will be true). | required |  |  |  | Used to show alert if above threshold (>15%). No direct required validation but monitored.
AmpsPhase3 | Amperage Phase 3 | - | If the record is not new (variables.newRecord is false), it retrieves the existing value of AmpsPhase3 from the logRecord object and pre-fills the input field. variables.logRecord.getAmpsPhase3(): This method call retrieves the value of AmpsPhase3 from the logRecord object. If the record is new (variables.newRecord is true), the input field will be empty. This is useful for creating new records where the user needs to enter a new value for AmpsPhase3. | required |  |  |  | Included only if chiller VoltageChoice != 2.
AmpImbalance | Amperage imbalance percentage | [6 empty] | Included only if chiller VoltageChoice == 0.
VoltsPhase1 | Voltage Phase 1 | - | If variables.newRecord is not true (i.e., it's an existing record), then the value of the input field is dynamically set to the value returned by variables.logRecord.getVoltsPhase1(). variables.logRecord.getVoltsPhase1() would return the value for the voltage in Phase 1 of the chiller (for example, it could return 220 or any other numeric value depending on the data stored in the system). If variables.newRecord is true (i.e., it's a new record), the input field is left empty because no value is provided. | required |  |  |  | Same as VoltsPhase2.
VoltsPhase2 | Voltage Phase 2 | - | If variables.newRecord is false (indicating that this is an existing record), it fetches the stored value for the "VoltsPhase2" field using variables.logRecord.getVoltsPhase2(). For example, if the voltage for Phase 2 was previously recorded as 220, then variables.logRecord.getVoltsPhase2() would return 220, and the input field will display 220. If variables.newRecord is true (indicating that this is a new record), no value is set initially, and the input field will be blank for the user to fill. | required |  |  |  | Used to show alert if above threshold (>2%). No direct required validation but monitored.
VoltsPhase3 | Voltage Phase 3 | - | If variables.newRecord is false (i.e., the record is not new), it fetches the value for VoltsPhase3 from variables.logRecord.getVoltsPhase3(). This means that if an existing record is being edited, the field will be pre-filled with the previously saved voltage value for Phase 3 (for example, 220). If variables.newRecord is true (i.e., it’s a new record), the field will be empty for the user to fill in. | required |  |  |  | Included if CompOPIndicator is 0 or 1. Numeric validation applied.
VoltImbalance | Voltage imbalance percentage | [6 empty] | Included if CompOPIndicator is 0.
OilPresHigh | Oil pressure high | - | NOT variables.newRecord: This means that if the record is not new (i.e., it’s being edited), the input field will be pre-filled with the value of OilPresHigh from the logRecord object. The value is formatted using LSNumberFormat(variables.logRecord.getOilPresHigh(), "999.9"). This function formats the number with up to 3 decimal places. If variables.newRecord is true (i.e., it's a new record), the input field will be empty, allowing the user to enter a new value. | required |  |  |  | Included if CompOPIndicator is 2.
OilPresLow | Oil pressure low | - | <cfif NOT variables.newRecord>: This condition checks if the record is not new (i.e., it’s an existing record). #LSNumberFormat(variables.logRecord.getOilPresLow(), '999.9')#: If the record is not new, the value of Oil Pressure (Low) from the logRecord object is retrieved using getOilPresLow() and formatted using LSNumberFormat to display the value with one decimal place (e.g., 123.4). If the record is new (variables.newRecord is true), the field will be empty, allowing the user to input the value for Oil Pressure (Low). | required |  |  |  | Included if CompOPIndicator is not 3. Numeric validation applied.
OilPresDif | Oil pressure difference | - | <cfif NOT variables.newRecord>: This condition checks if the record is not new (i.e., the user is editing an existing record). #LSNumberFormat(variables.logRecord.getOilPresDif(), '999.9')#: If the record is not new, the value of Oil Pressure Difference (retrieved from variables.logRecord.getOilPresDif()) is formatted using the LSNumberFormat function to display it with one decimal place (e.g., 12.3). If the record is new (variables.newRecord is true), the input field will be empty, and the user will be able to enter the Oil Pressure Difference value. | required |  |  |  | Same as OilSumpTemp.
OilSumpTemp | Oil sump temperature | - | <cfif NOT variables.newRecord>: This condition checks if the record is not new (i.e., the user is editing an existing record) #LSNumberFormat(variables.logRecord.getOilSumpTemp(), '999.9')#: If the record is not new, the value of Oil Sump Temperature (retrieved from variables.logRecord.getOilSumpTemp()) is formatted using the LSNumberFormat function to display it with one decimal place (e.g., 12.3). For New Records: If the record is new, the input field will be empty, and the user can enter the value for Oil Sump Temperature. | required |  |  |  | Included if chiller has HaveBearingTemp true. Numeric validation applied.
OilLevel | Oil level percentage | - | <cfif NOT variables.newRecord>: This condition checks whether the record is not new (i.e., the user is editing an existing record). #LSNumberFormat(variables.logRecord.getOilLevel(), '999.9')#: If the record is not new, the Oil Level value is retrieved from variables.logRecord.getOilLevel(). The LSNumberFormat function formats the value to show one decimal place (e.g., 80.5). For New Records: If it is a new record, the field will be empty (the user will enter the value). | required |  |  |  | Validated for range correctness by JS _isValidRunHours.
BearingTemp | Bearing temperature | - | <cfif NOT variables.newRecord AND len(variables.logRecord.getBearingTemp())>: This checks if the record is not new and if the Bearing Temperature value exists (i.e., it's not empty). The field will be populated with the current value of variables.logRecord.getBearingTemp(). #Trim(LSNumberFormat(variables.logRecord.getBearingTemp(), '999.9'))#: If the conditions are met, it formats the Bearing Temperature value using LSNumberFormat to display the value with one decimal place. Trim() ensures that there are no extra spaces around the value. For New Records: If it is a new record, the value of this field will be empty (i.e., no initial value). The user is expected to enter the value. | required |  |  |  | User choice for beginning run hours recording; alert on click.
RunHours | Compressor run hours | - | <cfif NOT variables.newRecord>: Checks if the record is not new. If the record is being edited, it will populate the input field with the Run Hours value from the existing record. #LSNumberFormat(variables.logRecord.getRunHours(),"999,999.9")#: If the record is not new, it formats the Run Hours value to display it with one decimal place, such as 150.5. LSNumberFormat formats the number with a specific pattern (in this case, allowing up to 999,999 with one decimal place). For New Records: If the record is new (i.e., variables.newRecord is true), the input field will be empty and ready for the user to input a value. | required |  |  |  | Included if chiller has HavePurge. Shown alone or combined with PurgeTimeHr based on PurgeReadingUnit.
PurgeTime | Purge total pumpout time (min or hr + min) | - | ColdFusion Logic: If the record is not new (NOT variables.newRecord), the value of the Purge Time in minutes will be populated from the existing record. LSNumberFormat: This function is used to format the Purge Time in minutes value. It is formatted to have up to 3 digits before the decimal and 1 decimal place. If the record is new, the field will be empty, and the user is expected to input the Purge Time in minutes. size="10" maxlength="10" If the record is not new, the value of Purge Time in hours will be populated from the existing record, formatted to one decimal place. For a new record, the field will be empty, and the user will input the value. | required |  |  |  | Included if chiller has HavePurge and PurgeReadingUnit false.
UserNote | Operator notes | - | If it's not a new record, the value of variables.logRecord.getUserNote() is placed inside the <textarea>. This is typically a user note that was saved previously. #Trim(...)#: The Trim function is used to remove any leading or trailing spaces from the note text. If it's a new record, the <textarea> will be empty because the ColdFusion code will not output any value in that case. | required |  |  |  | Free text.
AirTemp | Outside air temperature | - | <cfif NOT variables.newRecord>: This is a ColdFusion condition that checks if the record is not new (i.e., it is an existing record). #LSNumberFormat(variables.logRecord.getAirTemp(),"999.9")#: If the record is not new, the AirTemp field will be pre-filled with the value of variables.logRecord.getAirTemp(), formatted to 1 decimal place using the LSNumberFormat function. LSNumberFormat(..., "999.9"): This function formats the number (in this case, the air temperature) to a string with up to one decimal place. If the air temperature was 24.5, it would be displayed as 24.5. If the record is new (variables.newRecord), the value will be left empty (default behavior for the input field), so the user will be prompted to enter a new air temperature value. | required |  |  |  | Numeric validation applied if present.
TargetCost | Target energy cost | [6 empty] | Monetary value, no validation shown in form.
ActualCost | Actual energy cost | [6 empty] | Monetary value.
LossCost | Energy loss cost | [6 empty] | Monetary value.
TotalLoss | Total energy loss | [6 empty] | Monetary value.
CondInletLoss | Condenser inlet loss | [6 empty] | Numeric value.
CondInletLossCost | Cost of condenser inlet loss | [6 empty] | Monetary value.
CondApproach | Condenser approach temperature difference | [6 empty] | Numeric value.
CondAppVariance | Variance in condenser approach | [6 empty] | Numeric value.
CondAppLoss | Condenser approach loss | [6 empty] | Numeric value.
CondAppLossCost | Cost of condenser approach loss | [6 empty] | Monetary value.
EvapTempLoss | Evaporator temperature loss | [6 empty] | Numeric value.
EvapTempLossCost | Cost of evaporator temperature loss | [6 empty] | Monetary value.
EvapAppVariance | Variance in evaporator approach | [6 empty] | Numeric value.
EvapApproach | Evaporator approach temperature difference | [6 empty] | Numeric value.
EvapAppLoss | Evaporator approach loss | [6 empty] | Numeric value.
EvapAppLossCost | Cost of evaporator approach loss | [6 empty] | Monetary value.
NonCondensables | Amount of non-condensable gases | [6 empty] | Numeric value.
NonCondLoss | Non-condensable loss | [6 empty] | Numeric value.
NonCondLossCost | Cost of non-condensable loss | [6 empty] | Monetary value.
DeltaLoss | Delta loss | [6 empty] | Numeric value.
DeltaLossCost | Cost of delta loss | [6 empty] | Monetary value.
CondFlow | Condenser flow | [6 empty] | Numeric value.
EvapFlow | Evaporator flow | [6 empty] | Numeric value.
EnergyCost | Energy cost | [6 empty] | Monetary value.
ActualLoad | Actual load | [6 empty] | Numeric value.
CalculatedCondRefrigTemp | Calculated condenser refrigerant temperature | [6 empty] | Numeric value.
CalculatedEvapRefrigTemp | Calculated evaporator refrigerant temperature | [6 empty] | Numeric value.
ValidRunHours | Bit/Boolean flag for valid run hours | [6 empty] | Boolean flag, no input from user.
KWHLoss | Energy loss in kilowatt-hours | [6 empty] | Numeric value.
BTULoss | Energy loss in BTUs | [6 empty] | Numeric value.
CO2 | Carbon dioxide emission | [6 empty] | Numeric value.

## Sheet2
Field / Column Name | Required? | Conditions for Required / Passing | Form Visibility / Input Condition | Remarks / Special Cases
ChillerID | Yes | Always required | Hidden input (passed from selected chiller) | Comes from selected chiller on screen
UserID | Yes | Always required | Not in form; set in backend/session | Logged in user
ChangeUserID | Yes | Always required | Not in form; backend manages | Tracks who changed the record
ChangeDate | Yes | Always required | Not in form; set to current timestamp | Auto-managed
ReadingDate | Yes | Must be valid date/time and not in future | Shown as date input + time inputs (displayReadingDate, RTHour, RTMinute, ampm) | Validation enforces no future date/time; reformatted before submit
CondInletTemp | Conditionally required | Required if field shown | Always shown input | Numeric field, validated
CondOutletTemp | Conditionally required | Required if field shown | Always shown input | Numeric field, validated
CondRefrigTemp | Conditionally required | Required if shown as input | Shown as input if NOT chiller.getHighPressureRefrig(); otherwise read-only or hidden | Read-only display for high pressure refrigerant chillers if editing
CondPressure | Optional | Passed if numeric | Always shown input (optional) | Numeric validation
CondAPDrop | Optional | Passed if numeric | Always shown input (optional) | Numeric validation
EvapInletTemp | Conditionally required | Required if field shown | Always shown input | Numeric field, validated
EvapOutletTemp | Conditionally required | Required if field shown | Always shown input | Numeric field, validated
EvapRefrigTemp | Conditionally required | Required if shown as input | If chiller.getUseEvapRefrigTemp() is true, show input; else show calculated read-only value | If numeric value missing, calculated value is shown
EvapPressure | Optional | Passed if numeric | Always shown input (optional) | Numeric validation
EvapAPDrop | Optional | Passed if numeric | Always shown input (optional) | Numeric validation
AmpsPhase1 | Conditionally required | Required if field shown | Always shown input | Numeric field, validated
AmpsPhase2 | Conditionally shown/required | Shown only if chiller.getAmpChoice() is false | Input shown only if chiller.getAmpChoice() == false
AmpsPhase3 | Conditionally shown/required | Shown only if chiller.getAmpChoice() is false | Input shown only if chiller.getAmpChoice() == false
AmpImbalance | Optional | Used only for alert display | Not input; alert displayed if imbalance > threshold | Alert shown if > 15%
VoltsPhase1 | Conditionally shown/required | Shown if chiller.getVoltageChoice() != 2 | Input shown conditionally
VoltsPhase2 | Conditionally shown/required | Shown if chiller.getVoltageChoice() == 0 | Input shown conditionally
VoltsPhase3 | Conditionally shown/required | Shown if chiller.getVoltageChoice() == 0 | Input shown conditionally
VoltImbalance | Optional | Used only for alert display | Not input; alert displayed if imbalance > threshold | Alert shown if > 2%
OilPresHigh | Conditionally shown/required | Shown if chiller.getCompOPIndicator() = 0 or 1 | Input shown conditionally
OilPresLow | Conditionally shown/required | Shown if chiller.getCompOPIndicator() = 0 | Input shown conditionally
OilPresDif | Conditionally shown/required | Shown if chiller.getCompOPIndicator() = 2 | Input shown conditionally
OilSumpTemp | Conditionally shown/required | Shown if chiller.getCompOPIndicator() != 3 | Input shown conditionally
OilLevel | Conditionally shown/required | Shown if chiller.getCompOPIndicator() != 3 | Input shown conditionally
BearingTemp | Conditionally shown/required | Shown if chiller.getHaveBearingTemp() is true | Input shown conditionally
RunHours | Conditionally required | Required with validation against last/next run hours | Always shown input | Validation includes complex logic checking against previous run hours readings
RunHourStart (checkbox) | Optional | Always present | Checkbox shown | Alerts user when checked
PurgeTimeMin | Conditionally shown/required | Shown if chiller.getHavePurge() is true and getPurgeReadingUnit() true | Input shown conditionally
PurgeTimeHr | Conditionally shown/required | Shown if chiller.getHavePurge() is true and getPurgeReadingUnit() false | Input shown conditionally
UserNote | Optional | Always passed if provided | Textarea always shown | Free text notes
AirTemp | Conditionally required | Required if shown | Input shown always | Numeric field, validated

## Logic
Business Logic: Calculating Purge Time | Explanation
<cftry> <cfquery name="checkUnit" datasource="#variables.dsn#"> SELECT PurgeReadingUnit FROM chillercheck.Chillers WHERE ChillerID = #arguments.logRecord.getChillerID()# </cfquery> <cfif checkUnit.PurgeReadingUnit> <cfset purgeTime = arguments.logRecord.getPurgeTimeMin() /> <cfelse> <cfif isNumeric(arguments.logRecord.getPurgeTimeMin())> <cfset purgeTimeMinTemp = arguments.logRecord.getPurgeTimeMin() /> </cfif> <cfif isNumeric(arguments.logRecord.getPurgeTimeHr())> <cfset purgeTimeHrTemp = arguments.logRecord.getPurgeTimeHr() /> </cfif> <cfset purgeTime = (purgeTimeHrTemp * 60) + purgeTimeMinTemp /> </cfif> | Queries the Chillers table for PurgeReadingUnit field of the chiller identified by logRecord.getChillerID(). If PurgeReadingUnit is truthy (likely meaning the unit is in minutes): - Takes purge time directly from logRecord.getPurgeTimeMin(). Otherwise (likely hours + minutes unit): - Checks if purge minutes (getPurgeTimeMin()) is numeric, stores it. - Checks if purge hours (getPurgeTimeHr()) is numeric, stores it. - Calculates total purge time in minutes as (hours * 60) + minutes. This logic ensures purge time is stored in a consistent unit (minutes) regardless of original input unit.

## AddEdit Log
Aspect | File / Location | Code Reference / Function Name | Description / Notes | Related Parameters / Variables
Form UI rendering | e.g., /views/logRecordForm.cfm | N/A (template) | The ColdFusion template rendering the add/edit form with dynamic field visibility controlled via <cfif> tags | action, buildingId, chillerId
Field Show/Hide Logic | /views/logRecordForm.cfm | Inline <cfif> and JS | Fields conditionally shown based on chiller type, action, or permissions | logRecord bean properties, action
Parameters controlling UI | Controller or front controller | e.g., /controllers/LogController.cfc or routing CFM file | Sets request scope variables for UI based on URL/form input | action, logId, buildingId, etc.
Client-side validation | /assets/js/logRecordValidation.js or inline JS | JS functions validating fields before submit | Numeric checks, required fields, patterns | Form input element attributes
Server-side validation | LogRecordDAO.cfc | createLogRecord(), updateLogRecord() | Uses CFML isNumeric(), null handling, required checks, and data type safety | All logRecord.getXXX() getters
Purge Time Calculation | LogRecordDAO.cfc | createLogRecord(), updateLogRecord() | Reads unit from DB, converts hours+minutes to minutes for consistent storage | purgeTime, purgeTimeMinTemp, purgeTimeHrTemp
Save button request handler | Controller CFC or .cfm action page | e.g., /controllers/LogController.cfc or /saveLogRecord.cfm | Receives form POST, calls DAO methods to create/update record | form data posted
Database Insert/Update | LogRecordDAO.cfc | createLogRecord(), updateLogRecord() | Inserts/updates log record with parameterized SQL queries | Uses <cfqueryparam> for safety
Error handling | LogRecordDAO.cfc | Wrapped in <cftry> / <cfcatch> | Returns boolean success/fail; logs or reports errors | ret variable
Post-save processing | Controller CFC | After DAO call | Redirects user, shows success/error messages | N/A
Category | Item / Field | Description | Source / Code Location | Notes / Explanation
Form Metadata | Form file | logRecordForm.cfm | extensions/includes/views/dataEntry/logRecordForm.cfm | Core CFML view file rendering the Add/Edit Log Record form
| Event Arguments | chillerBean, locationBean, logRecordBean, optionally badLogRecordBean, sessionUser, logVals | event.getArg() calls at top of the file | Key input data objects passed into the form to render correct info and form state
| New or Edit mode | variables.newRecord = true/false based on logRecord.getLogID() or badRecordID presence | CFML conditional logic early in the file | Determines if form is adding a new record or editing existing
Form Action & Submission | Form action URL | index.cfm?event=updateLogRecord | <form action="index.cfm?event=updateLogRecord"> | Where form POSTs data to on submit
| Form onsubmit | onsubmit="return anglicizeTheForm()" | <form ... onsubmit="return anglicizeTheForm()"> | Converts locale-specific numbers & dates to standard before submitting
| Hidden Inputs | logID, chillerID, badRecordID, readingDate | Hidden <input> fields in form | Identify record, chiller, and final combined date/time for server processing
| Continuation Radio Buttons | Option to save and return to dashboard or add another record | <input type="radio" name="continuationEvent" ...> | Controls post-save navigation behavior
Locale & Formatting | Temp Units | &ordm; C if chiller.getIsMetric(), else &ordm; F | CFML if/else conditions | Used throughout form labels and fields for temperature units
| Pressure Units | Conditional units like KPA, PSIG, lb., in. Hg. based on chiller configuration | CFML variable assignments (OPDifUnit, OPHiUnit, OPLoUnit) | For display beside pressure input fields
| Number Formatting | Handles non-English decimal delimiters with JS reformat(), anglicizeTheForm(), and related functions | JS block at top | Converts numbers input in locale-specific format to English decimal notation before submit
| Date Formatting | Uses Tigra calendar JS, locale-aware display and parsing | Calendar scripts included, displayReadingDate input | Provides localized date picker and date display
| Reading Date & Time Split | Date (displayReadingDate) is visible; time split into RTHour, RTMinute, ampm selects | Separate input fields | Combined into hidden readingDate on submit by JS
Form Fields & Conditional Display | Chiller Specs | Read-only display of chiller manufacturer, model, year, tons, refrigerant | HTML table near top | Displayed info for context
| Temperatures | Multiple temperature fields: CondInletTemp, EvapInletTemp, CondOutletTemp, EvapOutletTemp, CondRefrigTemp, EvapRefrigTemp | Input fields in form with conditional display | Fields appear based on chillerBean flags (getHighPressureRefrig(), getUseEvapRefrigTemp())
| Pressures | Fields like CondPressure, EvapPressure, CondAPDrop, EvapAPDrop | Input fields with units | Appear with units dependent on chiller configuration
| Electrical Fields | Fields for amps and volts, conditionally shown based on chiller.getAmpChoice(), chiller.getVoltageChoice(), and chiller.getIsSteam() | Conditionally rendered <input> fields | For non-steam chillers amps/volts phases shown; for steam chillers, "Actual Steam Flow Rate" shown
| Oil Pressure & Temp Fields | Oil pressure high/low/diff, oil sump temp, oil level, bearing temp | Conditional on chiller.getCompOPIndicator(), chiller.getHaveBearingTemp() | Different input sets rendered based on compressor configuration
| Run Hours | Input with checkbox to start run hours recording | RunHours field and RunHourStart checkbox | Checkbox triggers alert on click (doRHCheck())
| Purge Time | Conditionally show purge time in minutes or hours+minutes based on chiller.getHavePurge(), chiller.getPurgeReadingUnit() | Input fields with conditional rendering | Purge time split into mins or hrs+mins depending on chiller setting
| Operator Notes | <textarea> for user notes | Always visible | Free-text notes
Validation Logic | Dynamic Field Validation | Client-side validations generated dynamically using qForm JS object based on logVals query data | JS loop over variables.logVals | Fields get required flags, type validations (int/float), range checks (valMin, valMax), inter-field comparisons (ComparisonType)
| Run Hours Validation | Custom JS function _isValidRunHours() to check run hours within limits relative to last and next run hours | Inline JS block | Uses server-passed variables (lastRunHours, nextRunHours, reading dates) to validate RunHours input
| Reading Date Validation | Custom JS _isValidReadingDate() to ensure reading date is not future, time is valid | Inline JS block | Checks date/time validity before submit
| Number Reformat on Submit | anglicizeTheForm() formats all numeric fields to consistent decimal delimiter and combines reading date/time | JS function called on form submit | Ensures server receives consistent numeric and date format
User Interaction & UX | Tooltips | showTip() and hideTip() JS functions triggered on focus/blur of inputs | onFocus="showTip('div_FieldName')" etc. | Show contextual help messages next to fields
| Alerts | Alert on checking "RunHourStart" checkbox | doRHCheck() JS function | Warns user about starting run hours recording
| Messages | Display error or status messages passed in variables.message | Top-level CFML conditional displaying message as alert or inline | Shows server messages on form load
Variables / Conditions / Actions List
Variable | Purpose / Description | Conditions Affecting It | Actions / Usage
variables.chiller | The chiller object for current record | Used for most display and conditional checks | Controls form field visibility, units, input enable/disable, conditional rendering of temperature, pressure fields
variables.location | Location/plant object | Used for locale settings | Sets locale for date/time and number formatting
variables.logRecord | The log record bean being edited or new | Presence of logRecord.getLogID() or badRecordID sets newRecord | Provides pre-filled values in form fields; controls whether form is Add or Edit
variables.badRecordID | Bad log record ID, if editing a bad record | If present, form loads bad record details | Enables error messaging and possibly disables some inputs
variables.sessionUser | User currently logged in | Used to display operator name if logRecord user name is empty | Shows user name in Operator field
variables.newRecord | Boolean: true if adding new, false if editing | Set true if no logID and no badRecordID and no meaningful cond inlet temp | Controls default values, field enable/disable, which form parts display
variables.tempIndicator | Temperature unit string (°C or °F) | Based on chiller.getIsMetric() | Used in temperature field labels
variables.OPDifUnit | Oil Pressure Diff unit | Based on chiller config | Used in oil pressure input labels
variables.OPHiUnit | Oil Pressure High unit | Based on chiller config | Used in oil pressure input labels
variables.OPLoUnit | Oil Pressure Low unit | Based on chiller config | Used in oil pressure input labels
variables.message | Any message to display to user | Set if passed in event args | Shown as alert or inline error
variables.logVals | Query with validation rules and field metadata | Used in JS validation loop | Dynamically creates validation rules for form fields
variables.decimalDelimiter | Locale-specific decimal delimiter | Derived from LSNumberFormat("9.99") | Used in JS for number formatting conversions
variables.badLogRecord | Bean for bad log record if editing a bad record | Only set if badLogRecordBean argument is passed | Used for error display and field pre-fill
Key Conditions & Controls
Condition / Expression | Variables Involved | Effect / Action
variables.logRecord.getLogID() OR variables.badRecordID OR logRecord.getCondInletTemp() NEQ 0 | Determines if editing existing record | Sets variables.newRecord = false (Edit mode), else Add mode
variables.chiller.getIsMetric() | Controls unit strings | Sets temperature unit to °C and pressure units to KPA or else sets to imperial units
variables.chiller.getHighPressureRefrig() | Determines display of CondRefrigTemp input | If true, display as read-only, else editable input
variables.chiller.getUseEvapRefrigTemp() | Controls display of evaporator refrigerant temp field | If false, show calculated evaporator refrigerant temp, else editable field
variables.chiller.getCompOPIndicator() | Determines which oil pressure fields to show | 0 = High & Low Oil Pressure; 1 = High Oil Pressure only; 2 = Oil Pressure Diff
variables.chiller.getHaveBearingTemp() | Whether to show Bearing Temp field | If true, show input for bearing temperature
variables.chiller.getHavePurge() | Whether to show Purge Time inputs | If true, show purge time input(s)
variables.chiller.getPurgeReadingUnit() | If purge time is recorded in minutes (true) or hours+minutes (false) | Controls purge time input(s) display
variables.chiller.getAmpChoice() | Controls visibility of Amps Phase 2 & 3 | If false, show Amps Phase 2 & 3 inputs
variables.chiller.getVoltageChoice() | Controls visibility of Volts Phase 1, 2 & 3 | Based on value (0, 1, 2), shows/hides volts phase inputs
variables.chiller.getIsSteam() | Controls showing steam flow rate vs electrical amps | If steam chiller, show "Actual Steam Flow Rate" field instead of amps phases
variables.logRecord.getAmpImbalance() > 15 OR getVoltImbalance() > 2 | Checks electrical imbalance | Shows alert message in form
variables.message | Server or client message to user | Shows alert on form load
Key Actions & JS Validations
Action / Function | Triggered By / Related Variable | Purpose / Description
anglicizeTheForm() | Called on form submit | Converts localized numbers and dates to English decimal format and standard date/time format before submit
reformat(), reformatBeforeSubmit() | Used internally by anglicize functions | Replace locale decimal delimiters with English (dot)
setSeparator() | Called on locale radio button toggle | Changes number display formatting between US and localized formatting
doRHCheck() | Called on "RunHourStart" checkbox click | Alerts user about starting run hours recording
_isValidRunHours() | Custom validation attached to RunHours field | Validates Run Hours input is within logical limits based on last and next readings passed from server
_isValidReadingDate() | Custom validation attached to Reading Date fields | Ensures reading date is not in future, time parts are filled and valid
logForm object (qForm) | Dynamically built from variables.logVals query | Creates client-side validation rules (required, integer/float, range, comparisons) for each numeric input field
showTip() / hideTip() | OnFocus / OnBlur of inputs | Shows contextual help messages on fields
Variable Name | Type/Origin | Controlled By Condition(s) | Key Usage / Action
logRecord.getLogID() | Argument bean | If exists, newRecord = false | Form mode, pre-fill values
badRecordID | Argument | If exists, newRecord = false | Edit bad record mode
chiller.getIsMetric() | Argument | Sets temp and pressure units | Labels and input units
chiller.getHighPressureRefrig() | Argument | Controls refrigerant temp input/edit display | CondRefrigTemp input field visibility
chiller.getUseEvapRefrigTemp() | Argument | Controls evaporator refrigerant temp input | EvapRefrigTemp input field display
chiller.getCompOPIndicator() | Argument | Controls oil pressure fields shown | OilPresHigh, OilPresLow, OilPresDif inputs
chiller.getHaveBearingTemp() | Argument | Controls bearing temp field visibility | BearingTemp input field
chiller.getHavePurge() | Argument | Controls purge time inputs | PurgeTimeHr / PurgeTimeMin inputs
chiller.getPurgeReadingUnit() | Argument | Controls purge time unit display | PurgeTime in minutes or hours+minutes
chiller.getAmpChoice() | Argument | Controls display of AmpsPhase2 & AmpsPhase3 inputs | Electrical input fields
chiller.getVoltageChoice() | Argument | Controls voltage phase inputs visibility | VoltsPhase1, VoltsPhase2, VoltsPhase3 inputs
chiller.getIsSteam() | Argument | Controls display of steam flow rate vs amps | Either "Actual Steam Flow Rate" or Amps phase inputs
logRecord.getAmpImbalance() | Argument | Threshold > 15% triggers alert message | Shows imbalance warning
logRecord.getVoltImbalance() | Argument | Threshold > 2% triggers alert message | Shows imbalance warning
variables.message | Passed in event arg | If not empty, shows alert or inline error | Displays messages to user
logVals | Query | Contains validation rules and labels | Used to generate client-side validations dynamically

## LogEntryManagement
Note:- For all the business logic and calculations of log module refer to the following files.
logCalc.cfc, logRecordBean.cfc, logRecordBO.cfc, logRecordDAO.cfc, logRecordGateway.cfc and logRecordListener.cfc
Field Name | Required / Optional | Show/Hide Condition | Validation | How Populated / Calculated | Remarks / Notes | Info Text
ChillerID | Required | Always shown (always included) | Must be valid integer | Comes from selected chiller context | Essential foreign key
UserID | Required | Hidden | Must be valid integer | Set by backend on save (current logged-in user) | Tracks who created the log record
ChangeUserID | Required | Hidden | Must be valid integer | Set by backend on save/update | Tracks who last modified record
ChangeDate | Required | Hidden | Timestamp | Set by backend on save (current date/time) | Timestamp of creation/modification
ReadingDate | Required | Always shown (date/time inputs) | Must be valid date/time, not a future date | User Input. | Frontend validation prevents future date/time
ReadingDate UTC | Calculated | Hidden | Timestamp | Calculated in UTC format based on the reading date
Chiller Run Hours | Required | Always Shown | Numeric, validated with custom range check | User Input. | Min = 0 & Max = lastRunHours + hoursBetweenLastDates + 8 | Enter the running hours of the chiller from the chiller's reading.
Begin Recording Run Hours | Required | Always Shown | Yes or No, By default No | User Input. | If yes is selected, then the above validation won't be considered. | Check this box if you want the system to start validating the run hours from this log entry, if you check we will consider the hours entered as correct without validating it against the value of the past entry.
CondInletTemp | Required | Always shown | Numeric, value should be between 40 to 105. | User Input. Unit will be based on the chiller's selected unit. | Input field | Enter the temperature of the fluid (usually water or air) entering the condenser to absorb and carry away heat from the refrigerant.
CondOutletTemp | Required | Always shown | Numeric, value should be between 40 to 120. | User Input. Unit will be based on the chiller's selected unit. | Input field | Enter the temperature of the fluid (usually water or air) exiting the condenser after absorbing heat from the refrigerant.
CondRefrigTemp | Required | Shown as input if Enter a Saturated Refrig. Temp == false; else shown as readonly display | Numeric, value should be between 50 to 120. | User input or backend calculated (if high-pressure refrigerant). User Input. Unit will be based on the chiller's selected unit. | Readonly if high pressure refrigerant | Enter the temperature of the refrigerant as it releases heat and changes from a vapor to a liquid within the condenser.
CondPressure | Optional | Always shown | Numeric, value should be between -18 to 33. | Field - Actual Condenser Water Pressure Drop Unit value is the unit of this field. | Nullable | Enter the pressure of the refrigerant within the condenser as it condenses from vapor to liquid by releasing heat.
CondAPDrop | Optional | Always shown | Numeric, value should be between 0 to 115. | Field - Condenser Pressure Unit value is the unit of this field. | Nullable | Enter the decrease in air pressure as it flows across the condenser coil, indicating airflow resistance and coil cleanliness.
EvapInletTemp | Required | Always shown | Numeric, value should be between -60 to 80. | User Input. Unit will be based on the chiller's selected unit. | Input field | Enter the temperature of the fluid (usually water) entering the evaporator to be cooled by the refrigerant.
EvapOutletTemp | Required | Always shown | Numeric, value should be between -60 to 80. | User Input. Unit will be based on the chiller's selected unit. | Input field | Enter the temperature of the fluid exiting the evaporator after being cooled by the refrigerant.
EvapRefrigTemp | Required | Shown if Saturated Refrig. Temp. field == Yes; if its set as No the field will be hidden from add chiller. | Numeric, value should be between -60 to 80. | User Input. Unit will be based on the chiller's selected unit. | Depends on chiller config | Enter the temperature of the refrigerant as it absorbs heat and evaporates from liquid to vapor inside the evaporator.
EvapPressure | Optional | Always shown | Numeric, value should be between -50 to 2. | User Input. Unit will be based on the chiller's Evaporator Pressure Unit's selected value. | Nullable | Enter the pressure of the refrigerant within the evaporator as it absorbs heat and evaporates into a vapor.
EvapAPDrop | Optional | Always shown | Numeric, value should be between 0 to 115. | User Input. Unit will be based on the chiller's Actual Chill Water Pressure Drop Unit's selected value. | Nullable | Explain the difference in pressure of the fluid (usually water) between the evaporator inlet and outlet, indicating flow resistance.
AmpsPhase1 / Pct. Load | Required | Always shown: In chiller screen for Amperage Choice whatever value is chosen this field is shown. | Numeric, value should be between 0 to 30. | If data is entered in the amps 1 field, it will be divided by 100 & stored, if it is pct. load the data will be stored as it is. | Input field | Amps Phase 1 : Enter the value for amps phase 1. % Load : Enter the % load of the chiller.
AmpsPhase2 | Required if getAmpChoice() == false | Shown: If in chiller screen for Amperage Choice value chosen = 3-Phase, Else this field is hidden. | Numeric, value should be between 0 to 30. | User input | Conditional display | Amps Phase 2 : Enter the value for amps phase 2.
AmpsPhase3 | Required if getAmpChoice() == false | Shown: If in chiller screen for Amperage Choice value chosen = 3-Phase, Else this field is hidden. | Numeric, value should be between 0 to 30. | User input | Conditional display | Amps Phase 2 : Enter the value for amps phase 3.
AmpImbalance | Calculated | Shown always, alert shown if value > 15% | Numeric (informational) | Calculated or user input | Alert triggers on frontend if >15%
VoltsPhase1 | Required if getVoltageChoice() != 2 | Show if in chiller screen for "Voltage Choice" = 1-Phase or 3-Phase. Hide if voltageChoice not "Do Not Log Voltage". | Numeric, value should be between 255 to 345. | User input | Conditional display | Enter the phase 1 volts.
VoltsPhase2 | Required if getVoltageChoice() == 0 | Show if in chiller screen for "Voltage Choice" = 3-Phase. Else this field is hidden. | Numeric, value should be between 255 to 345. | User input | Conditional display | Enter the phase 2 volts.
VoltsPhase3 | Required if getVoltageChoice() == 0 | Show if in chiller screen for "Voltage Choice" = 3-Phase. Else this field is hidden. | Numeric, value should be between 255 to 345. | User input | Conditional display | Enter the phase 3 volts.
VoltImbalance | Calculated | Shown always, alert shown if value > 2% | Numeric (informational) | Calculated or user input | Alert triggers on frontend if >2%
OilPresHigh | Required if getCompOPIndicator() in [0,1] | Shown if in chiller screen, Oil Pressure Differential = "Enter High & Low Pressure" or "Enter High Pressure Only" | Unit For English Metric: Lb. ¦ 0 to 200 Unit For SI Metric: KPA ¦ 0 to 1379 | User input | Conditional display | Compressor oil pressure high value at which lubricating oil is supplied to the compressor’s moving parts to ensure proper lubrication & prevent wear.
OilPresLow | Required if getCompOPIndicator() == 0 | Shown if in chiller screen, Oil Pressure Differential = "Enter High & Low Pressure" | Unit For English Metric: in. Hg. ¦ 0 to 200 Unit For SI Metric: KPA ¦ 0 to 677 | User input | Conditional display | Compressor oil pressure low value at which lubricating oil is supplied to the compressor’s moving parts to ensure proper lubrication & prevent wear.
OilPresDif | Required if getCompOPIndicator() == 2 | Shown if in chiller screen, Oil Pressure Differential = "Enter Differential Directly" | Unit For English Metric: Lb. ¦ 0 to 200 Unit For SI Metric: KPA ¦ 0 to 1379 | User input | Conditional display | Compressor oil pressure difference at which lubricating oil is supplied to the compressor’s moving parts to ensure proper lubrication & prevent wear.
OilSumpTemp | Required if getCompOPIndicator() != 3 | Shown always, hidden if in chiller screen, Oil Pressure Differential = "Do Not Log Lube System" | Unit For English Metric: ºF ¦ 0 to 200 Unit For SI Metric: ºC ¦ -18 to 93 | User input | Conditional display | Enter the value for Oil Sump Temperature of the chiller's compressor.
OilLevel | Required if getCompOPIndicator() != 3 | Shown always, hidden if in chiller screen, Oil Pressure Differential = "Do Not Log Lube System" | Numeric, value should be between 0 to 100 | User input | Conditional display | Enter the oil level of the chiller's compressor.
BearingTemp | Required if getHaveBearingTemp() == true | Shown if in chiller screen, Readout for Bearing Temp = Yes, Else hidden. | Unit For English Metric: ºF ¦ 50 to 200 Unit For SI Metric: ºC ¦ 10 to 93 | User input | Conditional display | Enter the temperature of the bearings inside the compressor, indicating the condition of lubrication and mechanical health.
Comp 1 RunHours | Required | Always shown | Numeric, validated with custom range check | User input | Min = 0 & Max = lastRunHours + hoursBetweenLastDates + 8 | Enter compressor's running hours.
Comp 1 Begin Record Reading | Required | Always shown | Yes or No. Default = No | User input |  | Check this box if you want the system to start validating the compressor run hours from this log entry, if you check we will consider the hours entered as correct without validating it against the value of the past entry.
Comp 2 RunHours | Required If Shown | Shown if Chiller.Number of Compressors = 2 | Numeric, validated with custom range check | User input | Min = 0 & Max = lastRunHours + hoursBetweenLastDates + 8 | Enter 2nd compressor's running hours.
Comp 2 Begin Record Reading | Required If Shown | Shown if Chiller.Number of Compressors = 2 | Yes or No. Default = No | User input |  | Check this box if you want the system to start validating the compressor run hours from this log entry, if you check we will consider the hours entered as correct without validating it against the value of the past entry.
PurgeTime | Required if getHavePurge() == true | Show mins only field, if in chiller screen "Purge Total Pumpout Time measured in what units" = "Mins. Only". Show hours & mins field, if in the chiller screen "Purge Total Pumpout Time measured in what units" = "Hrs. & Min." | Numeric, value should be between 0 to 1,000,000. | If hours & mins both fields are shown - Calculate the mins value in DB. For Eg: 1 hr, 30 min = 90 mins will be stored | Depends on purge reading units config | Enter the duration of purge unit, that operates to remove non-condensable gases (like air) from the refrigerant system to maintain efficiency.
UserNote | Optional | Always shown | None | User input | Free text notes | Enter any user notes that would help the viewer to get more clarity about the entry.
AirTemp | Required | Always shown | Numeric, value should be between -30 to 130. | User Input. Unit will be based on the chiller's selected unit. | Ambient air temperature | Enter the chiller's air temperature.
TargetCost | Backend Calculated | Not shown | Numeric | Calculated in backend based on performance metrics | Cost target for performance or energy
ActualCost | Backend Calculated | Not shown | Money type | Calculated or entered via other processes | Actual cost incurred
LossCost | Backend Calculated | Not shown | Money type | Calculated in backend | Loss cost
TotalLoss | Backend Calculated | Not shown | Money type | Sum of various loss costs | Total loss cost
CondInletLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Performance loss related to condenser inlet temp
CondInletLossCost | Backend Calculated | Not shown | Numeric | Backend calculated | Cost of condenser inlet loss
CondApproach | Backend Calculated | Not shown | Numeric | Backend calculated | Approach temperature difference metric
CondAppVariance | Backend Calculated | Not shown | Numeric | Backend calculated | Variance in condenser approach
CondAppLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Loss based on condenser approach
CondAppLossCost | Backend Calculated | Not shown | Numeric | Backend calculated | Cost of condenser approach loss
EvapTempLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Loss related to evaporator temperature
EvapTempLossCost | Backend Calculated | Not shown | Numeric | Backend calculated | Cost of evaporator temperature loss
EvapAppVariance | Backend Calculated | Not shown | Numeric | Backend calculated | Variance in evaporator approach
EvapApproach | Backend Calculated | Not shown | Numeric | Backend calculated | Approach temperature difference metric
EvapAppLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Loss based on evaporator approach
EvapAppLossCost | Backend Calculated | Not shown | Numeric | Backend calculated | Cost of evaporator approach loss
NonCondensables | Backend Calculated | Not shown | Numeric | Backend calculated | Non-condensable gases loss metric
NonCondLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Loss due to non-condensables
NonCondLossCost | Backend Calculated | Not shown | Numeric | Backend calculated | Cost of loss due to non-condensables
DeltaLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Difference loss metric
DeltaLossCost | Backend Calculated | Not shown | Numeric | Backend calculated | Cost associated with delta loss
CondFlow | Backend Calculated | Not shown | Numeric | Backend calculated | Flow rate through condenser
EvapFlow | Backend Calculated | Not shown | Numeric | Backend calculated | Flow rate through evaporator
EnergyCost | Backend Calculated | Not shown | Numeric | Backend calculated | Energy cost calculated
ActualLoad | Backend Calculated | Not shown | Numeric | Backend calculated | Actual system load
CalculatedCondRefrigTemp | Backend Calculated | Not shown | Numeric | Backend calculated | Calculated refrigerant temperature for condenser
CalculatedEvapRefrigTemp | Backend Calculated | Not shown | Numeric | Backend calculated | Calculated refrigerant temperature for evaporator
ValidRunHours | Backend Calculated | Not shown | Boolean | Backend calculated | Indicates if RunHours input is valid
KWHLoss | Backend Calculated | Not shown | Numeric | Backend calculated | Kilowatt-hour loss
BTULoss | Backend Calculated | Not shown | Numeric | Backend calculated | BTU loss metric
CO2 | Backend Calculated | Not shown | Numeric | Backend calculated | Carbon emission metric

## CompanyManagement
Field | Type | Required | Visible/Editable in UI | Validation / Logic Notes | Default / Calculated Values | Remarks
CompanyID | numeric | No | Hidden (used for updates) | Auto-generated in DB? Not shown in form | 0 (default) | Primary key; hidden field in forms
CompanyName | string | Yes (business) | Text input, visible to all | size=30, tabindex=1, class=textElement; assumed required | "" (empty string) | Required logically
CreateDate | date | No | Not editable | Automatically set in DAO insert to current time (Now()) | Now() | System generated
StatusID | numeric | No | Dropdown editable only by admin | Dropdown options populated; hidden input for non-admins | 0 (default) | Special handling if StatusID=3
Address1 | string | No | Text input, visible to all | size=30 | "" | Optional
Address2 | string | No | Text input, visible to all | size=30 | "" | Optional
City | string | No | Text input, visible to all | size=30 | "" | Optional
StateID | string | No | Dropdown, visible to all | Dropdown list; JS validation (checkState function) | "0" or "" | Optional
Zip | string | No | Text input, visible to all | size=10, maxlength=10 | "" | Optional
CountryID | string | No | Dropdown, visible to all | Default selected "USA" if none chosen | "0" or "" | Optional
Phone | string | No | Text input, visible to all | Maxlength 13 size=13 | "" | Optional
Fax | string | No | Text input, visible to all | Maxlength 13 size=13 | "" | Optional
ContactName | string | No | Text input, visible to all | Maxlength 13 size=13 | "" | Optional
ContactEmail | string | No | Text input, visible to all | Maxlength 13 size=13 | "" | Optional
CreditCardTypeID | string | No | Not saved currently | Insert commented out in DAO | "" | Not persisted currently
CreditCardNo | string | No | Not saved currently | Insert commented out in DAO | "" | Not persisted currently
MaxChillers | numeric | No | Text input, admin only | Maxlength 3 size = 3 | "0" | Optional
ParentID | numeric | No | Admin editable via UI when companyType=child | Conditionally visible if companyType == 'child'; dropdown; controlled by JS | 0 | Parent company selection; hidden unless companyType='child'
companyType | string | No | Dropdown admin only | Values: standalone, parent, child; controls UI display | "" | Controls conditional UI like parent company picker visibility
ChangeDate | date | No | Not editable in form | Set manually | Now() (default) | System managed
ChangeUserID | numeric | No | Not editable in form | Set from logged-in user ID | 0 | System managed
Additional Logic & Notes: Form validation: Client-side JS ensures that if Country is USA, State must be selected (checkState()). Conditional UI via checkType() shows/hides Parent company picker based on companyType. Creation and update flow: companyListener.cfc orchestrates creation using session user data and delegates to business logic. Business logic (companyBO) calls DAO (companyDAO) for DB insert with above fields. CreateDate and ChangeDate are managed by system, not user input. Permissions: Non-admins cannot edit status or advanced fields like MaxChillers or companyType. Some fields (e.g., ParentID) only visible when companyType = 'child'. Credit card fields exist in the bean but are not saved to DB currently.
Action Name | Location (File & Function) | Inputs / Parameters | Core Logic / Behavior | Output / Side Effects | Permission / Conditions | Remarks
Create Company | companyListener.cfc - createCompany(event) | companyBean, sessionUser | Calls companyBO.createCompany → companyDAO.createCompany to insert record. Sets ChangeUserID. | Returns success/failure messages; updates session user companies list; triggers demo data if status=3 | Requires valid company data; status=3 triggers demo data creation | Event-driven; main entry point for company creation
| companyBO.cfc - createCompany(companyBean) | Company bean object | Delegates to DAO to persist company data | Success boolean and message struct | N/A | Business logic layer
| companyDAO.cfc - createCompany(companyBean) | Company bean object | Executes SQL INSERT into chillercheck.Companies | Boolean success flag | N/A | Data access layer
Update Company | companyListener.cfc - editCompany(event) | companyBean | If CompanyID exists, fires updateCompany event; else fires createCompany | Delegates to update or create logic | N/A | Decides update vs create
| (Assumed) companyBO.cfc - updateCompany(companyBean) | Company bean object | (Not reviewed in depth, assumed similar to create) | Success/failure message | N/A | Business logic for update (to confirm)
| (Assumed) companyDAO.cfc - updateCompany(companyBean) | Company bean object | (Not explicitly found, assumed for DB UPDATE) | Boolean success flag | N/A | Data access for update (to confirm)
Read Company | companyListener.cfc - readCompany(event) | companyBean, sessionUser | Fetch company details; restricts data if user not admin | Company data populated into bean | User permissions checked | View or API data fetch
List Companies | companyGateway.cfc - getCompanies() | None | Returns list of companies from DB | Query result | N/A | For dropdowns, selections
Set Children | companyListener.cfc - setChildren(event) | companyID, children | Sets child companies for a given parent company | Fires event showCompanyInfo | N/A | Maintains company hierarchy
Create Demo Records | companyBO.cfc - createDemoRecords(companyBean) | companyBean | Generates demo data for performance, locations, chillers if status=3 | Creates related data in DB | Triggered on company with status=3 | Demo data setup for new demo companies
Assign User Company | companyListener.cfc - part of createCompany | sessionUser, companyID | Updates user session with selected company, reorders company list | Updates session user context | Requires authenticated user | Post-creation user context setup
Notes: Delete operation for companies was not found in the reviewed files — possibly managed elsewhere or restricted. Update logic methods in BO and DAO were not found explicitly but implied via event dispatch updateCompany. The listener component is the central orchestrator for all company actions, often bridging UI/events and business/DB layers. Permissions and visibility are checked mostly in the UI and listener, e.g., only admins can edit status or special fields. The creation action also handles audit fields like ChangeUserID and session updates.
Table 1: Create Company
Aspect | Details
Function(s) involved | companyListener.cfc:createCompany(event) companyBO.cfc:createCompany(companyBean) companyDAO.cfc:createCompany(companyBean)
Required Input Arguments | - companyBean object containing all company fields - sessionUser context to get ChangeUserID and permissions
Required Fields (at least) | - CompanyName (logically required but no explicit server-side validation) - If CountryID == 1 (USA), StateID must be selected (client-side JS)
Optional Fields | - Address1, Address2, City, Zip, Phone, Fax, ContactName, ContactEmail, MaxChillers, companyType, ParentID, StatusID, CreditCard fields (ignored)
Business Logic Steps | 1. Set ChangeUserID on companyBean from sessionUser 2. Call BO layer to create company 3. BO calls DAO to insert record into DB 4. If StatusID = 3, create demo data records 5. Update session user's company list and selected company 6. Fire relevant post-creation events (chooseCompanyChildren or createCompanyAdmin)
Validations | - Client-side: Country/State validation in form (checkState()) - Permissions: Only admins can set StatusID, MaxChillers, companyType, ParentID - No explicit server-side validation except DAO parameterized insert
Calculations / Defaults | - CreateDate and ChangeDate set to current time automatically in DAO - ChangeUserID set from session user - StatusID default to 0 unless set - companyType defaults to standalone if unset
Permissions / Restrictions | - Non-admins cannot edit StatusID, MaxChillers, companyType, ParentID - Only admin users can create company with special status (e.g., 3 for demo)
Output / Result | - Struct with success boolean and message - On failure, redisplay form with error message - On success, update session and redirect accordingly
Table 2: Update Company
Aspect | Details
Function(s) involved | companyListener.cfc:editCompany(event) (decides update vs create) companyBO.cfc:updateCompany(companyBean) (assumed) companyDAO.cfc:updateCompany(companyBean) (assumed)
Required Input Arguments | - companyBean object with valid CompanyID - sessionUser context for audit fields
Required Fields (at least) | - CompanyID to identify record - CompanyName logically required - If CountryID == 1 (USA), StateID must be selected (client-side JS)
Optional Fields | Same as Create Company except: - Audit fields ChangeDate, ChangeUserID updated
Business Logic Steps | 1. Check if CompanyID exists, else call create 2. Update fields in DB 3. Update audit fields (ChangeDate, ChangeUserID) 4. Return success/failure message 5. Update session and fire related events
Validations | Same as Create Company Plus: verify company exists before update
Calculations / Defaults | Update ChangeDate to current time Update ChangeUserID from session user
Permissions / Restrictions | Same as Create Company
Output / Result | Struct with success boolean and message
Table 3: Read Company
Aspect | Details
Function(s) involved | companyListener.cfc:readCompany(event) companyBO.cfc:readCompany(companyBean) (assumed)
Required Input Arguments | - companyBean with CompanyID - sessionUser for permissions
Business Logic Steps | 1. Check if user is admin 2. If not admin, restrict to their company only 3. Fetch company data from DB 4. Populate companyBean with data
Validations | Permissions restrict data visibility
Output / Result | Populated companyBean with company details
Table 4: Set Children (Company Hierarchy Management)
Aspect | Details
Function(s) involved | companyListener.cfc:setChildren(event) companyBO.cfc:setChildren(companyID, children)
Required Input Arguments | - companyID (parent company) - children (list of child company IDs)
Business Logic Steps | 1. Associate child companies with parent company in DB 2. Fire event to refresh UI or data
Permissions / Restrictions | Admin or authorized users only (assumed)
Output / Result | Updates company hierarchy in DB
Table 5: Create Demo Records
Aspect | Details
Function(s) involved | companyBO.cfc:createDemoRecords(companyBean)
Required Input Arguments | companyBean with at least CompanyID and StatusID == 3
Business Logic Steps | 1. Insert demo data for performance, locations, chillers linked to company 2. Insert logs and maintenance demo records
Permissions / Restrictions | Triggered automatically when creating a company with StatusID=3 (demo company)
Output / Result | Multiple demo records created in DB

## ChillerManagement
Chiller Entity Fields Definition
Field Name | Data Type | Required | UI Behavior | Validation | Default Value | Remarks
CHILLER_ID | numeric (int) | Yes | Hidden (primary key) | Auto-generated, primary key | Auto-increment | Unique identifier
CHILLER_NAME | string | Yes | Text input | Required, maxlength=50 | None | Chiller name
CHILLER_TYPE | string | Yes | Dropdown select | Required, must be in predefined list | None | Chiller type
CAPACITY | decimal(10,2) | Yes | Number input | Required, numeric, >0 | None | Capacity in tons
MANUFACTURER | string | No | Text input | Maxlength=100 | None | Manufacturer name
INSTALLATION_DATE | date | No | Date picker | Valid date | None | Date installed
STATUS | string | Yes | Select / Radio button | Enum: 'Active', 'Maintenance', 'Inactive' | Active' | Operational status
LAST_MAINTENANCE | date | No | Date picker | Valid date | None | Last maintenance date
NOTES | text | No | Textarea | Maxlength=500 | None | Additional notes
Create Chiller
Action Name | File & Function Location | Input Parameters | Remarks
createChiller | chillerService.cfc - function createChiller(chillerData) | struct chillerData | Inserts a new chiller record after validating input
<cffunction name="createChiller" access="public" returntype="numeric"> <cfargument name="chillerData" type="struct" required="true"> <cfset var newId = 0> <cfset validateChiller(chillerData)> <cfquery name="insertChiller" datasource="#application.dsn#"> INSERT INTO chillers (CHILLER_NAME, CHILLER_TYPE, CAPACITY, MANUFACTURER, INSTALLATION_DATE, STATUS, LAST_MAINTENANCE, NOTES) VALUES ( <cfqueryparam value="#chillerData.chillerName#" cfsqltype="cf_sql_varchar">, <cfqueryparam value="#chillerData.chillerType#" cfsqltype="cf_sql_varchar">, <cfqueryparam value="#chillerData.capacity#" cfsqltype="cf_sql_decimal">, <cfqueryparam value="#chillerData.manufacturer#" cfsqltype="cf_sql_varchar">, <cfqueryparam value="#chillerData.installationDate#" cfsqltype="cf_sql_date">, <cfqueryparam value="#chillerData.status#" cfsqltype="cf_sql_varchar">, <cfqueryparam value="#chillerData.lastMaintenance#" cfsqltype="cf_sql_date">, <cfqueryparam value="#chillerData.notes#" cfsqltype="cf_sql_longvarchar"> ) </cfquery> <cfset newId = insertChiller.generatedKey> <cfreturn newId> </cffunction>
Get Chiller By ID
Action Name | File & Function Location | Input Parameters | Remarks
getChillerById | chillerService.cfc - function getChillerById(chillerId) | numeric chillerId | Returns chiller struct by ID
<cffunction name="getChillerById" access="public" returntype="struct"> <cfargument name="chillerId" type="numeric" required="true"> <cfquery name="qChiller" datasource="#application.dsn#"> SELECT * FROM chillers WHERE CHILLER_ID = <cfqueryparam value="#arguments.chillerId#" cfsqltype="cf_sql_integer"> </cfquery> <cfreturn qChiller.recordCount ? qChiller[1] : {} > </cffunction>
Update Chiller
Action Name | File & Function Location | Input Parameters | Remarks
updateChiller | chillerService.cfc - function updateChiller(chillerId, chillerData) | numeric chillerId, struct chillerData | Updates chiller record after validation
<cffunction name="updateChiller" access="public" returntype="boolean"> <cfargument name="chillerId" type="numeric" required="true"> <cfargument name="chillerData" type="struct" required="true"> <cfset validateChiller(arguments.chillerData)> <cfquery datasource="#application.dsn#"> UPDATE chillers SET CHILLER_NAME = <cfqueryparam value="#chillerData.chillerName#" cfsqltype="cf_sql_varchar">, CHILLER_TYPE = <cfqueryparam value="#chillerData.chillerType#" cfsqltype="cf_sql_varchar">, CAPACITY = <cfqueryparam value="#chillerData.capacity#" cfsqltype="cf_sql_decimal">, MANUFACTURER = <cfqueryparam value="#chillerData.manufacturer#" cfsqltype="cf_sql_varchar">, INSTALLATION_DATE = <cfqueryparam value="#chillerData.installationDate#" cfsqltype="cf_sql_date">, STATUS = <cfqueryparam value="#chillerData.status#" cfsqltype="cf_sql_varchar">, LAST_MAINTENANCE = <cfqueryparam value="#chillerData.lastMaintenance#" cfsqltype="cf_sql_date">, NOTES = <cfqueryparam value="#chillerData.notes#" cfsqltype="cf_sql_longvarchar"> WHERE CHILLER_ID = <cfqueryparam value="#arguments.chillerId#" cfsqltype="cf_sql_integer"> </cfquery> <cfreturn true> </cffunction>
Delete Chiller
Action Name | File & Function Location | Input Parameters | Remarks
deleteChiller | chillerService.cfc - function deleteChiller(chillerId) | numeric chillerId | Deletes chiller record
<cffunction name="deleteChiller" access="public" returntype="boolean"> <cfargument name="chillerId" type="numeric" required="true"> <cfquery datasource="#application.dsn#"> DELETE FROM chillers WHERE CHILLER_ID = <cfqueryparam value="#arguments.chillerId#" cfsqltype="cf_sql_integer"> </cfquery> <cfreturn true> </cffunction>
List All Chillers
Action Name | File & Function Location | Input Parameters | Remarks
listChillers | chillerService.cfc - function listChillers() | None | Returns array of all chillers
<cffunction name="listChillers" access="public" returntype="query"> <cfquery name="qChillers" datasource="#application.dsn#"> SELECT * FROM chillers ORDER BY CHILLER_NAME </cfquery> <cfreturn qChillers> </cffunction>
Validate Chiller Data
Action Name | File & Function Location | Input Parameters | Remarks
validateChiller | chillerService.cfc - function validateChiller(chillerData) | struct chillerData | Validates chiller input data
<cffunction name="validateChiller" access="private" returntype="void"> <cfargument name="chillerData" type="struct" required="true"> <cfif NOT structKeyExists(arguments.chillerData, "chillerName") OR len(trim(arguments.chillerData.chillerName)) EQ 0> <cfthrow message="Chiller name is required."> </cfif> <cfif NOT structKeyExists(arguments.chillerData, "chillerType") OR len(trim(arguments.chillerData.chillerType)) EQ 0> <cfthrow message="Chiller type is required."> </cfif> <cfif NOT structKeyExists(arguments.chillerData, "capacity") OR NOT isNumeric(arguments.chillerData.capacity) OR arguments.chillerData.capacity LTE 0> <cfthrow message="Capacity must be a positive number."> </cfif> <cfif structKeyExists(arguments.chillerData, "manufacturer") AND len(arguments.chillerData.manufacturer) GT 100> <cfthrow message="Manufacturer name too long. Max 100 characters allowed."> </cfif> <cfif structKeyExists(arguments.chillerData, "installationDate") AND NOT isDate(arguments.chillerData.installationDate)> <cfthrow message="Installation date is invalid."> </cfif> <cfif NOT structKeyExists(arguments.chillerData, "status") OR listFindNoCase("Active,Maintenance,Inactive", arguments.chillerData.status) EQ 0> <cfthrow message="Status must be one of Active, Maintenance, or Inactive."> </cfif> <cfif structKeyExists(arguments.chillerData, "lastMaintenance") AND NOT isDate(arguments.chillerData.lastMaintenance)> <cfthrow message="Last maintenance date is invalid."> </cfif> <cfif structKeyExists(arguments.chillerData, "notes") AND len(arguments.chillerData.notes) GT 500> <cfthrow message="Notes too long. Max 500 characters allowed."> </cfif> </cffunction>

## ChillerManagementFinal
Files to look at:- chillerBean, chillerBO, chillerDAO, chillerGateway, chillerListener, userGateway, utilDAO, util, emailSvc
Field Name | Type | Required (in Bean Init) | Visible/Editable in UI (based on typical usage) | Default / Calculated Values | Remarks | Validation | Info Text
ChillerID | numeric | No | Likely hidden / read-only | Default 0 | Primary key, set after insert
ChillerNo | number | No | Yes | Default "" | Unique identifier string for chiller
LocationID | numeric | No | Yes | Default 0 | Foreign key to Location
LocationName | string | No | Likely read-only | Default "" | Display purpose only
Make | numeric | No | Yes | Default 0 | Manufacturer make code
Manufacturer | string | No | Yes | Default "" | Manufacturer name
Model | string | No | Yes | Default "" | Model name/number |  | Enter the model of the chiller.
SerialNum | string | No | Yes | Default "" | Serial number |  | Enter chiller's unique serial number.
IsSteam | boolean | No | Yes (checkbox) | Default false | Indicates steam type
RefrigID | numeric | No | Yes | Default 0 | Refrigerant ID
RefrigType | string | No | Yes (likely dropdown) | Default "0" | Refrigerant type |  | Select the refrigerant Id of the chiller. It would let us know if its a high or low pressure chiller.
HighPressureRefrig | boolean | No | Yes (checkbox) | Default false | High pressure refrigerant flag
UseEvapRefrigTemp | boolean | No | Yes (checkbox) | Default false | Whether to use evaporator refrigerant temp
YearManufactured | numeric | No | Yes | Default 0 | Year of manufacture
EfficiencyRating | numeric | No | Yes | Default 0 | Efficiency rating | 1. Must be between 0.3 and 3 2. must be between 3 and 12 COP | kw/ton - Value Must be between 0.3 and 3 COP - Value must be between 3 and 12
EnergyCost | numeric | No | Yes | Default 0 | Energy cost |  | Enter the energy cost in USD for (kw/hr).
HoursPerWeek | numeric | No | Yes | Default 0 | Operating hours per week | Must be between 1 and 168 | Enter the hours is the chiller going to operate in a week. Ideally between 1 and 168
WeeksPerYear | numeric | No | Yes | Default 0 | Operating weeks per year | must be between 1 and 52 | Enter the number of weeks the chiller is going to operate in a year. Ideally between 1 and 52.
AvgLoadProfile | numeric | No | Yes | Default 0 | Average load profile | must be between 10% and 100% | An average load profile in a chiller represents the typical cooling demand or load on the chiller over a specific time period, used to assess performance and efficiency. Ideally within 10% to 100%.
Tons | numeric | No | Yes | Default 0 | Capacity in tons | 1. The chiller capacity must be between 10 and 8000 2. must be between 35 and 28.128 | Specify the chiller's capacity for the given unit.
DesignInletWaterTemp | numeric | No | Yes | Default 85 | °F unit, value will be either 85 or 86 |  | Enter the designed inlet water temperature of the chiller.
DesignVoltage | numeric | No | Yes | Default 0 | Design voltage | must be between 208 and 13000 | Enter the designed voltage of the chiller.
VoltageChoice | numeric | No | Yes | Default 0 | Voltage choice option |  | Select the voltage choice of the chiller. You can select 'Do not log voltage' if you don't want to report voltage.
FullLoadAmps | numeric | No | Yes | Default 0 | Full load amps | must be between 15 and 3000 | Enter the amperage at full load.
AmpChoice | numeric | No | Yes | Default 0 | Amp choice |  | Select how the Amperage will be reported.
CondDPDrop | string | No | Yes | Default "" | Condenser differential pressure drop |  | Enter the Condenser differential pressure drop.
CondDPDropUnitID | string | No | Yes | Default "" | Unit ID for condenser DP drop
CondDPDropUnit | string | No | Yes | Default "" | Unit name |  | Select the Condenser differential pressure drop unit.
CondPressureUnitID | numeric | No | Yes | Default 0 | Unit ID for condenser pressure
CondPressureUnit | string | No | Yes | Default "" | Unit name |  | Select the Condenser pressure unit.
CondAPDropUnitID | numeric | No | Yes | Default 0 | Condenser approach pressure drop unit ID
CondAPDropUnit | string | No | Yes | Default "" | Unit name |  | Select the Condenser approach pressure drop unit.
CondApproach | string | No | Yes | Default "0" | Condenser approach temperature | 1. should be between 0 and 20 degrees 2. should be between 0 and 11 | Enter the Condenser Approach - in a chiller is the pressure of the refrigerant inside the condenser as it releases heat and condenses from a vapor to a liquid.
EvapDPDrop | string | No | Yes | Default "" | Evaporator differential pressure drop |  | Enter Evaporator differential pressure drop
EvapDPDropUnitID | string | No | Yes | Default "" | Unit ID for evaporator DP drop
EvapDPDropUnit | string | No | Yes | Default "" | Unit name |  | Enter Evaporator differential pressure drop unit.
EvapPressureUnitID | numeric | No | Yes | Default 0 | Evaporator pressure unit ID
EvapPressureUnit | string | No | Yes | Default "" | Unit name |  | Enter Evaporator pressure unit.
EvapAPDropUnitID | numeric | No | Yes | Default 0 | Evaporator approach pressure drop unit ID
EvapAPDropUnit | string | No | Yes | Default "" | Unit name |  | Enter Evaporator Approach Pressure Drop Unit
EvapApproach | string | No | Yes | Default "" | Evaporator approach temperature | 1. should be between 0 and 20 degrees 2. shoudl be between 0 and 11 | Enter the evaporator approach.
EvapDOWTemp | numeric | No | Yes | Default 0 | Evaporator DOW temperature |  | Enter the evaporator DOW temperature.
CompOPIndicator | numeric | No | Yes | Default 0 | Compressor OP Indicator |  | Enter the compressor OP indicator.
CreateDate | date | No | No (auto) | Default now | Created date
UserNote | string | No | Yes (text area) | Default "" | User comments |  | Enter any notes for the chiller.
HavePurge | boolean | No | Yes (checkbox) | Default false | Whether purge exists |  | Select if the purge exists.
MaxPurgeTime | string | No | Yes | Default "0" | Max purge time |  | Specify what is the maximum purge time.
PurgeReadingUnit | boolean | No | Yes (checkbox) | Default false | Purge reading unit |  | Select the purge reading unit.
HaveBearingTemp | boolean | No | Yes (checkbox) | Default false | Bearing temperature presence |  | Specify the bearing temperature presence.
UseRunHours | boolean | No | Yes (checkbox) | Default false | Use run hours |  | If you check this box, Log reading must include Run Hours.
ChangeDate | date | No | No (auto) | Default now | Date of last change
ChangeUserID | string | No | No | Default "0" | User ID who made change
Inactive | boolean | No | Yes (checkbox) | Default false | Inactive flag
isMetric | boolean | No | Yes (checkbox) | Default false | Metric units flag |  | The metric system to be used for the data collected during readings. You can change it later but won't affect the units of the past log entries.
OilPresHighUnitID | numeric | No | Yes | Default 0 | Oil pressure high unit ID
OilPresHighUnit | string | No | Yes | Default "" | Unit name |  | Select Compressor oil pressure (High) unit.
OilPresLowUnitID | numeric | No | Yes | Default 0 | Oil pressure low unit ID
OilPresLowUnit | string | No | Yes | Default "" | Unit name |  | Select Compressor oil pressure (Low) unit.
OilPresDifUnitID | numeric | No | Yes | Default 0 | Oil pressure differential unit ID
OilPresDifUnit | string | No | Yes | Default "" | Unit name |  | Select Compressor oil pressure difference unit.
CondDesignDeltaT | string | No | Yes | Default "" | Condenser design delta T |  | The temperature difference between the condensing temperature and the entering condenser water temperature under design conditions. This ΔT helps determine heat rejection performance and sizing for cooling towers and condenser water loops.
CondDesignFlow | string | No | Yes | Default "" | Condenser design flow |  | The specified rate of water flow required through the condenser to efficiently reject heat under design conditions.
EvapDesignDeltaT | string | No | Yes | Default "" | Evaporator design delta T |  | The temperature difference between the chilled water entering and leaving the evaporator under design conditions.
EvapDesignFlow | string | No | Yes | Default "" | Evaporator design flow |  | The specified chilled water flow rate needed to absorb the desired cooling load under design conditions.
NumberOfCompressors | numeric | No | Yes | Default 1 | Value will be either 1 or 2. |  | Select how many compressors does the chiller have.
ChillerAlerts | query | No | No | Default empty query | Query object holding alerts
UseLoad | boolean | No | Yes (checkbox) | Default false | Whether to use load
validations:-
The function getChillerValidations is used to get the validation rules from utilDAO, apply them and used to validate the chiller details before saving.
Overview:-
This function retrieves the validation rules for a given chiller’s data to ensure that any entered or processed information about the chiller meets the system’s required standards. It accepts a chiller data object as input. Based on whether the chiller uses metric or imperial units, it selects the appropriate validation rules. It converts validation limits (such as temperature or capacity ranges) into the correct units for the chiller. Finally, it returns a set of validation criteria — including allowable minimums, maximums, and messages — that can be used to verify or enforce correct data input for the chiller.
Chiller Retrieval Methods:-
getChillerList(chillerIDList) — returns a list of chillers by ID.
Overview:-
This function retrieves detailed information about a specific set of chillers identified by their IDs. It accepts a list of chiller IDs as input. It fetches and returns all relevant data records for those chillers. The returned information can be used to display, manage, or process the chillers associated with a user or another entity.
getCompanyChillers(companyID) — returns chillers belonging to a company.
Overview:-
This function retrieves all chiller records associated with a specific company. It takes a company’s unique identifier as input. It queries the data source to fetch detailed information about every chiller owned or managed by that company. The returned data can be used for company-wide monitoring, reporting, or management of chillers.
getLocationChillers(LocationID) — returns chillers for a specific location.
Overview:-
This function retrieves all chiller records located at a specific physical location. It accepts a location identifier as input. It fetches detailed information about every chiller installed or assigned to that location. The data returned can be used for location-based management, monitoring, or reporting.
Design Approach Calculations:-
getCDA(YearManufactured) — Returns an integer code representing the Condenser Design Approach based on the year manufactured.
Overview:-
This function determines the appropriate condenser design approach code based on the chiller’s manufacturing year. It accepts the year the chiller was manufactured as input. Based on defined year ranges, it assigns a numeric code representing the condenser design approach typical for that era. Returns this code for use in design calculations, validation, or reporting.
getEDA(YearManufactured) — Returns an integer code representing the Evaporator Design Approach based on the year.
Overview:-
This function returns a code representing the evaporator design approach based on the manufacturing year of the chiller. Takes the chiller’s year of manufacture as input. Assigns a numeric code corresponding to the typical evaporator design approach for that time period. Outputs this code for use in design calculations, validations, or performance evaluations.
getDesignApproaches(chiller) — Combines the above approaches and returns them in a struct, using actual values if present or defaults based on age.
Overview:-
This function retrieves the design approach values for both the condenser and evaporator of a given chiller. It accepts a chiller data object as input. Checks if specific design approach values are already set on the chiller. If set, it uses those values directly. If not set, it calculates appropriate default design approaches based on the chiller’s manufacturing year using related helper functions. Returns a structured result containing the final condenser and evaporator design approach codes.
Create, Read, Update, Delete Operations:-
createChiller(chiller, sessionUser) — Inserts a new chiller if it doesn't exist, updating user session data if successful.
Overview:-
This function creates a new chiller record in the system if it does not already exist. It accepts a chiller data object and the current user’s session object. Checks if a chiller with the same location and number already exists to avoid duplicates. If the chiller is new, it inserts the chiller data into the database. If the chiller uses load information, it sets a default Full Load Amps (FLA) value for safety. Updates the user’s session data to include the newly created chiller for immediate access. Returns a structured response indicating success or failure along with a relevant message.
readChiller(chiller) — Reads a chiller record and loads alerts.
Overview:-
This function retrieves detailed information for a specific chiller. It accepts a chiller data object (typically containing an identifier). Loads the full chiller record from the database into the provided chiller object. Also fetches any alerts associated with the chiller to provide a complete status overview. Does not return data directly, but updates the passed chiller object with the retrieved information.
updateChiller(chiller) — Updates an existing chiller, ensuring Full Load Amps (FLA) is set to 100 if load is used.
Overview:-
This function updates an existing chiller’s information in the system. It accepts a chiller data object containing the updated details. If the chiller uses load data, it ensures the Full Load Amps (FLA) value is safely set to 100. Calls the data access layer to save the updated chiller data to the database. Returns a structured response indicating whether the update was successful, along with a message.
deleteChiller(chiller) — Marks a chiller as inactive (soft delete).
Overview:-
This function marks a chiller record as inactive instead of permanently deleting it. It accepts a chiller data object representing the chiller to be deactivated. Calls the data access layer to update the chiller’s status, effectively performing a soft delete. Does not return any data.
getInactiveChillers() — Gets chillers marked inactive.
Overview:-
This function retrieves a list of all chillers that have been marked as inactive. It does not require any input arguments. Queries the data source to fetch chillers that are currently inactive or deactivated. Returns the list of inactive chillers for reporting, management, or potential reactivation.
reactivateChiller(chillerID) — Reactivates a previously inactive chiller.
Overview:-
This function reactivates a previously inactive chiller. It accepts the unique identifier (chillerID) of the chiller to be reactivated. Calls the data access layer to update the chiller’s status, making it active again. Does not return any data.
Validation Logic:
validateChiller:- Uses the validation rules to check the chiller bean fields. Checks for required fields, numeric ranges, and comparison types. Returns a struct indicating if the chiller is valid and any error messages. If invalid and new chiller, sets ChillerID to -1 (likely a flag).
Overview:-
This function performs comprehensive validation on a chiller’s data record to ensure it meets defined quality and business rules before processing or saving. It takes a chiller data object as input. Retrieves the set of validation rules relevant to the chiller. Checks each field for: Required presence, Correct data type (e.g., numeric), Value ranges (min/max limits), Custom comparisons with other fields. Collects any validation errors found, marking the record as invalid if any rule is broken. If the record is invalid and new (no valid ID), it flags the chiller accordingly. Returns a structured result indicating overall validity and any specific error messages.
Alert Management (in CFScript)
setChillerAlerts(chillerID, chillerAlerts) — Saves alerts for a chiller.
Overview:-
This function assigns or updates alert settings for a specific chiller. It takes a chiller’s unique identifier (chillerID) and a list of alert configurations (chillerAlerts). Passes this data to the data access layer to save or update the alert information linked to that chiller. Does not return any value.
getAvailableAlertsForChiller(chillerID) — Retrieves alerts that can be assigned to a chiller.
Overview:-
This function retrieves all alert types or notifications that can be assigned to a specific chiller. It accepts a chiller’s unique identifier (chillerID) as input. Queries the data source to fetch the list of possible alerts relevant to that chiller. Returns this list as a query for use in configuration or display.
sendChillerAlerts(period) — Sends alert emails for chillers for a given period.
Overview:-
This function manages the process of sending chiller alert notifications for a specified time period. It takes a time period as input (e.g., daily, weekly). Retrieves all alert types relevant to that period. For each alert type, it collects the current alert data grouped by subscribed users. If alerts exist for a user, it triggers the sending of alert notification emails tailored to that user. Coordinates fetching alert data, building email content, and sending notifications in a structured workflow.
getCurrentChillerAlerts(possibleAlert) — Retrieves current alert data grouped by user for sending notifications.
Overview:-
This function gathers and organizes current alert data for a specific alert type, grouped by the users who are subscribed to those alerts. It takes an alert definition (possibleAlert) as input. Based on the alert type, it fetches relevant alert records (e.g., loss alerts or no-log-record alerts). Iterates through the alerts and groups them by user ID. For each user, collects all associated alert details along with user contact info and alert metadata. Returns an array where each entry represents a user with their list of alerts ready for notification.
getLossAlerts(alertID) — Gets alerts related to loss thresholds exceeded.
Overview:-
This function retrieves and compiles loss-related alert data for chillers associated with a specific alert ID. It takes an alert identifier (alertID) as input. Queries to find chillers that have triggered loss alerts. Logs information about chillers with loss alerts for tracking. Retrieves users subscribed to these alerts for the identified chillers. For each chiller-user pair, it creates alert records containing details like location, chiller number, loss value, and reading date. Returns a sorted list of these alert records for further processing or notification.
getDaysWithoutRecordAlerts(alertID) — Gets alerts when chillers haven't logged data recently.
Overview:-
This function retrieves alert data for chillers that have not recorded any log entries within a specified period, based on a given alert ID. It accepts an alert identifier (alertID) as input. Queries chillers that are missing log records triggering this alert. Logs the chillers identified for monitoring purposes. Retrieves users subscribed to alerts for these chillers. For each matching user-chiller pair, it creates alert records containing user contact info, location, chiller details, and how many days have passed since the last log. Returns a sorted list of these alerts for further use, such as sending notifications.
sortAlerts(alerts) — Sorts alerts by user ID.
Overview:-
This function sorts a list of alert records based on the user ID associated with each alert. It accepts an array of alert objects as input. Orders the alerts in ascending order by the UserID field. Returns the sorted array for consistent processing or display
sendChillerAlert(alerts) — Sends emails with alert details.
Overview:-
This function sends email notifications for a list of chiller alerts. It accepts an array of alert objects as input. For each alert, it creates a new email message. Sets the email subject based on the alert’s friendly name. Sets the recipient’s email address. Builds the email body by combining a logo, the alert-specific content, and a closing section. Sends the email using the email service component.
buildAlertEmailBody(alert) — Builds email body based on alert type.
Overview:-
This function generates the email content body based on the type of chiller alert. It accepts an alert structure containing alert details. Determines the type of alert (e.g., loss alert, no log record alert). Calls the appropriate specialized function to build the detailed HTML content for that alert type. Returns the constructed email body as a string for use in notifications.
buildNoLogRecordEmail(alerts) — HTML email for no log record alerts.
Overview:-
This function creates the HTML content for an email alert about chillers that have not recorded log readings within a specified timeframe. It takes an array of alert records as input. Builds a preamble message explaining the alert purpose. Constructs an HTML table listing each chiller’s location, identifier, and the number of days since its last log reading. Returns the complete HTML string combining the preamble, table rows, and closing tags
buildLossAlertEmail(alerts) — HTML email for loss alerts.
Overview:-
This function creates the HTML content for an email alert reporting chillers that exceeded their loss thresholds during the past week. It accepts an array of loss alert records. Builds an introductory message explaining the alert context and significance. Constructs an HTML table showing each chiller’s location, identifier, highest loss percentage, and the date/time of the reading. Formats numeric loss values and timestamps for clear presentation. Returns the full HTML string combining the preamble, detailed table rows, and closing tags.
Below is a list of functions called from other files and used:-
Function / Method Called | Likely Source Component / File | Purpose / Notes
variables.chillerDAO.createChiller() | chillerDAO.cfc | Handles database insert for chiller
variables.chillerDAO.readChiller() | chillerDAO.cfc | Retrieves chiller data from database
variables.chillerDAO.updateChiller() | chillerDAO.cfc | Updates chiller record in database
variables.chillerDAO.deleteChiller() | chillerDAO.cfc | Marks chiller as inactive (soft delete)
variables.chillerDAO.checkChillerRecord() | chillerDAO.cfc | Checks for existing chiller to prevent duplicates
variables.chillerDAO.reactivateChiller() | chillerDAO.cfc | Reactivates an inactive chiller
variables.chillerDAO.getChillerAlerts() | chillerDAO.cfc | Gets alert info related to chillers
variables.chillerDAO.setChillerAlerts() | chillerDAO.cfc | Assigns alert configurations to chillers
variables.chillerGateway.getChillerList() | chillerGateway.cfc | Retrieves chiller lists
variables.chillerGateway.getCompanyChillers() | chillerGateway.cfc | Gets chillers by company
variables.chillerGateway.getChillers() | chillerGateway.cfc | Gets chillers by location
variables.chillerGateway.getChillersWithLossAlerts() | chillerGateway.cfc | Gets chillers with loss alerts
variables.chillerGateway.getChillersWithNoRecordAlerts() | chillerGateway.cfc | Gets chillers missing log records
variables.userGateway.getUsersForAlert() | userGateway.cfc | Gets users subscribed to specific alerts
variables.utilDAO.getChillerValidations() | utilDAO.cfc | Gets validation rules for chillers
variables.util.convertDegrees() | util.cfc | Converts temperature units
variables.util.convertCapacity() | util.cfc | Converts capacity units
variables.util.getCDA() | util.cfc | Gets condenser design approach based on year
variables.util.getEDA() | util.cfc | Gets evaporator design approach based on year
variables.emailSvc.createEmail() | email.cfc | Creates an email object
variables.emailSvc.sendEmail() | email.cfc | Sends an email
Key Functionalities Provided by ChillerDAO
Create Chiller
createChiller(chillerBean) :- Inserts a new chiller record into the database using values from the provided chiller bean object. Handles nullable fields and sets the new chiller ID on the bean after successful insert.
Overview:-
This function inserts a new chiller record into the database with detailed technical and operational information. It accepts a chiller object containing all relevant chiller attributes such as identification, specifications, usage parameters, and metadata. Executes a parameterized SQL INSERT statement to safely add the record to the Chillers table. Handles optional fields carefully by inserting null values when data is not provided. Retrieves and assigns the newly generated unique chiller ID back to the chiller object. Returns a boolean indicating whether the creation succeeded or failed.
Update Chiller
updateChiller(chillerBean) Updates an existing chiller record with the latest data from the chiller bean. Supports nullable fields and tracks who made the change.
Overview:-
This function updates an existing chiller record in the database with new or modified details. It accepts a chiller object containing updated attributes such as identification, technical specifications, operational parameters, and metadata. Performs a parameterized SQL UPDATE statement targeting the specific chiller by its unique ID. Handles optional numeric fields by setting them to null if no valid value is provided. Records the timestamp and user who made the change for auditing purposes. Returns a boolean indicating whether the update was successful or if it failed due to database errors.
Delete Chiller (Soft Delete)
deleteChiller(chillerBean) Marks a chiller record as inactive instead of deleting it physically (soft delete), preserving historical data.
Overview:-
This function marks a chiller record as inactive in the database rather than deleting it permanently. It accepts a chiller object identifying the chiller to be "deleted." Executes an SQL UPDATE query to set the Inactive flag to 1 (true), effectively disabling the chiller record. Updates the change timestamp and records the user who performed the inactivation. Does not remove the record from the database, preserving historical data and allowing future reactivation. Returns nothing (void).
Read Chiller
readChiller(chillerBean) Fetches detailed information about a specific chiller by ID, joining related data like location, refrigerant, manufacturer, and unit names. Populates the chiller bean with the retrieved data.
Overview:-
This function retrieves detailed information about a single chiller from the database and populates a chiller object with this data. It takes a chiller object (which includes the chiller's ID) as input. Executes a database query to fetch all relevant chiller fields along with related data such as location name, refrigerant details, manufacturer info, and unit names by joining multiple tables. Checks if the query returned a record. If found, updates the chiller object’s properties with the retrieved data, including technical specs, measurements, and metadata. Handles numeric checks before setting optional numeric properties to avoid errors. Does not return data directly but modifies the input chiller object with complete, current details.
Check for Existing Chiller
checkChillerRecord(LocationID, ChillerNo) Checks if a chiller with the given location and chiller number already exists and is active, helping prevent duplicates.
Overview:-
This function checks whether a chiller record already exists in the database for a specific location and chiller number, helping to prevent duplicate entries. It accepts a LocationID and a ChillerNo as input parameters. Executes a query against the chiller records to find any active (not inactive) chiller that matches both the location and chiller number. Returns a boolean value: true if a matching active chiller record exists, false if no such record is found.
Reactivate Chiller
reactivateChiller(chillerID) Reactivates a previously inactivated (soft deleted) chiller by setting its inactive flag back to false.
Overview:-
This function reactivates a previously deactivated (inactive) chiller record in the database. It takes a single input parameter: the unique chillerID of the chiller to be reactivated. Executes an update query that sets the inactive status of the specified chiller record to 0 (active). Does not return any value.
Manage Chiller Alerts
getChillerAlerts(chiller) Retrieves alerts linked to a specific chiller and sets them on the chiller bean.
Overview:-
This function retrieves all alert settings associated with a specific chiller. It accepts a chiller object as input. Queries the database to get alert IDs and their friendly names for the given chiller’s ID by joining ChillerAlerts and Alerts tables. Stores the retrieved alert information back into the chiller object via its setChillerAlerts method.
setChillerAlerts(chillerID, chillerAlerts) Removes existing alerts and inserts new alert configurations for the chiller.
Overview:-
This function updates the alert configurations for a specific chiller. It accepts a chiller ID and an array of alert objects (each containing AlertID and Threshold). First, it removes any existing alert entries associated with the given chiller by deleting them from the ChillerAlerts table. Then, if there are new alerts provided, it inserts each alert with its threshold value back into the ChillerAlerts table for the specified chiller.
getAvailableAlertsForChiller(chillerID) Returns a list of all available alerts, indicating which are enabled for the specified chiller.
Overview:-
This function retrieves all possible alerts along with their current configuration status for a specific chiller. It accepts a chiller ID as input. Queries the database to list all alerts available in the system. For each alert, it checks if the alert is currently enabled for the specified chiller and retrieves its configured threshold value. Returns a result set with alert details including AlertID, name, unit, threshold, and whether the alert is enabled (1) or not (0) for that chiller.
Function/Operation | Component/Module | Description | Flow / How Request is Handled | Helpers/Dependencies
createChiller | chillerListener | Creates a new chiller record after validating input and setting alert thresholds | Request enters createChiller function in chillerListener. Validates chillerBean using chillerBO.validateChiller. If valid, processes alert thresholds, calls setChillerAlerts to update alerts, then calls chillerBO.createChiller to save record. Finally announces events for UI update or error display. | chillerBO.validateChiller, chillerBO.setChillerAlerts
updateChiller | chillerListener | Updates existing chiller record with new data and alert thresholds | Similar to createChiller, but calls chillerBO.updateChiller instead. Validates input, updates alerts, triggers events for recalculation or dashboard refresh. On validation failure, sets error messages and re-displays editing screen. | chillerBO.validateChiller, chillerBO.setChillerAlerts
getUsersForCompany | userGateway | Retrieves a list of users for a company with access and location filtering | SQL query filters users by company ID, role, active status, and location list. Supports limited access mode to exclude some roles. Returns user details including role and company name. | Uses SQL joins on UserInfo, Roles, Companies, UserLocs tables
userSearch | userGateway | Searches users by login, password, first/last name, and company | Builds dynamic SQL query based on input search criteria. Returns users matching any provided fields. | None
sendEmail | email component | Sends an email via AWS SMTP using preconfigured settings | Reads SMTP config from JSON, builds email struct, logs the email sending action, then calls mail service to send the email. | AWS SMTP settings from email_settings.json
queryConcat | utility | Concatenates two CF queries with matching columns | Takes two queries, appends rows of second query into first, returns combined query | None
buildDateRange | utility | Builds start and end dates for a year, quarter, or month | Takes year, quarter, and month as inputs; calculates corresponding start/end datetime objects; supports full year, quarter, or month ranges. | CF date/time functions
getLogValidations | utilityDAO | Retrieves validation rules for log entries specific to a chiller | Runs a query with conditional filters based on chiller type (steam/electric), voltage, amps, etc., to return active validation rules for log fields. Applies calculated min/max validation values for amps and volts in code. | Utilizes chillerBean getters for filtering
getLastCalcSavedDate | utilityDAO | Returns last date calculations were saved | Simple query for max CalcSavedDate from CalcSaved table | None
convertPressure | utility | Converts pressure units between PSIG, PSIA, INHG, Feet, KPA, BAR | Converts any input pressure value into PSIG first, then converts PSIG to requested output unit using switch statements | None
CSVToQuery | utility | Parses a CSV string into a ColdFusion query object | Splits CSV string into rows and columns, creates a new query object with corresponding columns, and populates rows with CSV data | None
writeError | utility | Logs error messages related to chillers and bad log records | Calls DAO to insert error info into ErrorLog table. Returns ID of inserted error record | utilDAO.writeError
getErrors | utility | Retrieves detailed error log records with related chiller, location, and company names | Calls DAO to fetch errors by ID list. For each error, fetches chiller/location/company info and appends it to the result for display or reporting. | utilDAO.getErrors, utilDAO.getTextInfoForError
getChillerAlerts | chillerBO | Retrieves alert configurations for a chiller | Queries ChillerAlerts and Alerts tables joined on AlertID for a specific ChillerID | None
setChillerAlerts | chillerBO | Sets or updates alert thresholds for a chiller | Deletes existing alerts for chiller, inserts new alert threshold records per alert in the input array | None
getAvailableAlertsForChiller | chillerBO | Lists all alerts with enabled status and thresholds for a given chiller | Left join Alerts and ChillerAlerts to indicate which alerts are enabled for the chiller | None